## Limitations Not Addressed
Limitations Not Addressed
The following limitations currently do not require a solution.
Energex has contingency plans in place and is actively monitoring load developments in the supply area.
Location:
Maps of Energex’s network showing the location of all Energex’s bulk supply and zone substations are presented via the following link:
https://www.energex.com.au/daprmap2022
Supply Point | Class | Limitation | Comments
Abermain CP | Lockrose BS | 110/33kV Lockrose bulk supply exceeds NCC rating. | Monitoring load development.
Blackstone CP | Raceview BS | 110/33kV Raceview bulk supply exceeds NCC rating. | Monitoring load development.
Brendale BS | Arana Hills ZS | N-1 limitation for the loss of a 33/11 kV 25MVA transformer | Monitoring load development.
Lockrose BS | Laidley ZS | N-1 limitation for the loss of a 33/11kV 10MVA transformer | Monitoring load development.
Postmans Ridge BS | Postmans Ridge ZS | NCC limitation for system normal operation | Monitoring load development.
Lockrose BS | Wivenhoe ZS | N-1 limitation for the loss of a 33/11kV 8MVA transformer | Monitoring load development.
Brendale BS | Lawnton ZS | NCC limitation for system normal operation | Monitoring load development. Operational strategy to remotely reconfigure network.
Beerwah BS | Landsborough ZS | N-1 limitation for the loss of a 33/11kV 10MVA transformer | Monitoring load development.
Abermain BS | 110kV Feeder | Feeder 7259 exceeds ECC rating. | Monitoring load development.
Abermain BS | 33kV Feeder | Feeder 366-1 minor overload under a contingency | Monitoring load development.
Burleigh BS | 33kV Feeder | Feeder 3751 and 3755 exceeds NCC rating. | Monitoring load development.
Caboolture BS | 33 kV Feeder | Voltage constraint at Toorbul Point Substation when feeder 350 and 412 are out of service. | Operational strategy to remotely reconfigure network under contingency.
Gympie BS | 33kV Feeder | Feeder 341-1 overloads when 429 is out of service | Operational strategy to deploy generators under contingency.
Gympie BS | 33kV Feeder | Voltage constraint at Tin Can Bay and Customer Substations when feeder 429 is out of service. | Operational strategy to deploy generators under contingency.
Lockrose BS | 33kV Feeder | Feeders 3828 & 3829 overloads under a contingency. | Operation strategy to deploy generators under contingency.
Lytton BS | 33kV Feeder | Feeder F491-1 overloads when F493-1 is out of service. | Operational strategy to remotely reconfigure network under contingency.
Caboolture BS | 33kV Feeder | Feeder 499-1 overloads when F461 is out of service | Operational strategy to install a POPs scheme
Hays Inlet | 33kV Feeder | Feeder 305-1 overloads under N-1 | Monitoring load development.
Goodna BS | 33kV Feeder | Feeder 3802-1 and 3806-1 overload for contingency of alternate feeder | Monitoring load development.
Belmont ZS | 11kV Feeder | BBSRDL12 exceeds TMU by 0.10MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Burpengary ZS | 11kV Feeder | BGY15A exceeds TMU by 0.10MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Burpengary ZS | 11kV Feeder | BGY6A exceeds TMU by 0.10MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Caboolture ZS | 11kV Feeder | CBT12A exceeds TMU by 0.60MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Caboolture ZS | 11kV Feeder | CBT8A exceeds TMU by 1.40MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Caboolture West ZS | 11kV Feeder | CBW6 exceeds TMU by 1.10MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Caloundra ZS | 11kV Feeder | CLD11 exceeds TMU by 0.20MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Caloundra ZS | 11kV Feeder | CLD1A exceeds TMU by 0.10MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Caloundra ZS | 11kV Feeder | CLD29A exceeds TMU by 0.20MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Coomera ZS | 11kV Feeder | CMA17A exceeds TMU by 0.80MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Crestmead ZS | 11kV Feeder | CRM3A exceeds TMU by 0.60MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Kallangur ZS | 11kV Feeder | KLG10A exceeds TMU by 0.50MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Mango Hill ZS | 11kV Feeder | MHL13A exceeds TMU by 0.05MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Mango Hill ZS | 11kV Feeder | MHL2A exceeds TMU by 0.70MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Mooloolaba ZS | 11kV Feeder | MLB13A exceeds TMU by 0.10MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Nudgee ZS | 11kV Feeder | GCNNGE15 exceeds TMU by 0.20MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Newstead ZS | 11kV Feeder | NSD8A exceeds TMU by 0.20MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Newstead ZS | 11kV Feeder | NSD9A exceeds TMU by 0.50MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Redbank Plains ZS | 11kV Feeder | RPN4A exceeds TMU by 0.80MW in summer 2022/23 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.