## Notes
Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2022-23 to 2026-27)
This workbook provides 5 year DER forecast for sub-transmission feeders in the Energex network.
This workbook forms part of the Energex Distribution Annual Planning Report 2022-23 to 2026-27 (DAPR) and should be read in conjunction with the report document.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation due to COVID 19 impacts. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
The following sections list the 110kV and 132kV feeders and their DER forecasts.
Feeder capacities are shown for ECC and NCC. These ratings have also been adjusted for known committed projects.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
Interconnected feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.

## 110kV & 132kV Feeders DER
Connection Point | Feeder | From Substation | To Substation | Attributes | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | Customer Category | Voltage (kV)
Abermain | F7259/1 | Abermain | Wulkuraka Tee | NCC Rating (A) | 407 | 407 | 407 | 407 | 407 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 22 | 47 | 72 | 96 | 116
|  |  |  | Available Total Capacity for Embedded Generation | 344 | 319 | 294 | 270 | 250
|  |  |  | ECC Rating (A) | 407 | 407 | 407 | 407 | 407
|  |  |  | DER Forecast (A) for N-1 Contingency | 27 | 61 | 95 | 127 | 154
|  |  |  | Available Firm Capacity for Embedded Generation | 339 | 305 | 271 | 239 | 212
Abermain | F7259/2 | Wulkuraka Tee | Lockrose | NCC Rating (A) | 407 | 407 | 407 | 407 | 407 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 56 | 81 | 105 | 129 | 148
|  |  |  | Available Total Capacity for Embedded Generation | 310 | 285 | 261 | 237 | 218
|  |  |  | ECC Rating (A) | 407 | 407 | 407 | 407 | 407
|  |  |  | DER Forecast (A) for N-1 Contingency | 62 | 95 | 128 | 160 | 187
|  |  |  | Available Firm Capacity for Embedded Generation | 304 | 271 | 238 | 206 | 179
Abermain | F7289 | Lockrose | Gatton | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 0 | 0 | 0 | 0 | 0
|  |  |  | Available Total Capacity for Embedded Generation | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | DER Forecast (A) for N-1 Contingency | 0 | 0 | 0 | 0 | 0
|  |  |  | Available Firm Capacity for Embedded Generation | 0 | 0 | 0 | 0 | 0
Belmont | F750 | Belmont | Beenleigh | NCC Rating (A) | 524 | 524 | 524 | 524 | 524 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 123 | 133 | 163 | 187 | 193
|  |  |  | Available Total Capacity for Embedded Generation | 348 | 338 | 308 | 284 | 278
|  |  |  | ECC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | DER Forecast (A) for N-1 Contingency | 151 | 178 | 216 | 249 | 267
|  |  |  | Available Firm Capacity for Embedded Generation | 320 | 293 | 255 | 222 | 204
Belmont | F766 | Belmont | Cleveland | NCC Rating (A) | 1394 | 1394 | 1394 | 1394 | 1394 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 70 | 107 | 145 | 181 | 212
|  |  |  | Available Total Capacity for Embedded Generation | 1184 | 1147 | 1109 | 1073 | 1042
|  |  |  | ECC Rating (A) | 1394 | 1394 | 1394 | 1394 | 1394
|  |  |  | DER Forecast (A) for N-1 Contingency | 140 | 215 | 290 | 362 | 426
|  |  |  | Available Firm Capacity for Embedded Generation | 1114 | 1039 | 964 | 892 | 828
Belmont | F767 | Belmont | Cleveland | NCC Rating (A) | 1394 | 1394 | 1394 | 1394 | 1394 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 70 | 107 | 145 | 181 | 212
|  |  |  | Available Total Capacity for Embedded Generation | 1184 | 1147 | 1109 | 1073 | 1042
|  |  |  | ECC Rating (A) | 1394 | 1394 | 1394 | 1394 | 1394
|  |  |  | DER Forecast (A) for N-1 Contingency | 140 | 215 | 290 | 362 | 426
|  |  |  | Available Firm Capacity for Embedded Generation | 1114 | 1039 | 964 | 892 | 828
Blackstone | F713 | Blackstone | Raceview | NCC Rating (A) | 756 | 756 | 756 | 756 | 756 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 16 | 16 | 31 | 46 | 61
|  |  |  | Available Total Capacity for Embedded Generation | 664 | 664 | 649 | 634 | 619
|  |  |  | ECC Rating (A) | 756 | 756 | 756 | 756 | 756
|  |  |  | DER Forecast (A) for N-1 Contingency | 16 | 32 | 62 | 93 | 121
|  |  |  | Available Firm Capacity for Embedded Generation | 664 | 648 | 618 | 587 | 559
Blackstone | F714 | Blackstone | Raceview | NCC Rating (A) | 756 | 756 | 756 | 756 | 756 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 17 | 16 | 31 | 46 | 61
|  |  |  | Available Total Capacity for Embedded Generation | 663 | 664 | 649 | 634 | 619
|  |  |  | ECC Rating (A) | 756 | 756 | 756 | 756 | 756
|  |  |  | DER Forecast (A) for N-1 Contingency | 17 | 32 | 62 | 93 | 121
|  |  |  | Available Firm Capacity for Embedded Generation | 663 | 648 | 618 | 587 | 559
CBD East | F7231 | Wellington Road | Charlotte St | NCC Rating (A) | 1184 | 1184 | 1184 | 1184 | 1184 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 207 | 207 | 211 | 211 | 212
|  |  |  | Available Total Capacity for Embedded Generation | 858 | 858 | 854 | 854 | 853
|  |  |  | ECC Rating (A) | 1184 | 1184 | 1184 | 1184 | 1184
|  |  |  | DER Forecast (A) for N-1 Contingency | 392 | 392 | 399 | 400 | 400
|  |  |  | Available Firm Capacity for Embedded Generation | 673 | 673 | 666 | 665 | 665
CBD East | F7232 | Wellington Road | Charlotte St | NCC Rating (A) | 1184 | 1184 | 1184 | 1184 | 1184 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 207 | 207 | 211 | 211 | 212
|  |  |  | Available Total Capacity for Embedded Generation | 858 | 858 | 854 | 854 | 853
|  |  |  | ECC Rating (A) | 1184 | 1184 | 1184 | 1184 | 1184
|  |  |  | DER Forecast (A) for N-1 Contingency | 392 | 392 | 399 | 400 | 400
|  |  |  | Available Firm Capacity for Embedded Generation | 673 | 673 | 666 | 665 | 665
CBD East | F7287/3 | Tingalpa Tee | Wellington Road | NCC Rating (A) | 1130 | 1130 | 1130 | 1130 | 1130 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 296 | 278 | 267 | 248 | 235
|  |  |  | Available Total Capacity for Embedded Generation | 721 | 739 | 750 | 769 | 782
|  |  |  | ECC Rating (A) | 1130 | 1130 | 1130 | 1130 | 1130
|  |  |  | DER Forecast (A) for N-1 Contingency | 510 | 482 | 468 | 438 | 419
|  |  |  | Available Firm Capacity for Embedded Generation | 507 | 535 | 549 | 579 | 598
CBD East | F7288/3 | Tingalpa Tee | Wellington Road | NCC Rating (A) | 1130 | 1130 | 1130 | 1130 | 1130 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 294 | 277 | 266 | 248 | 234
|  |  |  | Available Total Capacity for Embedded Generation | 723 | 740 | 751 | 769 | 783
|  |  |  | ECC Rating (A) | 1130 | 1130 | 1130 | 1130 | 1130
|  |  |  | DER Forecast (A) for N-1 Contingency | 508 | 481 | 466 | 438 | 417
|  |  |  | Available Firm Capacity for Embedded Generation | 509 | 536 | 551 | 579 | 600
CBD East | F7230 | Wellington Road | Coorparoo | NCC Rating (A) | 1155 | 1155 | 1155 | 1155 | 1155 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 18 | 21 | 30 | 43 | 55
|  |  |  | Available Total Capacity for Embedded Generation | 1021 | 1018 | 1009 | 996 | 984
|  |  |  | ECC Rating (A) | 1155 | 1155 | 1155 | 1155 | 1155
|  |  |  | DER Forecast (A) for N-1 Contingency | 19 | 27 | 52 | 80 | 106
|  |  |  | Available Firm Capacity for Embedded Generation | 1020 | 1012 | 987 | 959 | 933
CBD East | F7362 | Wellington Road | Coorparoo | NCC Rating (A) | 1155 | 1155 | 1155 | 1155 | 1155 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 18 | 21 | 30 | 43 | 55
|  |  |  | Available Total Capacity for Embedded Generation | 1021 | 1018 | 1009 | 996 | 984
|  |  |  | ECC Rating (A) | 1155 | 1155 | 1155 | 1155 | 1155
|  |  |  | DER Forecast (A) for N-1 Contingency | 19 | 27 | 52 | 80 | 106
|  |  |  | Available Firm Capacity for Embedded Generation | 1020 | 1012 | 987 | 959 | 933
CBD East | F752 | Murarrie | Newstead | NCC Rating (A) | 1352 | 1352 | 1352 | 1352 | 1352 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 91 | 82 | 66 | 58 | 42
|  |  |  | Available Total Capacity for Embedded Generation | 1125 | 1134 | 1150 | 1158 | 1174
|  |  |  | ECC Rating (A) | 1352 | 1352 | 1352 | 1352 | 1352
|  |  |  | DER Forecast (A) for N-1 Contingency | 199 | 189 | 177 | 166 | 152
|  |  |  | Available Firm Capacity for Embedded Generation | 1017 | 1027 | 1039 | 1050 | 1064
CBD East | F753 | Murarrie | Newstead | NCC Rating (A) | 1352 | 1352 | 1352 | 1352 | 1352 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 91 | 82 | 66 | 58 | 42
|  |  |  | Available Total Capacity for Embedded Generation | 1125 | 1134 | 1150 | 1158 | 1174
|  |  |  | ECC Rating (A) | 1352 | 1352 | 1352 | 1352 | 1352
|  |  |  | DER Forecast (A) for N-1 Contingency | 199 | 189 | 177 | 166 | 152
|  |  |  | Available Firm Capacity for Embedded Generation | 1017 | 1027 | 1039 | 1050 | 1064
CBD East | F809 | Newstead | Victoria Park | NCC Rating (A) | 655 | 655 | 655 | 655 | 655 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 27 | 26 | 22 | 23 | 21
|  |  |  | Available Total Capacity for Embedded Generation | 562 | 563 | 567 | 566 | 568
|  |  |  | ECC Rating (A) | 655 | 655 | 655 | 655 | 655
|  |  |  | DER Forecast (A) for N-1 Contingency | 71 | 64 | 57 | 50 | 44
|  |  |  | Available Firm Capacity for Embedded Generation | 518 | 525 | 532 | 539 | 545
CBD East | F810 | Newstead | Victoria Park | NCC Rating (A) | 655 | 655 | 655 | 655 | 655 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 27 | 26 | 22 | 23 | 21
|  |  |  | Available Total Capacity for Embedded Generation | 562 | 563 | 567 | 566 | 568
|  |  |  | ECC Rating (A) | 655 | 655 | 655 | 655 | 655
|  |  |  | DER Forecast (A) for N-1 Contingency | 71 | 64 | 57 | 50 | 44
|  |  |  | Available Firm Capacity for Embedded Generation | 518 | 525 | 532 | 539 | 545
CBD East | F829 | Charlotte St | Ann St | NCC Rating (A) | 909 | 909 | 909 | 909 | 909 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 138 | 137 | 140 | 140 | 140
|  |  |  | Available Total Capacity for Embedded Generation | 680 | 681 | 678 | 678 | 678
|  |  |  | ECC Rating (A) | 909 | 909 | 909 | 909 | 909
|  |  |  | DER Forecast (A) for N-1 Contingency | 271 | 269 | 276 | 275 | 276
|  |  |  | Available Firm Capacity for Embedded Generation | 547 | 549 | 542 | 543 | 542
CBD East | F833 | Charlotte St | Ann St | NCC Rating (A) | 909 | 909 | 909 | 909 | 909 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 138 | 137 | 140 | 140 | 140
|  |  |  | Available Total Capacity for Embedded Generation | 680 | 681 | 678 | 678 | 678
|  |  |  | ECC Rating (A) | 909 | 909 | 909 | 909 | 909
|  |  |  | DER Forecast (A) for N-1 Contingency | 271 | 269 | 276 | 275 | 276
|  |  |  | Available Firm Capacity for Embedded Generation | 547 | 549 | 542 | 543 | 542
CBD East | F834 | McLachlan St | Ann St | NCC Rating (A) | 908 | 908 | 908 | 908 | 908 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 219 | 216 | 223 | 221 | 223
|  |  |  | Available Total Capacity for Embedded Generation | 598 | 601 | 594 | 596 | 594
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast (A) for N-1 Contingency | 281 | 272 | 268 | 259 | 252
|  |  |  | Available Firm Capacity for Embedded Generation | 536 | 545 | 549 | 558 | 565
CBD East | F835 | McLachlan St | Victoria Park | NCC Rating (A) | 908 | 908 | 908 | 908 | 908 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 96 | 88 | 82 | 73 | 68
|  |  |  | Available Total Capacity for Embedded Generation | 721 | 729 | 735 | 744 | 749
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast (A) for N-1 Contingency | 111 | 102 | 93 | 84 | 81
|  |  |  | Available Firm Capacity for Embedded Generation | 706 | 715 | 724 | 733 | 736
CBD East | F914 | Newstead | McLachlan St | NCC Rating (A) | 1232 | 1232 | 1232 | 1232 | 1232 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 20 | 18 | 27 | 29 | 36
|  |  |  | Available Total Capacity for Embedded Generation | 1088 | 1090 | 1081 | 1079 | 1072
|  |  |  | ECC Rating (A) | 1232 | 1232 | 1232 | 1232 | 1232
|  |  |  | DER Forecast (A) for N-1 Contingency | 71 | 66 | 66 | 64 | 69
|  |  |  | Available Firm Capacity for Embedded Generation | 1037 | 1042 | 1042 | 1044 | 1039
CBD East | F915 | Newstead | McLachlan St | NCC Rating (A) | 1232 | 1232 | 1232 | 1232 | 1232 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 20 | 18 | 27 | 29 | 36
|  |  |  | Available Total Capacity for Embedded Generation | 1088 | 1090 | 1081 | 1079 | 1072
|  |  |  | ECC Rating (A) | 1232 | 1232 | 1232 | 1232 | 1232
|  |  |  | DER Forecast (A) for N-1 Contingency | 71 | 66 | 66 | 64 | 69
|  |  |  | Available Firm Capacity for Embedded Generation | 1037 | 1042 | 1042 | 1044 | 1039
CBD South | F830 | West End | Charlotte St | NCC Rating (A) | 651 | 651 | 651 | 651 | 651 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 141 | 133 | 110 | 125 | 109
|  |  |  | Available Total Capacity for Embedded Generation | 444 | 452 | 475 | 460 | 476
|  |  |  | ECC Rating (A) | 651 | 651 | 651 | 651 | 651
|  |  |  | DER Forecast (A) for N-1 Contingency | 193 | 212 | 196 | 191 | 184
|  |  |  | Available Firm Capacity for Embedded Generation | 392 | 373 | 389 | 394 | 401
CBD South | F905 | Rocklea | West End | NCC Rating (A) | 653 | 653 | 653 | 653 | 653 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 218 | 202 | 176 | 180 | 164
|  |  |  | Available Total Capacity for Embedded Generation | 369 | 385 | 411 | 407 | 423
|  |  |  | ECC Rating (A) | 653 | 653 | 653 | 653 | 653
|  |  |  | DER Forecast (A) for N-1 Contingency | 259 | 261 | 236 | 227 | 209
|  |  |  | Available Firm Capacity for Embedded Generation | 328 | 326 | 351 | 360 | 378
CBD West | F7266 | Milton | Customer | NCC Rating (A) | 908 | 908 | 908 | 908 | 908 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 87 | 81 | 71 | 73 | 75
|  |  |  | Available Total Capacity for Embedded Generation | 730 | 736 | 746 | 744 | 742
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast (A) for N-1 Contingency | 160 | 152 | 134 | 155 | 146
|  |  |  | Available Firm Capacity for Embedded Generation | 657 | 665 | 683 | 662 | 671
CBD West | F7267 | Milton | Makerston St | NCC Rating (A) | 908 | 908 | 908 | 908 | 908 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 79 | 76 | 67 | 89 | 73
|  |  |  | Available Total Capacity for Embedded Generation | 738 | 741 | 750 | 728 | 744
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast (A) for N-1 Contingency | 161 | 153 | 135 | 156 | 144
|  |  |  | Available Firm Capacity for Embedded Generation | 656 | 664 | 682 | 661 | 673
CBD West | F7321 | Customer | Makerston St | NCC Rating (A) | 908 | 908 | 908 | 908 | 908 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 49 | 46 | 36 | 34 | 39
|  |  |  | Available Total Capacity for Embedded Generation | 768 | 771 | 781 | 783 | 778
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast (A) for N-1 Contingency | 118 | 113 | 96 | 118 | 107
|  |  |  | Available Firm Capacity for Embedded Generation | 699 | 704 | 721 | 699 | 710
CBD West | F7365 | Kelvin Grove | Milton | NCC Rating (A) | 905 | 905 | 905 | 905 | 905 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 83 | 78 | 67 | 73 | 68
|  |  |  | Available Total Capacity for Embedded Generation | 731 | 736 | 747 | 741 | 746
|  |  |  | ECC Rating (A) | 905 | 905 | 905 | 905 | 905
|  |  |  | DER Forecast (A) for N-1 Contingency | 177 | 164 | 141 | 121 | 135
|  |  |  | Available Firm Capacity for Embedded Generation | 637 | 650 | 673 | 693 | 679
CBD West | F781 | Ashgrove West | Kelvin Grove | NCC Rating (A) | 857 | 857 | 857 | 857 | 857 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 91 | 83 | 71 | 72 | 63
|  |  |  | Available Total Capacity for Embedded Generation | 680 | 688 | 700 | 699 | 708
|  |  |  | ECC Rating (A) | 857 | 857 | 857 | 857 | 857
|  |  |  | DER Forecast (A) for N-1 Contingency | 186 | 170 | 145 | 123 | 132
|  |  |  | Available Firm Capacity for Embedded Generation | 585 | 601 | 626 | 648 | 639
CBD West | F782 | Ashgrove West | Milton | NCC Rating (A) | 857 | 857 | 857 | 857 | 857 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 113 | 104 | 89 | 92 | 82
|  |  |  | Available Total Capacity for Embedded Generation | 658 | 667 | 682 | 679 | 689
|  |  |  | ECC Rating (A) | 857 | 857 | 857 | 857 | 857
|  |  |  | DER Forecast (A) for N-1 Contingency | 191 | 175 | 149 | 136 | 142
|  |  |  | Available Firm Capacity for Embedded Generation | 580 | 596 | 622 | 635 | 629
CBD West | F807 | Makerston St | Charlotte St | NCC Rating (A) | 588 | 588 | 588 | 588 | 588 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 63 | 59 | 48 | 71 | 48
|  |  |  | Available Total Capacity for Embedded Generation | 466 | 470 | 481 | 458 | 481
|  |  |  | ECC Rating (A) | 588 | 588 | 588 | 588 | 588
|  |  |  | DER Forecast (A) for N-1 Contingency | 127 | 119 | 96 | 144 | 100
|  |  |  | Available Firm Capacity for Embedded Generation | 402 | 410 | 433 | 385 | 429
CBD West | F808 | Makerston St | Charlotte St | NCC Rating (A) | 588 | 588 | 588 | 588 | 588 | CBD | 110
|  |  |  | DER Forecast (A) for System Normal | 73 | 68 | 56 | 48 | 56
|  |  |  | Available Total Capacity for Embedded Generation | 456 | 461 | 473 | 481 | 473
|  |  |  | ECC Rating (A) | 588 | 588 | 588 | 588 | 588
|  |  |  | DER Forecast (A) for N-1 Contingency | 142 | 132 | 109 | 99 | 114
|  |  |  | Available Firm Capacity for Embedded Generation | 387 | 397 | 420 | 430 | 415
Loganlea | F704 | Beenleigh | Yatala | NCC Rating (A) | 908 | 908 | 908 | 908 | 908 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 20 | 23 | 24 | 47 | 66
|  |  |  | Available Total Capacity for Embedded Generation | 797 | 794 | 793 | 770 | 751
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast (A) for N-1 Contingency | 119 | 189 | 253 | 309 | 359
|  |  |  | Available Firm Capacity for Embedded Generation | 698 | 628 | 564 | 508 | 458
Loganlea | F7351 | Jimboomba | Beaudesert | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 10 | 25 | 40 | 55 | 69
|  |  |  | Available Total Capacity for Embedded Generation | 510 | 495 | 480 | 465 | 451
|  |  |  | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | DER Forecast (A) for N-1 Contingency | 0 | 0 | 0 | 0 | 0
|  |  |  | Available Firm Capacity for Embedded Generation | 0 | 0 | 0 | 0 | 0
Loganlea | F7354 | Loganlea | Jimboomba | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 96 | 128 | 159 | 187 | 212
|  |  |  | Available Total Capacity for Embedded Generation | 606 | 574 | 543 | 515 | 490
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast (A) for N-1 Contingency | 160 | 215 | 267 | 316 | 358
|  |  |  | Available Firm Capacity for Embedded Generation | 542 | 487 | 435 | 386 | 344
Loganlea | F7377 | Yatala | Coomera | NCC Rating (A) | 908 | 908 | 908 | 908 | 908 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 47 | 51 | 45 | 41 | 37
|  |  |  | Available Total Capacity for Embedded Generation | 770 | 766 | 772 | 776 | 780
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast (A) for N-1 Contingency | 85 | 137 | 185 | 227 | 264
|  |  |  | Available Firm Capacity for Embedded Generation | 732 | 680 | 632 | 590 | 553
Loganlea | F787 | Loganlea | Beenleigh | NCC Rating (A) | 1047 | 1047 | 1047 | 1047 | 1047 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 38 | 68 | 90 | 120 | 141
|  |  |  | Available Total Capacity for Embedded Generation | 904 | 874 | 852 | 822 | 801
|  |  |  | ECC Rating (A) | 1047 | 1047 | 1047 | 1047 | 1047
|  |  |  | DER Forecast (A) for N-1 Contingency | 83 | 129 | 173 | 215 | 251
|  |  |  | Available Firm Capacity for Embedded Generation | 859 | 813 | 769 | 727 | 691
Loganlea | F788/1 | Beenleigh | Russell Island Tee | NCC Rating (A) | 184 | 184 | 184 | 184 | 184 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 16 | 22 | 27 | 33 | 38
|  |  |  | Available Total Capacity for Embedded Generation | 149 | 143 | 138 | 132 | 127
|  |  |  | ECC Rating (A) | 184 | 184 | 184 | 184 | 184
|  |  |  | DER Forecast (A) for N-1 Contingency | 16 | 22 | 27 | 33 | 38
|  |  |  | Available Firm Capacity for Embedded Generation | 149 | 143 | 138 | 132 | 127
Loganlea | F788/2 | Russell Island Tee | Stradbroke Island | NCC Rating (A) | 184 | 184 | 184 | 184 | 184 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 6 | 5 | 6 | 6 | 7
|  |  |  | Available Total Capacity for Embedded Generation | 159 | 160 | 159 | 159 | 158
|  |  |  | ECC Rating (A) | 184 | 184 | 184 | 184 | 184
|  |  |  | DER Forecast (A) for N-1 Contingency | 7 | 5 | 6 | 6 | 7
|  |  |  | Available Firm Capacity for Embedded Generation | 158 | 160 | 159 | 159 | 158
Loganlea | F788/3 | Russell Island Tee | Russell Island | NCC Rating (A) | 681 | 681 | 681 | 681 | 681 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 16 | 20 | 24 | 29 | 33
|  |  |  | Available Total Capacity for Embedded Generation | 596 | 592 | 588 | 583 | 579
|  |  |  | ECC Rating (A) | 681 | 681 | 681 | 681 | 681
|  |  |  | DER Forecast (A) for N-1 Contingency | 16 | 20 | 24 | 29 | 33
|  |  |  | Available Firm Capacity for Embedded Generation | 596 | 592 | 588 | 583 | 579
Loganlea | F793 | Loganlea | North Springwood | NCC Rating (A) | 640 | 640 | 640 | 640 | 640 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 19 | 71 | 19 | 74 | 30
|  |  |  | Available Total Capacity for Embedded Generation | 557 | 505 | 557 | 502 | 546
|  |  |  | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | DER Forecast (A) for N-1 Contingency | 25 | 71 | 65 | 83 | 100
|  |  |  | Available Firm Capacity for Embedded Generation | 551 | 505 | 511 | 493 | 476
Loganlea | F799 | Loganlea | North Springwood | NCC Rating (A) | 640 | 640 | 640 | 640 | 640 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 24 | 71 | 47 | 85 | 73
|  |  |  | Available Total Capacity for Embedded Generation | 552 | 505 | 529 | 491 | 503
|  |  |  | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | DER Forecast (A) for N-1 Contingency | 25 | 71 | 65 | 85 | 99
|  |  |  | Available Firm Capacity for Embedded Generation | 551 | 505 | 511 | 491 | 477
Loganlea | F820 | Loganlea | Jimboomba | NCC Rating (A) | 743 | 743 | 743 | 743 | 743 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 65 | 88 | 109 | 129 | 146
|  |  |  | Available Total Capacity for Embedded Generation | 603 | 580 | 559 | 539 | 522
|  |  |  | ECC Rating (A) | 743 | 743 | 743 | 743 | 743
|  |  |  | DER Forecast (A) for N-1 Contingency | 159 | 214 | 267 | 314 | 356
|  |  |  | Available Firm Capacity for Embedded Generation | 509 | 454 | 401 | 354 | 312
Loganlea | F837 | Loganlea | Beenleigh | NCC Rating (A) | 1047 | 1047 | 1047 | 1047 | 1047 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 38 | 68 | 90 | 120 | 141
|  |  |  | Available Total Capacity for Embedded Generation | 904 | 874 | 852 | 822 | 801
|  |  |  | ECC Rating (A) | 1047 | 1047 | 1047 | 1047 | 1047
|  |  |  | DER Forecast (A) for N-1 Contingency | 83 | 129 | 173 | 215 | 251
|  |  |  | Available Firm Capacity for Embedded Generation | 859 | 813 | 769 | 727 | 691
Loganlea | F836 | Loganlea | Browns Plains | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 22 | 32 | 50 | 66 | 81
|  |  |  | Available Total Capacity for Embedded Generation | 542 | 532 | 514 | 498 | 483
|  |  |  | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | DER Forecast (A) for N-1 Contingency | 32 | 73 | 113 | 150 | 183
|  |  |  | Available Firm Capacity for Embedded Generation | 532 | 491 | 451 | 414 | 381
Loganlea | F843 | Loganlea | Browns Plains | NCC Rating (A) | 684 | 684 | 684 | 684 | 684 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 29 | 41 | 63 | 84 | 103
|  |  |  | Available Total Capacity for Embedded Generation | 586 | 574 | 552 | 531 | 512
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast (A) for N-1 Contingency | 32 | 73 | 113 | 150 | 183
|  |  |  | Available Firm Capacity for Embedded Generation | 583 | 542 | 502 | 465 | 432
Loganlea | F904/1 | Beenleigh | Rocky Point Tee | NCC Rating (A) | 625 | 625 | 625 | 625 | 625 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 147 | 147 | 148 | 148 | 148
|  |  |  | Available Total Capacity for Embedded Generation | 415 | 415 | 414 | 414 | 414
|  |  |  | ECC Rating (A) | 625 | 625 | 625 | 625 | 625
|  |  |  | DER Forecast (A) for N-1 Contingency | 147 | 147 | 148 | 148 | 148
|  |  |  | Available Firm Capacity for Embedded Generation | 415 | 415 | 414 | 414 | 414
Loganlea | F904/2 | Rocky Point Tee | Rocky Point | NCC Rating (A) | 640 | 640 | 640 | 640 | 640 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 150 | 150 | 150 | 150 | 150
|  |  |  | Available Total Capacity for Embedded Generation | 426 | 426 | 426 | 426 | 426
|  |  |  | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | DER Forecast (A) for N-1 Contingency | 150 | 150 | 150 | 150 | 150
|  |  |  | Available Firm Capacity for Embedded Generation | 426 | 426 | 426 | 426 | 426
Loganlea | F904/3 | Rocky Point Tee | Ibis | NCC Rating (A) | 309 | 309 | 309 | 309 | 309 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 5 | 4 | 4 | 4 | 4
|  |  |  | Available Total Capacity for Embedded Generation | 273 | 274 | 274 | 274 | 274
|  |  |  | ECC Rating (A) | 309 | 309 | 309 | 309 | 309
|  |  |  | DER Forecast (A) for N-1 Contingency | 24 | 22 | 22 | 21 | 21
|  |  |  | Available Firm Capacity for Embedded Generation | 254 | 256 | 256 | 257 | 257
Middle Ridge | F726 | Postmans Ridge | Gatton | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 9 | 16 | 24 | 33 | 40
|  |  |  | Available Total Capacity for Embedded Generation | 387 | 380 | 372 | 363 | 356
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | DER Forecast (A) for N-1 Contingency | 62 | 94 | 128 | 158 | 186
|  |  |  | Available Firm Capacity for Embedded Generation | 334 | 302 | 268 | 238 | 210
Middle Ridge | F727 | Middle Ridge | Postmans Ridge | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 9 | 13 | 18 | 23 | 28
|  |  |  | Available Total Capacity for Embedded Generation | 387 | 383 | 378 | 373 | 368
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | DER Forecast (A) for N-1 Contingency | 33 | 50 | 67 | 82 | 97
|  |  |  | Available Firm Capacity for Embedded Generation | 363 | 346 | 329 | 314 | 299
Middle Ridge | F7348 | Middle Ridge | Postmans Ridge | NCC Rating (A) | 1000 | 1000 | 1000 | 1000 | 1000 | Rural | 110
|  |  |  | DER Forecast (A) for System Normal | 12 | 17 | 22 | 28 | 33
|  |  |  | Available Total Capacity for Embedded Generation | 888 | 883 | 878 | 872 | 867
|  |  |  | ECC Rating (A) | 1000 | 1000 | 1000 | 1000 | 1000
|  |  |  | DER Forecast (A) for N-1 Contingency | 39 | 58 | 77 | 95 | 111
|  |  |  | Available Firm Capacity for Embedded Generation | 861 | 842 | 823 | 805 | 789
Molendinar | F7193 | Molendinar | Cades County | NCC Rating (A) | 895 | 895 | 895 | 895 | 895 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 86 | 126 | 160 | 189 | 213
|  |  |  | Available Total Capacity for Embedded Generation | 719 | 679 | 645 | 616 | 592
|  |  |  | ECC Rating (A) | 895 | 895 | 895 | 895 | 895
|  |  |  | DER Forecast (A) for N-1 Contingency | 156 | 226 | 287 | 340 | 383
|  |  |  | Available Firm Capacity for Embedded Generation | 649 | 579 | 518 | 465 | 422
Molendinar | F7229 | Molendinar | Robina | NCC Rating (A) | 929 | 929 | 929 | 929 | 929 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 59 | 70 | 78 | 46 | 63
|  |  |  | Available Total Capacity for Embedded Generation | 777 | 766 | 758 | 790 | 773
|  |  |  | ECC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | DER Forecast (A) for N-1 Contingency | 123 | 134 | 144 | 114 | 128
|  |  |  | Available Firm Capacity for Embedded Generation | 713 | 702 | 692 | 722 | 708
Molendinar | F7283 | Cades County | Coomera | NCC Rating (A) | 908 | 908 | 908 | 908 | 908 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 131 | 186 | 231 | 268 | 296
|  |  |  | Available Total Capacity for Embedded Generation | 686 | 631 | 586 | 549 | 521
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast (A) for N-1 Contingency | 158 | 214 | 264 | 312 | 359
|  |  |  | Available Firm Capacity for Embedded Generation | 659 | 603 | 553 | 505 | 458
Molendinar | F7297 | Molendinar | Cades County | NCC Rating (A) | 895 | 895 | 895 | 895 | 895 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 86 | 126 | 160 | 189 | 213
|  |  |  | Available Total Capacity for Embedded Generation | 719 | 679 | 645 | 616 | 592
|  |  |  | ECC Rating (A) | 895 | 895 | 895 | 895 | 895
|  |  |  | DER Forecast (A) for N-1 Contingency | 156 | 226 | 287 | 340 | 383
|  |  |  | Available Firm Capacity for Embedded Generation | 649 | 579 | 518 | 465 | 422
Molendinar | F798 | Molendinar | Nerang | NCC Rating (A) | 929 | 929 | 929 | 929 | 929 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 47 | 67 | 74 | 60 | 86
|  |  |  | Available Total Capacity for Embedded Generation | 789 | 769 | 762 | 776 | 750
|  |  |  | ECC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | DER Forecast (A) for N-1 Contingency | 88 | 97 | 94 | 118 | 139
|  |  |  | Available Firm Capacity for Embedded Generation | 748 | 739 | 742 | 718 | 697
Molendinar | F907 | Molendinar | Southport | NCC Rating (A) | 777 | 777 | 777 | 777 | 777 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 77 | 71 | 65 | 58 | 52
|  |  |  | Available Total Capacity for Embedded Generation | 622 | 628 | 634 | 641 | 647
|  |  |  | ECC Rating (A) | 777 | 777 | 777 | 777 | 777
|  |  |  | DER Forecast (A) for N-1 Contingency | 166 | 154 | 139 | 126 | 112
|  |  |  | Available Firm Capacity for Embedded Generation | 533 | 545 | 560 | 573 | 587
Molendinar | F917 | Molendinar | Southport | NCC Rating (A) | 777 | 777 | 777 | 777 | 777 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 89 | 83 | 75 | 68 | 60
|  |  |  | Available Total Capacity for Embedded Generation | 610 | 616 | 624 | 631 | 639
|  |  |  | ECC Rating (A) | 777 | 777 | 777 | 777 | 777
|  |  |  | DER Forecast (A) for N-1 Contingency | 165 | 154 | 139 | 126 | 112
|  |  |  | Available Firm Capacity for Embedded Generation | 534 | 545 | 560 | 573 | 587
Molendinar | F916 | Molendinar | Surfers Paradise | NCC Rating (A) | 1037 | 1037 | 1037 | 1037 | 1037 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 210 | 281 | 236 | 195 | 200
|  |  |  | Available Total Capacity for Embedded Generation | 723 | 652 | 697 | 738 | 733
|  |  |  | ECC Rating (A) | 1037 | 1037 | 1037 | 1037 | 1037
|  |  |  | DER Forecast (A) for N-1 Contingency | 237 | 342 | 282 | 231 | 247
|  |  |  | Available Firm Capacity for Embedded Generation | 696 | 591 | 651 | 702 | 686
Mudgeeraba | F706 | Mudgeeraba | Nerang | NCC Rating (A) | 929 | 929 | 929 | 929 | 929 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 56 | 73 | 86 | 66 | 84
|  |  |  | Available Total Capacity for Embedded Generation | 780 | 763 | 750 | 770 | 752
|  |  |  | ECC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | DER Forecast (A) for N-1 Contingency | 119 | 138 | 155 | 136 | 154
|  |  |  | Available Firm Capacity for Embedded Generation | 717 | 698 | 681 | 700 | 682
Mudgeeraba | F754 | Mudgeeraba | Burleigh Heads | NCC Rating (A) | 982 | 982 | 982 | 982 | 982 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 17 | 8 | 34 | 58 | 82
|  |  |  | Available Total Capacity for Embedded Generation | 866 | 875 | 849 | 825 | 801
|  |  |  | ECC Rating (A) | 982 | 982 | 982 | 982 | 982
|  |  |  | DER Forecast (A) for N-1 Contingency | 34 | 16 | 67 | 117 | 164
|  |  |  | Available Firm Capacity for Embedded Generation | 849 | 867 | 816 | 766 | 719
Mudgeeraba | F755 | Mudgeeraba | Burleigh Heads | NCC Rating (A) | 982 | 982 | 982 | 982 | 982 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 17 | 8 | 34 | 59 | 82
|  |  |  | Available Total Capacity for Embedded Generation | 866 | 875 | 849 | 824 | 801
|  |  |  | ECC Rating (A) | 982 | 982 | 982 | 982 | 982
|  |  |  | DER Forecast (A) for N-1 Contingency | 34 | 16 | 67 | 117 | 164
|  |  |  | Available Firm Capacity for Embedded Generation | 849 | 867 | 816 | 766 | 719
Mudgeeraba | F779 | Mudgeeraba | Merrimac | NCC Rating (A) | 1333 | 1333 | 1333 | 1333 | 1333 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 73 | 56 | 90 | 43 | 74
|  |  |  | Available Total Capacity for Embedded Generation | 1126 | 1143 | 1109 | 1156 | 1125
|  |  |  | ECC Rating (A) | 1333 | 1333 | 1333 | 1333 | 1333
|  |  |  | DER Forecast (A) for N-1 Contingency | 121 | 110 | 138 | 90 | 114
|  |  |  | Available Firm Capacity for Embedded Generation | 1078 | 1089 | 1061 | 1109 | 1085
Mudgeeraba | F780 | Mudgeeraba | Merrimac | NCC Rating (A) | 1333 | 1333 | 1333 | 1333 | 1333 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 73 | 56 | 90 | 43 | 74
|  |  |  | Available Total Capacity for Embedded Generation | 1126 | 1143 | 1109 | 1156 | 1125
|  |  |  | ECC Rating (A) | 1333 | 1333 | 1333 | 1333 | 1333
|  |  |  | DER Forecast (A) for N-1 Contingency | 121 | 110 | 138 | 90 | 114
|  |  |  | Available Firm Capacity for Embedded Generation | 1078 | 1089 | 1061 | 1109 | 1085
Mudgeeraba | F794 | Mudgeeraba | Robina | NCC Rating (A) | 929 | 929 | 929 | 929 | 929 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 50 | 64 | 62 | 29 | 57
|  |  |  | Available Total Capacity for Embedded Generation | 786 | 772 | 774 | 807 | 779
|  |  |  | ECC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | DER Forecast (A) for N-1 Contingency | 79 | 107 | 117 | 95 | 121
|  |  |  | Available Firm Capacity for Embedded Generation | 757 | 729 | 719 | 741 | 715
Mudgeeraba | F826 | Broadbeach | Surfers Paradise | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 66 | 95 | 87 | 46 | 68
|  |  |  | Available Total Capacity for Embedded Generation | 417 | 388 | 396 | 437 | 415
|  |  |  | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | DER Forecast (A) for N-1 Contingency | 125 | 158 | 164 | 89 | 129
|  |  |  | Available Firm Capacity for Embedded Generation | 358 | 325 | 319 | 394 | 354
Mudgeeraba | F827 | Broadbeach | Surfers Paradise | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 66 | 95 | 87 | 46 | 68
|  |  |  | Available Total Capacity for Embedded Generation | 417 | 388 | 396 | 437 | 415
|  |  |  | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | DER Forecast (A) for N-1 Contingency | 125 | 158 | 164 | 89 | 129
|  |  |  | Available Firm Capacity for Embedded Generation | 358 | 325 | 319 | 394 | 354
Mudgeeraba | F838 | Mudgeeraba | Varsity Lakes | NCC Rating (A) | 1272 | 1272 | 1272 | 1272 | 1272 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 12 | 15 | 21 | 28 | 35
|  |  |  | Available Total Capacity for Embedded Generation | 1132 | 1129 | 1123 | 1116 | 1109
|  |  |  | ECC Rating (A) | 1272 | 1272 | 1272 | 1272 | 1272
|  |  |  | DER Forecast (A) for N-1 Contingency | 13 | 23 | 38 | 53 | 66
|  |  |  | Available Firm Capacity for Embedded Generation | 1131 | 1121 | 1106 | 1091 | 1078
Mudgeeraba | F839 | Mudgeeraba | Varsity Lakes | NCC Rating (A) | 1272 | 1272 | 1272 | 1272 | 1272 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 12 | 15 | 21 | 28 | 35
|  |  |  | Available Total Capacity for Embedded Generation | 1132 | 1129 | 1123 | 1116 | 1109
|  |  |  | ECC Rating (A) | 1272 | 1272 | 1272 | 1272 | 1272
|  |  |  | DER Forecast (A) for N-1 Contingency | 13 | 23 | 38 | 53 | 66
|  |  |  | Available Firm Capacity for Embedded Generation | 1131 | 1121 | 1106 | 1091 | 1078
Mudgeeraba | F918 | Merrimac | Broadbeach | NCC Rating (A) | 1214 | 1214 | 1214 | 1214 | 1214 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 73 | 73 | 88 | 40 | 70
|  |  |  | Available Total Capacity for Embedded Generation | 1019 | 1019 | 1004 | 1052 | 1022
|  |  |  | ECC Rating (A) | 1214 | 1214 | 1214 | 1214 | 1214
|  |  |  | DER Forecast (A) for N-1 Contingency | 126 | 142 | 146 | 110 | 113
|  |  |  | Available Firm Capacity for Embedded Generation | 966 | 950 | 946 | 982 | 979
Mudgeeraba | F919 | Merrimac | Broadbeach | NCC Rating (A) | 1214 | 1214 | 1214 | 1214 | 1214 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 73 | 73 | 88 | 40 | 70
|  |  |  | Available Total Capacity for Embedded Generation | 1019 | 1019 | 1004 | 1052 | 1022
|  |  |  | ECC Rating (A) | 1214 | 1214 | 1214 | 1214 | 1214
|  |  |  | DER Forecast (A) for N-1 Contingency | 126 | 142 | 146 | 110 | 113
|  |  |  | Available Firm Capacity for Embedded Generation | 966 | 950 | 946 | 982 | 979
Murarrie | F7270 | Murarrie | Lytton Bulk | NCC Rating (A) | 1009 | 1009 | 1009 | 1009 | 1009 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 125 | 113 | 102 | 92 | 81
|  |  |  | Available Total Capacity for Embedded Generation | 783 | 795 | 806 | 816 | 827
|  |  |  | ECC Rating (A) | 1009 | 1009 | 1009 | 1009 | 1009
|  |  |  | DER Forecast (A) for N-1 Contingency | 251 | 229 | 206 | 186 | 164
|  |  |  | Available Firm Capacity for Embedded Generation | 657 | 679 | 702 | 722 | 744
Murarrie | F7271 | Murarrie | Lytton Bulk | NCC Rating (A) | 1009 | 1009 | 1009 | 1009 | 1009 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 126 | 115 | 103 | 93 | 82
|  |  |  | Available Total Capacity for Embedded Generation | 782 | 793 | 805 | 815 | 826
|  |  |  | ECC Rating (A) | 1009 | 1009 | 1009 | 1009 | 1009
|  |  |  | DER Forecast (A) for N-1 Contingency | 251 | 229 | 206 | 186 | 164
|  |  |  | Available Firm Capacity for Embedded Generation | 657 | 679 | 702 | 722 | 744
Murarrie | F7272 | Murarrie | Doboy | NCC Rating (A) | 908 | 908 | 908 | 908 | 908 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 29 | 18 | 6 | 5 | 15
|  |  |  | Available Total Capacity for Embedded Generation | 788 | 799 | 811 | 812 | 802
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast (A) for N-1 Contingency | 43 | 27 | 9 | 7 | 22
|  |  |  | Available Firm Capacity for Embedded Generation | 774 | 790 | 808 | 810 | 795
Murarrie | F7273 | Murarrie | Doboy | NCC Rating (A) | 908 | 908 | 908 | 908 | 908 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 29 | 18 | 6 | 5 | 15
|  |  |  | Available Total Capacity for Embedded Generation | 788 | 799 | 811 | 812 | 802
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast (A) for N-1 Contingency | 43 | 27 | 9 | 7 | 22
|  |  |  | Available Firm Capacity for Embedded Generation | 774 | 790 | 808 | 810 | 795
Murarrie | F7274 | Murarrie | Doboy | NCC Rating (A) | 908 | 908 | 908 | 908 | 908 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 29 | 18 | 6 | 5 | 15
|  |  |  | Available Total Capacity for Embedded Generation | 788 | 799 | 811 | 812 | 802
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast (A) for N-1 Contingency | 43 | 27 | 9 | 7 | 22
|  |  |  | Available Firm Capacity for Embedded Generation | 774 | 790 | 808 | 810 | 795
Palmwoods | F745/2 | Moodlu | Beerwah Tee | NCC Rating (A) | 768 | 768 | 768 | 768 | 768 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 99 | 104 | 111 | 122 | 136
|  |  |  | Available Total Capacity for Embedded Generation | 592 | 587 | 580 | 569 | 555
|  |  |  | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast (A) for N-1 Contingency | 236 | 234 | 228 | 238 | 256
|  |  |  | Available Firm Capacity for Embedded Generation | 455 | 457 | 463 | 453 | 435
Palmwoods | F745/3 | Moodlu | Caboolture | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 70 | 113 | 154 | 192 | 226
|  |  |  | Available Total Capacity for Embedded Generation | 650 | 607 | 566 | 528 | 494
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | DER Forecast (A) for N-1 Contingency | 141 | 227 | 307 | 384 | 450
|  |  |  | Available Firm Capacity for Embedded Generation | 579 | 493 | 413 | 336 | 270
Palmwoods | F745/4 | Palmwoods | Beerwah Tee | NCC Rating (A) | 768 | 768 | 768 | 768 | 768 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 114 | 132 | 150 | 174 | 198
|  |  |  | Available Total Capacity for Embedded Generation | 577 | 559 | 541 | 517 | 493
|  |  |  | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast (A) for N-1 Contingency | 252 | 260 | 268 | 289 | 325
|  |  |  | Available Firm Capacity for Embedded Generation | 439 | 431 | 423 | 402 | 366
Palmwoods | F745/5 | Beerwah Tee | Beerwah | NCC Rating (A) | 684 | 684 | 684 | 684 | 684 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 17 | 30 | 41 | 52 | 63
|  |  |  | Available Total Capacity for Embedded Generation | 598 | 585 | 574 | 563 | 552
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast (A) for N-1 Contingency | 35 | 59 | 82 | 105 | 125
|  |  |  | Available Firm Capacity for Embedded Generation | 580 | 556 | 533 | 510 | 490
Palmwoods | F746/2 | Moodlu | Beerwah Tee | NCC Rating (A) | 768 | 768 | 768 | 768 | 768 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 99 | 104 | 111 | 122 | 136
|  |  |  | Available Total Capacity for Embedded Generation | 592 | 587 | 580 | 569 | 555
|  |  |  | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast (A) for N-1 Contingency | 236 | 234 | 228 | 238 | 256
|  |  |  | Available Firm Capacity for Embedded Generation | 455 | 457 | 463 | 453 | 435
Palmwoods | F746/3 | Moodlu | Caboolture | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 70 | 114 | 154 | 193 | 226
|  |  |  | Available Total Capacity for Embedded Generation | 650 | 606 | 566 | 527 | 494
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | DER Forecast (A) for N-1 Contingency | 141 | 227 | 307 | 384 | 450
|  |  |  | Available Firm Capacity for Embedded Generation | 579 | 493 | 413 | 336 | 270
Palmwoods | F746/4 | Palmwoods | Beerwah Tee | NCC Rating (A) | 768 | 768 | 768 | 768 | 768 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 114 | 132 | 150 | 174 | 198
|  |  |  | Available Total Capacity for Embedded Generation | 577 | 559 | 541 | 517 | 493
|  |  |  | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast (A) for N-1 Contingency | 252 | 261 | 268 | 290 | 325
|  |  |  | Available Firm Capacity for Embedded Generation | 439 | 430 | 423 | 401 | 366
Palmwoods | F746/5 | Beerwah Tee | Beerwah | NCC Rating (A) | 976 | 976 | 976 | 976 | 976 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 17 | 30 | 41 | 52 | 63
|  |  |  | Available Total Capacity for Embedded Generation | 861 | 848 | 837 | 826 | 815
|  |  |  | ECC Rating (A) | 976 | 976 | 976 | 976 | 976
|  |  |  | DER Forecast (A) for N-1 Contingency | 35 | 59 | 82 | 105 | 125
|  |  |  | Available Firm Capacity for Embedded Generation | 843 | 819 | 796 | 773 | 753
Palmwoods 132 kV | F7189/1 | Palmwoods | Image Flat | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 67 | 81 | 57 | 63 | 69
|  |  |  | Available Total Capacity for Embedded Generation | 606 | 592 | 616 | 610 | 604
|  |  |  | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | DER Forecast (A) for N-1 Contingency | 194 | 198 | 196 | 208 | 227
|  |  |  | Available Firm Capacity for Embedded Generation | 479 | 475 | 477 | 465 | 446
Palmwoods 132 kV | F7189/2 | Image Flat | Cooroy | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 115 | 126 | 114 | 117 | 123
|  |  |  | Available Total Capacity for Embedded Generation | 517 | 506 | 518 | 515 | 509
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast (A) for N-1 Contingency | 259 | 277 | 291 | 318 | 351
|  |  |  | Available Firm Capacity for Embedded Generation | 373 | 355 | 341 | 314 | 281
Palmwoods 132 kV | F7189/3 | Image Flat | Nambour | NCC Rating (A) | 524 | 524 | 524 | 524 | 524 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 65 | 83 | 99 | 114 | 128
|  |  |  | Available Total Capacity for Embedded Generation | 406 | 388 | 372 | 357 | 343
|  |  |  | ECC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | DER Forecast (A) for N-1 Contingency | 131 | 165 | 198 | 228 | 257
|  |  |  | Available Firm Capacity for Embedded Generation | 340 | 306 | 273 | 243 | 214
Palmwoods 132 kV | F7298 | Sunrise Hills | Noosaville | NCC Rating (A) | 684 | 684 | 684 | 684 | 684 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 10 | 2 | 7 | 14 | 22
|  |  |  | Available Total Capacity for Embedded Generation | 605 | 613 | 608 | 601 | 593
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast (A) for N-1 Contingency | 19 | 4 | 13 | 29 | 43
|  |  |  | Available Firm Capacity for Embedded Generation | 596 | 611 | 602 | 586 | 572
Palmwoods 132 kV | F777 | Palmwoods | Mooloolaba | NCC Rating (A) | 1078 | 1078 | 1078 | 1078 | 1078 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 20 | 50 | 78 | 105 | 130
|  |  |  | Available Total Capacity for Embedded Generation | 950 | 920 | 892 | 865 | 840
|  |  |  | ECC Rating (A) | 1078 | 1078 | 1078 | 1078 | 1078
|  |  |  | DER Forecast (A) for N-1 Contingency | 28 | 72 | 115 | 154 | 190
|  |  |  | Available Firm Capacity for Embedded Generation | 942 | 898 | 855 | 816 | 780
Palmwoods 132 kV | F778 | Palmwoods | Mooloolaba | NCC Rating (A) | 1078 | 1078 | 1078 | 1078 | 1078 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 20 | 50 | 78 | 105 | 130
|  |  |  | Available Total Capacity for Embedded Generation | 950 | 920 | 892 | 865 | 840
|  |  |  | ECC Rating (A) | 1078 | 1078 | 1078 | 1078 | 1078
|  |  |  | DER Forecast (A) for N-1 Contingency | 39 | 89 | 137 | 181 | 222
|  |  |  | Available Firm Capacity for Embedded Generation | 931 | 881 | 833 | 789 | 748
Palmwoods 132 kV | F790 | Sunrise Hills | Noosaville | NCC Rating (A) | 684 | 684 | 684 | 684 | 684 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 10 | 2 | 7 | 14 | 22
|  |  |  | Available Total Capacity for Embedded Generation | 605 | 613 | 608 | 601 | 593
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast (A) for N-1 Contingency | 19 | 4 | 13 | 29 | 44
|  |  |  | Available Firm Capacity for Embedded Generation | 596 | 611 | 602 | 586 | 571
Palmwoods 132 kV | F795/1 | Palmwoods | Image Flat | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 67 | 81 | 57 | 63 | 69
|  |  |  | Available Total Capacity for Embedded Generation | 606 | 592 | 616 | 610 | 604
|  |  |  | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | DER Forecast (A) for N-1 Contingency | 195 | 198 | 197 | 209 | 227
|  |  |  | Available Firm Capacity for Embedded Generation | 478 | 475 | 476 | 464 | 446
Palmwoods 132 kV | F795/2 | Image Flat | Cooroy | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 115 | 126 | 114 | 117 | 124
|  |  |  | Available Total Capacity for Embedded Generation | 517 | 506 | 518 | 515 | 508
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast (A) for N-1 Contingency | 259 | 278 | 291 | 319 | 352
|  |  |  | Available Firm Capacity for Embedded Generation | 373 | 354 | 341 | 313 | 280
Palmwoods 132 kV | F795/3 | Image Flat | Nambour | NCC Rating (A) | 524 | 524 | 524 | 524 | 524 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 65 | 83 | 99 | 114 | 128
|  |  |  | Available Total Capacity for Embedded Generation | 406 | 388 | 372 | 357 | 343
|  |  |  | ECC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | DER Forecast (A) for N-1 Contingency | 131 | 165 | 198 | 228 | 257
|  |  |  | Available Firm Capacity for Embedded Generation | 340 | 306 | 273 | 243 | 214
Palmwoods 132 kV | F796 | Cooroy | Sunrise Hills | NCC Rating (A) | 684 | 684 | 684 | 684 | 684 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 52 | 83 | 114 | 144 | 172
|  |  |  | Available Total Capacity for Embedded Generation | 563 | 532 | 501 | 471 | 443
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast (A) for N-1 Contingency | 103 | 165 | 227 | 287 | 342
|  |  |  | Available Firm Capacity for Embedded Generation | 512 | 450 | 388 | 328 | 273
Palmwoods 132 kV | F797 | Cooroy | Sunrise Hills | NCC Rating (A) | 684 | 684 | 684 | 684 | 684 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 52 | 83 | 114 | 144 | 172
|  |  |  | Available Total Capacity for Embedded Generation | 563 | 532 | 501 | 471 | 443
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast (A) for N-1 Contingency | 103 | 165 | 227 | 287 | 342
|  |  |  | Available Firm Capacity for Embedded Generation | 512 | 450 | 388 | 328 | 273
Palmwoods 132 kV | F803 | Mooloolaba | Caloundra | NCC Rating (A) | 684 | 684 | 684 | 684 | 684 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 34 | 51 | 67 | 80 | 93
|  |  |  | Available Total Capacity for Embedded Generation | 581 | 564 | 548 | 535 | 522
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast (A) for N-1 Contingency | 69 | 111 | 149 | 184 | 215
|  |  |  | Available Firm Capacity for Embedded Generation | 546 | 504 | 466 | 431 | 400
Palmwoods 132 kV | F804 | Caloundra | Currimundi | NCC Rating (A) | 664 | 664 | 664 | 664 | 664 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 9 | 12 | 14 | 15 | 16
|  |  |  | Available Total Capacity for Embedded Generation | 588 | 585 | 583 | 582 | 581
|  |  |  | ECC Rating (A) | 664 | 664 | 664 | 664 | 664
|  |  |  | DER Forecast (A) for N-1 Contingency | 41 | 62 | 79 | 93 | 110
|  |  |  | Available Firm Capacity for Embedded Generation | 556 | 535 | 518 | 504 | 487
Palmwoods 132 kV | F815 | Mooloolaba | Alexandra Headlands | NCC Rating (A) | 684 | 684 | 684 | 684 | 684 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 54 | 51 | 46 | 40 | 34
|  |  |  | Available Total Capacity for Embedded Generation | 561 | 564 | 569 | 575 | 581
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast (A) for N-1 Contingency | 79 | 95 | 107 | 117 | 126
|  |  |  | Available Firm Capacity for Embedded Generation | 536 | 520 | 508 | 498 | 489
Palmwoods 132 kV | F816 | Mooloolaba | West Maroochydore | NCC Rating (A) | 684 | 684 | 684 | 684 | 684 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 25 | 34 | 42 | 49 | 55
|  |  |  | Available Total Capacity for Embedded Generation | 590 | 581 | 573 | 566 | 560
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast (A) for N-1 Contingency | 31 | 50 | 67 | 82 | 96
|  |  |  | Available Firm Capacity for Embedded Generation | 584 | 565 | 548 | 533 | 519
Palmwoods 132 kV | F819 | Mooloolaba | Kawana | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 35 | 60 | 83 | 104 | 123
|  |  |  | Available Total Capacity for Embedded Generation | 529 | 504 | 481 | 460 | 441
|  |  |  | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | DER Forecast (A) for N-1 Contingency | 68 | 111 | 149 | 184 | 215
|  |  |  | Available Firm Capacity for Embedded Generation | 496 | 453 | 415 | 380 | 349
Palmwoods 132 kV | F821 | West Maroochydore | Alexandra Headlands | NCC Rating (A) | 684 | 684 | 684 | 684 | 684 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 36 | 17 | 3 | 22 | 39
|  |  |  | Available Total Capacity for Embedded Generation | 579 | 598 | 612 | 593 | 576
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast (A) for N-1 Contingency | 37 | 27 | 65 | 100 | 131
|  |  |  | Available Firm Capacity for Embedded Generation | 578 | 588 | 550 | 515 | 484
Palmwoods 132 kV | F844 | Kawana | Birtinya | NCC Rating (A) | 664 | 664 | 664 | 664 | 664 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 36 | 51 | 64 | 75 | 85
|  |  |  | Available Total Capacity for Embedded Generation | 561 | 546 | 533 | 522 | 512
|  |  |  | ECC Rating (A) | 664 | 664 | 664 | 664 | 664
|  |  |  | DER Forecast (A) for N-1 Contingency | 69 | 102 | 130 | 155 | 177
|  |  |  | Available Firm Capacity for Embedded Generation | 528 | 495 | 467 | 442 | 420
Palmwoods 132 kV | F851 | Birtinya | Currimundi | NCC Rating (A) | 664 | 664 | 664 | 664 | 664 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 42 | 52 | 60 | 66 | 72
|  |  |  | Available Total Capacity for Embedded Generation | 555 | 545 | 537 | 531 | 525
|  |  |  | ECC Rating (A) | 664 | 664 | 664 | 664 | 664
|  |  |  | DER Forecast (A) for N-1 Contingency | 75 | 103 | 126 | 146 | 164
|  |  |  | Available Firm Capacity for Embedded Generation | 522 | 494 | 471 | 451 | 433
Palmwoods 132 kV | F845 | Palmwoods | West Maroochydore | NCC Rating (A) | 1018 | 1018 | 1018 | 1018 | 1018 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 6 | 28 | 50 | 70 | 89
|  |  |  | Available Total Capacity for Embedded Generation | 910 | 888 | 866 | 846 | 827
|  |  |  | ECC Rating (A) | 1018 | 1018 | 1018 | 1018 | 1018
|  |  |  | DER Forecast (A) for N-1 Contingency | 11 | 41 | 70 | 99 | 126
|  |  |  | Available Firm Capacity for Embedded Generation | 905 | 875 | 846 | 817 | 790
Palmwoods 132 kV | F846 | Palmwoods | West Maroochydore | NCC Rating (A) | 1018 | 1018 | 1018 | 1018 | 1018 | Urban | 132
|  |  |  | DER Forecast (A) for System Normal | 6 | 28 | 50 | 70 | 89
|  |  |  | Available Total Capacity for Embedded Generation | 910 | 888 | 866 | 846 | 827
|  |  |  | ECC Rating (A) | 1018 | 1018 | 1018 | 1018 | 1018
|  |  |  | DER Forecast (A) for N-1 Contingency | 11 | 41 | 70 | 99 | 126
|  |  |  | Available Firm Capacity for Embedded Generation | 905 | 875 | 846 | 817 | 790
Rocklea | F817 | Rocklea | Archerfield | NCC Rating (A) | 908 | 908 | 908 | 908 | 908 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 4 | 9 | 21 | 33 | 42
|  |  |  | Available Total Capacity for Embedded Generation | 813 | 808 | 796 | 784 | 775
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast (A) for N-1 Contingency | 8 | 18 | 43 | 66 | 85
|  |  |  | Available Firm Capacity for Embedded Generation | 809 | 799 | 774 | 751 | 732
Rocklea | F818 | Rocklea | Archerfield | NCC Rating (A) | 908 | 908 | 908 | 908 | 908 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 4 | 9 | 21 | 33 | 42
|  |  |  | Available Total Capacity for Embedded Generation | 813 | 808 | 796 | 784 | 775
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast (A) for N-1 Contingency | 8 | 18 | 43 | 66 | 85
|  |  |  | Available Firm Capacity for Embedded Generation | 809 | 799 | 774 | 751 | 732
South Pine | F7337 | Nudgee | Myrtletown | NCC Rating (A) | 1106 | 1106 | 1106 | 1106 | 1106 | High Sec | 110
|  |  |  | DER Forecast (A) for System Normal | 67 | 67 | 66 | 66 | 66
|  |  |  | Available Total Capacity for Embedded Generation | 928 | 928 | 929 | 929 | 929
|  |  |  | ECC Rating (A) | 1106 | 1106 | 1106 | 1106 | 1106
|  |  |  | DER Forecast (A) for N-1 Contingency | 123 | 124 | 123 | 123 | 122
|  |  |  | Available Firm Capacity for Embedded Generation | 872 | 871 | 872 | 872 | 873
South Pine | F7338 | Nudgee | Myrtletown | NCC Rating (A) | 1106 | 1106 | 1106 | 1106 | 1106 | High Sec | 110
|  |  |  | DER Forecast (A) for System Normal | 67 | 67 | 66 | 66 | 66
|  |  |  | Available Total Capacity for Embedded Generation | 928 | 928 | 929 | 929 | 929
|  |  |  | ECC Rating (A) | 1106 | 1106 | 1106 | 1106 | 1106
|  |  |  | DER Forecast (A) for N-1 Contingency | 123 | 124 | 123 | 123 | 122
|  |  |  | Available Firm Capacity for Embedded Generation | 872 | 871 | 872 | 872 | 873
South Pine | F7341 | South Pine | Nudgee | NCC Rating (A) | 1553 | 1553 | 1553 | 1553 | 1553 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 187 | 171 | 155 | 141 | 129
|  |  |  | Available Total Capacity for Embedded Generation | 1210 | 1226 | 1242 | 1256 | 1268
|  |  |  | ECC Rating (A) | 1553 | 1553 | 1553 | 1553 | 1553
|  |  |  | DER Forecast (A) for N-1 Contingency | 367 | 335 | 302 | 274 | 248
|  |  |  | Available Firm Capacity for Embedded Generation | 1030 | 1062 | 1095 | 1123 | 1149
South Pine | F7342 | South Pine | Nudgee | NCC Rating (A) | 1553 | 1553 | 1553 | 1553 | 1553 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 187 | 172 | 155 | 141 | 129
|  |  |  | Available Total Capacity for Embedded Generation | 1210 | 1225 | 1242 | 1256 | 1268
|  |  |  | ECC Rating (A) | 1553 | 1553 | 1553 | 1553 | 1553
|  |  |  | DER Forecast (A) for N-1 Contingency | 367 | 335 | 302 | 274 | 248
|  |  |  | Available Firm Capacity for Embedded Generation | 1030 | 1062 | 1095 | 1123 | 1149
South Pine | F7344 | South Pine | Griffin | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 28 | 52 | 75 | 119 | 116
|  |  |  | Available Total Capacity for Embedded Generation | 1070 | 1046 | 1023 | 979 | 982
|  |  |  | ECC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220
|  |  |  | DER Forecast (A) for N-1 Contingency | 53 | 100 | 145 | 227 | 222
|  |  |  | Available Firm Capacity for Embedded Generation | 1045 | 998 | 953 | 871 | 876
South Pine | F7345 | South Pine | Griffin | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 28 | 52 | 75 | 119 | 116
|  |  |  | Available Total Capacity for Embedded Generation | 1070 | 1046 | 1023 | 979 | 982
|  |  |  | ECC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220
|  |  |  | DER Forecast (A) for N-1 Contingency | 53 | 100 | 145 | 227 | 222
|  |  |  | Available Firm Capacity for Embedded Generation | 1045 | 998 | 953 | 871 | 876
South Pine | F7358 | Griffin | Hays Inlet | NCC Rating (A) | 1373 | 1373 | 1373 | 1373 | 1373 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 42 | 64 | 85 | 168 | 123
|  |  |  | Available Total Capacity for Embedded Generation | 1193 | 1171 | 1150 | 1067 | 1112
|  |  |  | ECC Rating (A) | 1373 | 1373 | 1373 | 1373 | 1373
|  |  |  | DER Forecast (A) for N-1 Contingency | 61 | 96 | 129 | 187 | 188
|  |  |  | Available Firm Capacity for Embedded Generation | 1174 | 1139 | 1106 | 1048 | 1047
South Pine | F737/1 | South Pine | Bunyaville | NCC Rating (A) | 918 | 918 | 918 | 918 | 918 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 54 | 36 | 29 | 40 | 59
|  |  |  | Available Total Capacity for Embedded Generation | 772 | 790 | 797 | 786 | 767
|  |  |  | ECC Rating (A) | 918 | 918 | 918 | 918 | 918
|  |  |  | DER Forecast (A) for N-1 Contingency | 95 | 52 | 30 | 63 | 108
|  |  |  | Available Firm Capacity for Embedded Generation | 731 | 774 | 796 | 763 | 718
South Pine | F737/2 | Bunyaville | Stafford | NCC Rating (A) | 1264 | 1264 | 1264 | 1264 | 1264 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 53 | 35 | 28 | 39 | 59
|  |  |  | Available Total Capacity for Embedded Generation | 1084 | 1102 | 1109 | 1098 | 1078
|  |  |  | ECC Rating (A) | 1264 | 1264 | 1264 | 1264 | 1264
|  |  |  | DER Forecast (A) for N-1 Contingency | 95 | 51 | 28 | 63 | 108
|  |  |  | Available Firm Capacity for Embedded Generation | 1042 | 1086 | 1109 | 1074 | 1029
South Pine | F738/1 | South Pine | Bunyaville | NCC Rating (A) | 918 | 918 | 918 | 918 | 918 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 54 | 36 | 29 | 40 | 59
|  |  |  | Available Total Capacity for Embedded Generation | 772 | 790 | 797 | 786 | 767
|  |  |  | ECC Rating (A) | 918 | 918 | 918 | 918 | 918
|  |  |  | DER Forecast (A) for N-1 Contingency | 95 | 52 | 30 | 63 | 108
|  |  |  | Available Firm Capacity for Embedded Generation | 731 | 774 | 796 | 763 | 718
South Pine | F738/2 | Bunyaville B | Stafford | NCC Rating (A) | 1264 | 1264 | 1264 | 1264 | 1264 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 53 | 35 | 28 | 39 | 59
|  |  |  | Available Total Capacity for Embedded Generation | 1084 | 1102 | 1109 | 1098 | 1078
|  |  |  | ECC Rating (A) | 1264 | 1264 | 1264 | 1264 | 1264
|  |  |  | DER Forecast (A) for N-1 Contingency | 95 | 51 | 28 | 63 | 108
|  |  |  | Available Firm Capacity for Embedded Generation | 1042 | 1086 | 1109 | 1074 | 1029
South Pine | F739 | South Pine | Bald Hills | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 20 | 40 | 60 | 81 | 99
|  |  |  | Available Total Capacity for Embedded Generation | 1420 | 1400 | 1380 | 1359 | 1341
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | DER Forecast (A) for N-1 Contingency | 46 | 87 | 127 | 167 | 205
|  |  |  | Available Firm Capacity for Embedded Generation | 1394 | 1353 | 1313 | 1273 | 1235
South Pine | F740 | South Pine | Sandgate | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 26 | 47 | 67 | 87 | 106
|  |  |  | Available Total Capacity for Embedded Generation | 1414 | 1393 | 1373 | 1353 | 1334
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | DER Forecast (A) for N-1 Contingency | 64 | 104 | 144 | 184 | 222
|  |  |  | Available Firm Capacity for Embedded Generation | 1376 | 1336 | 1296 | 1256 | 1218
South Pine | F741 | South Pine | Hays Inlet | NCC Rating (A) | 635 | 635 | 635 | 635 | 635 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 43 | 67 | 89 | 131 | 131
|  |  |  | Available Total Capacity for Embedded Generation | 528 | 504 | 482 | 440 | 440
|  |  |  | ECC Rating (A) | 635 | 635 | 635 | 635 | 635
|  |  |  | DER Forecast (A) for N-1 Contingency | 64 | 100 | 134 | 199 | 198
|  |  |  | Available Firm Capacity for Embedded Generation | 507 | 471 | 437 | 372 | 373
South Pine | F742 | South Pine | Hays Inlet | NCC Rating (A) | 635 | 635 | 635 | 635 | 635 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 43 | 67 | 89 | 130 | 130
|  |  |  | Available Total Capacity for Embedded Generation | 528 | 504 | 482 | 441 | 441
|  |  |  | ECC Rating (A) | 635 | 635 | 635 | 635 | 635
|  |  |  | DER Forecast (A) for N-1 Contingency | 64 | 100 | 134 | 199 | 197
|  |  |  | Available Firm Capacity for Embedded Generation | 507 | 471 | 437 | 372 | 374
South Pine | F7299 | South Pine | Brendale | NCC Rating (A) | 949 | 949 | 949 | 949 | 949 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 43 | 67 | 89 | 110 | 129
|  |  |  | Available Total Capacity for Embedded Generation | 811 | 787 | 765 | 744 | 725
|  |  |  | ECC Rating (A) | 949 | 949 | 949 | 949 | 949
|  |  |  | DER Forecast (A) for N-1 Contingency | 65 | 100 | 133 | 165 | 194
|  |  |  | Available Firm Capacity for Embedded Generation | 789 | 754 | 721 | 689 | 660
South Pine | F743 | South Pine | Brendale | NCC Rating (A) | 594 | 594 | 594 | 594 | 594 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 43 | 67 | 89 | 110 | 129
|  |  |  | Available Total Capacity for Embedded Generation | 491 | 467 | 445 | 424 | 405
|  |  |  | ECC Rating (A) | 594 | 594 | 594 | 594 | 594
|  |  |  | DER Forecast (A) for N-1 Contingency | 65 | 100 | 133 | 165 | 194
|  |  |  | Available Firm Capacity for Embedded Generation | 469 | 434 | 401 | 369 | 340
South Pine | F744 | South Pine | Brendale | NCC Rating (A) | 594 | 594 | 594 | 594 | 594 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 43 | 67 | 89 | 110 | 129
|  |  |  | Available Total Capacity for Embedded Generation | 491 | 467 | 445 | 424 | 405
|  |  |  | ECC Rating (A) | 594 | 594 | 594 | 594 | 594
|  |  |  | DER Forecast (A) for N-1 Contingency | 65 | 100 | 133 | 165 | 194
|  |  |  | Available Firm Capacity for Embedded Generation | 469 | 434 | 401 | 369 | 340
South Pine | F745/1 | South Pine | Moodlu | NCC Rating (A) | 768 | 768 | 768 | 768 | 768 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 38 | 32 | 51 | 70 | 90
|  |  |  | Available Total Capacity for Embedded Generation | 653 | 659 | 640 | 621 | 601
|  |  |  | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast (A) for N-1 Contingency | 167 | 128 | 152 | 206 | 250
|  |  |  | Available Firm Capacity for Embedded Generation | 524 | 563 | 539 | 485 | 441
South Pine | F746/1 | South Pine | Moodlu | NCC Rating (A) | 768 | 768 | 768 | 768 | 768 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 38 | 32 | 51 | 71 | 90
|  |  |  | Available Total Capacity for Embedded Generation | 653 | 659 | 640 | 620 | 601
|  |  |  | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast (A) for N-1 Contingency | 167 | 128 | 152 | 205 | 250
|  |  |  | Available Firm Capacity for Embedded Generation | 524 | 563 | 539 | 486 | 441
South Pine | F831 | Bald Hills | Sandgate | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 37 | 58 | 78 | 98 | 116
|  |  |  | Available Total Capacity for Embedded Generation | 1403 | 1382 | 1362 | 1342 | 1324
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | DER Forecast (A) for N-1 Contingency | 64 | 104 | 145 | 184 | 222
|  |  |  | Available Firm Capacity for Embedded Generation | 1376 | 1336 | 1295 | 1256 | 1218
South Pine | F912 | Nudgee | Meeandah | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 50 | 50 | 50 | 50 | 50
|  |  |  | Available Total Capacity for Embedded Generation | 359 | 359 | 359 | 359 | 359
|  |  |  | ECC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | DER Forecast (A) for N-1 Contingency | 62 | 61 | 61 | 62 | 62
|  |  |  | Available Firm Capacity for Embedded Generation | 347 | 348 | 348 | 347 | 347
South Pine | F913 | Nudgee | Meeandah | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | Urban | 110
|  |  |  | DER Forecast (A) for System Normal | 50 | 50 | 50 | 50 | 50
|  |  |  | Available Total Capacity for Embedded Generation | 359 | 359 | 359 | 359 | 359
|  |  |  | ECC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | DER Forecast (A) for N-1 Contingency | 62 | 61 | 61 | 62 | 62
|  |  |  | Available Firm Capacity for Embedded Generation | 347 | 348 | 348 | 347 | 347
Woolooga 132 kV | F7186 | Cooran | Cooroy | NCC Rating (A) | 734 | 734 | 734 | 734 | 734 | Rural | 132
|  |  |  | DER Forecast (A) for System Normal | 142 | 172 | 190 | 218 | 246
|  |  |  | Available Total Capacity for Embedded Generation | 518 | 488 | 470 | 442 | 414
|  |  |  | ECC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | DER Forecast (A) for N-1 Contingency | 277 | 319 | 357 | 407 | 460
|  |  |  | Available Firm Capacity for Embedded Generation | 383 | 341 | 303 | 253 | 200
Woolooga 132 kV | F7343 | Traveston | Cooran | NCC Rating (A) | 734 | 734 | 734 | 734 | 734 | Rural | 132
|  |  |  | DER Forecast (A) for System Normal | 152 | 184 | 205 | 236 | 266
|  |  |  | Available Total Capacity for Embedded Generation | 508 | 476 | 455 | 424 | 394
|  |  |  | ECC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | DER Forecast (A) for N-1 Contingency | 288 | 332 | 373 | 425 | 481
|  |  |  | Available Firm Capacity for Embedded Generation | 372 | 328 | 287 | 235 | 179
Woolooga 132 kV | F747/1 | Gympie | Traveston | NCC Rating (A) | 734 | 734 | 734 | 734 | 734 | Rural | 132
|  |  |  | DER Forecast (A) for System Normal | 138 | 170 | 191 | 222 | 252
|  |  |  | Available Total Capacity for Embedded Generation | 522 | 490 | 469 | 438 | 408
|  |  |  | ECC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | DER Forecast (A) for N-1 Contingency | 273 | 317 | 358 | 411 | 467
|  |  |  | Available Firm Capacity for Embedded Generation | 387 | 343 | 302 | 249 | 193
Woolooga 132 kV | F747/2 | Woolooga | Gympie | NCC Rating (A) | 763 | 763 | 763 | 763 | 763 | Rural | 132
|  |  |  | DER Forecast (A) for System Normal | 143 | 185 | 227 | 273 | 317
|  |  |  | Available Total Capacity for Embedded Generation | 543 | 501 | 459 | 413 | 369
|  |  |  | ECC Rating (A) | 763 | 763 | 763 | 763 | 763
|  |  |  | DER Forecast (A) for N-1 Contingency | 283 | 340 | 399 | 467 | 537
|  |  |  | Available Firm Capacity for Embedded Generation | 403 | 346 | 287 | 219 | 149
Woolooga 132 kV | F748/1 | Gympie | Cooroy | NCC Rating (A) | 734 | 734 | 734 | 734 | 734 | Rural | 132
|  |  |  | DER Forecast (A) for System Normal | 173 | 208 | 238 | 276 | 314
|  |  |  | Available Total Capacity for Embedded Generation | 487 | 452 | 422 | 384 | 346
|  |  |  | ECC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | DER Forecast (A) for N-1 Contingency | 336 | 388 | 440 | 504 | 573
|  |  |  | Available Firm Capacity for Embedded Generation | 324 | 272 | 220 | 156 | 87
Woolooga 132 kV | F748/2 | Woolooga | Gympie | NCC Rating (A) | 763 | 763 | 763 | 763 | 763 | Rural | 132
|  |  |  | DER Forecast (A) for System Normal | 170 | 219 | 258 | 306 | 353
|  |  |  | Available Total Capacity for Embedded Generation | 516 | 467 | 428 | 380 | 333
|  |  |  | ECC Rating (A) | 763 | 763 | 763 | 763 | 763
|  |  |  | DER Forecast (A) for N-1 Contingency | 330 | 395 | 456 | 530 | 607
|  |  |  | Available Firm Capacity for Embedded Generation | 356 | 291 | 230 | 156 | 79