## Notes
Sub-Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2022-23 to 2026-27)
This workbook provides 5 year forecast capacity and loading information for sub-transmission feeders in the Energex network.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation due to COVID 19 impacts. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
The following sections list the 33kV feeders and their DER forecast.
Feeder capacities are shown for ECC and NCC.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
Interconnected feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.

## 33kV Fdr DER Forecast
Feeder | Section | Item | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27
F3009 | 3009-1 | Load (A) | 16.5276 | 25.7995 | 36.6491 | 47.9532 | 58.8358
|  | Rating (A) | 704 | 704 | 704 | 704 | 704
|  | Utilisation (%) | 2.3477 | 3.6647 | 5.2058 | 6.8115 | 8.3574
|  | Hosting Capacity (A) | 687.4724 | 678.2005 | 667.3509 | 656.0468 | 645.1642
|  | Power Factor | 0.68914 | 0.88982 | 0.95021 | 0.97371 | 0.9845
|  | N-1 Load (A) | 25.6821 | 47.3115 | 70.4519 | 93.4534 | 115.8427
|  | N-1 Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Contingency Utilisation (%) | 3.648 | 6.7204 | 10.0074 | 13.3505 | 16.549
|  | N-1 Hosting Capacity (A) | 674.3179 | 652.6885 | 629.5481 | 606.5466 | 584.1573
|  | N-1 Power Factor | 0.68914 | 0.88982 | 0.95021 | 0.99307 | 0.99638
|  | N-1 Limiting section | 3009-1(1) | 3009-1(1) | 3009-1(1) | 3009-1(3) | 3009-1(3)
|  | Contingency Scenario | F3011 | F3011 | F3011 | F3011 | F3011
F3011 | 3011-1 | Load (A) | 16.5263 | 25.8027 | 36.6563 | 47.964 | 58.85
|  | Rating (A) | 704 | 704 | 704 | 704 | 704
|  | Utilisation (%) | 2.3475 | 3.6652 | 5.2069 | 6.8131 | 8.3594
|  | Hosting Capacity (A) | 687.4737 | 678.1973 | 667.3437 | 656.036 | 645.15
|  | Power Factor | 0.68935 | 0.88994 | 0.95027 | 0.97375 | 0.98452
|  | N-1 Load (A) | 25.681 | 47.311 | 70.4516 | 93.4526 | 115.8423
|  | N-1 Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Contingency Utilisation (%) | 3.6479 | 6.7203 | 10.0073 | 13.3504 | 16.5489
|  | N-1 Hosting Capacity (A) | 674.319 | 652.689 | 629.5484 | 606.5474 | 584.1577
|  | N-1 Power Factor | 0.68935 | 0.88994 | 0.95027 | 0.99311 | 0.99641
|  | N-1 Limiting section | 3011-1 | 3011-1 | 3011-1 | 3011-1(3) | 3011-1(3)
|  | Contingency Scenario | F3009 | F3009 | F3009 | F3009 | F3009
F303 | 303-1 | Load (A) | 57.3131 | 76.1629 | 95.1818 | 114.0154 | 131.715
|  | Rating (A) | 725 | 725 | 725 | 725 | 725
|  | Utilisation (%) | 7.9053 | 10.5114 | 13.1347 | 15.7263 | 18.1736
|  | Hosting Capacity (A) | 667.6869 | 648.8371 | 629.8182 | 610.9846 | 593.285
|  | Power Factor | 0.99877 | 0.9998 | 0.99925 | 0.9983 | 0.99805
|  | N-1 Load (A) | 115.9684 | 154.4146 | 193.1269 | 231.516 | 267.9339
|  | N-1 Rating (A) | 824 | 824 | 824 | 824 | 824
|  | Contingency Utilisation (%) | 15.9956 | 21.2986 | 26.6382 | 31.9332 | 36.9564
|  | N-1 Hosting Capacity (A) | 708.0316 | 669.5854 | 630.8731 | 592.484 | 556.0661
|  | N-1 Power Factor | 0.99954 | 0.99922 | 0.9988 | 0.9983 | 0.99774
|  | N-1 Limiting section | 303-1(9) | 303-1(9) | 303-1(9) | 303-1(9) | 303-1(9)
|  | Contingency Scenario | F3364 | F3364 | F3364 | F3364 | F3364
F305 | 305-1 | Load (A) | 79.3463 | 133.757 | 187.6391 | 240.0939 | 288.6059
|  | Rating (A) | 759 | 759 | 759 | 759 | 759
|  | Utilisation (%) | 10.4541 | 17.6228 | 24.7219 | 31.6329 | 38.0245
|  | Hosting Capacity (A) | 679.6537 | 625.243 | 571.3609 | 518.9061 | 470.3941
|  | Power Factor | 0.99321 | 0.99855 | 0.99978 | 0.99998 | 0.99973
|  | N-1 Load (A) | 120.4617 | 199.4528 | 279.5458 | 356.9204 | 428.191
|  | N-1 Rating (A) | 759 | 759 | 759 | 759 | 759
|  | Contingency Utilisation (%) | 15.8711 | 26.2784 | 36.8308 | 47.0251 | 56.4151
|  | N-1 Hosting Capacity (A) | 638.5383 | 559.5472 | 479.4542 | 402.0796 | 330.809
|  | N-1 Power Factor | 0.99321 | 0.99855 | 0.99978 | 0.99998 | 0.99973
|  | N-1 Limiting section | 305-1(1) | 305-1(1) | 305-1(1) | 305-1(1) | 305-1(1)
|  | Contingency Scenario | F448 | F497 | F497 | F497 | F497
F307 | 307-1 | Load (A) | 173.9252 | 187.8081 | 201.5741 | 214.5898 | 225.9912
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 21.2623 | 22.9594 | 24.6423 | 26.2335 | 27.6273
|  | Hosting Capacity (A) | 644.0748 | 630.1919 | 616.4259 | 603.4102 | 592.0088
|  | Power Factor | 0.99866 | 0.99841 | 0.9983 | 0.99833 | 0.99842
|  | N-1 Load (A) | 246.8835 | 284.4695 | 352.9964 | 423.142 | 490.8968
|  | N-1 Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Contingency Utilisation (%) | 30.1814 | 34.7762 | 43.1536 | 51.7288 | 60.0118
|  | N-1 Hosting Capacity (A) | 571.1165 | 533.5305 | 465.0036 | 394.858 | 327.1032
|  | N-1 Power Factor | 0.99866 | 0.99841 | 0.9983 | 0.99833 | 0.99842
|  | N-1 Limiting section | 307-1(1) | 307-1(1) | 307-1(1) | 307-1(1) | 307-1(1)
|  | Contingency Scenario | F489 | F3100 | F3100 | F3100 | F3100
F307 | 307-2 | Load (A) | 38.5122 | 27.9699 | 21.4748 | 22.3166 | 28.3135
|  | Rating (A) | 755 | 755 | 755 | 755 | 755
|  | Utilisation (%) | 5.101 | 3.7046 | 2.8443 | 2.9558 | 3.7501
|  | Hosting Capacity (A) | 716.4878 | 727.0301 | 733.5252 | 732.6834 | 726.6865
|  | Power Factor | 0.89304 | 0.73131 | 0.30844 | 0.28976 | 0.6338
|  | N-1 Load (A) | 54.9602 | 65.1723 | 91.124 | 115.6213 | 137.0656
|  | N-1 Rating (A) | 755 | 755 | 755 | 755 | 755
|  | Contingency Utilisation (%) | 7.2795 | 8.6321 | 12.0694 | 15.3141 | 18.1544
|  | N-1 Hosting Capacity (A) | 700.0398 | 689.8277 | 663.876 | 639.3787 | 617.9344
|  | N-1 Power Factor | 0.89304 | 0.73131 | 0.30844 | 0.28976 | 0.6338
|  | N-1 Limiting section | 307-2(1) | 307-2(1) | 307-2(1) | 307-2(1) | 307-2(1)
|  | Contingency Scenario | F3100 | F489 | F489 | F489 | F489
F307 | 307-3 | Load (A) | 208.1942 | 208.0326 | 207.8825 | 207.7498 | 207.6408
|  | Rating (A) | 680 | 680 | 680 | 680 | 680
|  | Utilisation (%) | 30.6168 | 30.593 | 30.571 | 30.5514 | 30.5354
|  | Hosting Capacity (A) | 471.8058 | 471.9674 | 472.1175 | 472.2502 | 472.3592
|  | Power Factor | 0.99931 | 0.99931 | 0.99932 | 0.99932 | 0.99932
|  | N-1 Load (A) | 269.8932 | 339.5721 | 414.2164 | 492.2555 | 569.3906
|  | N-1 Rating (A) | 680 | 680 | 680 | 680 | 680
|  | Contingency Utilisation (%) | 39.6902 | 49.9371 | 60.9142 | 72.3905 | 83.7339
|  | N-1 Hosting Capacity (A) | 410.1068 | 340.4279 | 265.7836 | 187.7445 | 110.6094
|  | N-1 Power Factor | 0.99931 | 0.99931 | 0.99932 | 0.99932 | 0.99932
|  | N-1 Limiting section | 307-3(5) | 307-3(5) | 307-3(5) | 307-3(5) | 307-3(5)
|  | Contingency Scenario | F3100 | F3100 | F3100 | F3100 | F3100
F308 | 308-1 | Load (A) | 23.3836 | 71.0786 | 122.026 | 174.9097 | 227.0037
|  | Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Utilisation (%) | 2.9981 | 9.1136 | 15.6444 | 22.4243 | 29.103
|  | Hosting Capacity (A) | 756.6164 | 708.9214 | 657.974 | 605.0903 | 552.9963
|  | Power Factor | 0.99041 | 0.99975 | 0.99911 | 0.99822 | 0.99709
|  | N-1 Load (A) | 40.2916 |  |  |  | 0.0018496
|  | N-1 Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Contingency Utilisation (%) | 5.1656 |  |  |  | 0.00023713
|  | N-1 Hosting Capacity (A) | 739.7084 | #VALUE! | #VALUE! | #VALUE! | 779.9982
|  | N-1 Power Factor | 0.99975 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 308-1(4) | 308-1(7) | 308-1(7) | 308-1(7) | 308-1(7)
|  | Contingency Scenario | F3100 |  |  |  | F3100
F308 | 308-2 | Load (A) | 23.1628 | 71.0786 | 122.0344 | 174.9213 | 227.0037
|  | Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Utilisation (%) | 2.9703 | 9.1143 | 15.6454 | 22.4258 | 29.1049
|  | Hosting Capacity (A) | 756.8372 | 708.9214 | 657.9656 | 605.0787 | 552.9963
|  | Power Factor | 0.99975 | 0.99975 | 0.99931 | 0.99869 | 0.99709
|  | N-1 Load (A) | 40.3089
|  | N-1 Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Contingency Utilisation (%) | 5.1678
|  | N-1 Hosting Capacity (A) | 739.6911 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | N-1 Power Factor | 0.99975 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 308-1(4) | 308-1(7) | 308-1(7) | 308-1(7) | 308-1(7)
|  | Contingency Scenario | F3100 |  |  |  | F3100
F309 | 309-1 | Load (A) | 50.4126 | 69.7833 | 89.1321 | 108.1293 | 125.9337
|  | Rating (A) | 627 | 627 | 627 | 627 | 627
|  | Utilisation (%) | 8.0405 | 11.1306 | 14.2171 | 17.2455 | 20.0851
|  | Hosting Capacity (A) | 576.5874 | 557.2167 | 537.8679 | 518.8707 | 501.0663
|  | Power Factor | 0.99999 | 0.99975 | 0.99928 | 0.99887 | 0.99825
|  | N-1 Load (A) | 93.8679 | 131.4994 | 169.1146 | 206.0475 | 240.7342
|  | N-1 Rating (A) | 627 | 627 | 627 | 627 | 627
|  | Contingency Utilisation (%) | 14.971 | 20.9728 | 26.972 | 32.8624 | 38.3946
|  | N-1 Hosting Capacity (A) | 533.1321 | 495.5006 | 457.8854 | 420.9525 | 386.2658
|  | N-1 Power Factor | 0.99999 | 0.99975 | 0.99928 | 0.99866 | 0.99791
|  | N-1 Limiting section | 309-1 | 309-1 | 309-1 | 309-1 | 309-1
|  | Contingency Scenario | F310 | F310 | F310 | F310 | F310
F309 | 309-2 | Load (A) | 38.072 | 48.4423 | 58.6262 | 68.3496 | 77.1421
|  | Rating (A) | 711 | 711 | 711 | 711 | 711
|  | Utilisation (%) | 5.3547 | 6.8133 | 8.2456 | 9.6132 | 10.8498
|  | Hosting Capacity (A) | 672.928 | 662.5577 | 652.3738 | 642.6504 | 633.8579
|  | Power Factor | 0.99964 | 0.99941 | 0.99911 | 0.99875 | 0.99836
|  | N-1 Load (A) | 85.6984 | 112.2052 | 138.3879 | 163.6318 | 186.7942
|  | N-1 Rating (A) | 711 | 711 | 711 | 711 | 711
|  | Contingency Utilisation (%) | 12.0532 | 15.7813 | 19.4638 | 23.0143 | 26.272
|  | N-1 Hosting Capacity (A) | 625.3016 | 598.7948 | 572.6121 | 547.3682 | 524.2058
|  | N-1 Power Factor | 0.99964 | 0.99941 | 0.99911 | 0.99875 | 0.99836
|  | N-1 Limiting section | 309-2 | 309-2 | 309-2 | 309-2 | 309-2
|  | Contingency Scenario | F464 | F464 | F464 | F464 | F464
F309 | 309-3 | Load (A) | 12.3602 | 21.3783 | 30.5596 | 39.8349 | 48.8551
|  | Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Utilisation (%) | 1.7657 | 3.054 | 4.3657 | 5.6907 | 6.9793
|  | Hosting Capacity (A) | 687.6398 | 678.6217 | 669.4404 | 660.1651 | 651.1449
|  | Power Factor | 0.99998 | 0.99986 | 0.99965 | 0.99931 | 0.99875
|  | N-1 Load (A) | 73.0907 | 107.6621 | 142.4049 | 176.814 | 209.4879
|  | N-1 Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Contingency Utilisation (%) | 10.4415 | 15.3803 | 20.3436 | 25.2591 | 29.9268
|  | N-1 Hosting Capacity (A) | 626.9093 | 592.3379 | 557.5951 | 523.186 | 490.5121
|  | N-1 Power Factor | 0.99998 | 0.99986 | 0.99965 | 0.99931 | 0.99875
|  | N-1 Limiting section | 309-3 | 309-3 | 309-3 | 309-3 | 309-3
|  | Contingency Scenario | F310 | F310 | F310 | F310 | F310
F310 | 310-1 | Load (A) | 61.0625 | 86.9436 | 112.8936 | 138.5069 | 162.7061
|  | Rating (A) | 627 | 627 | 627 | 627 | 627
|  | Utilisation (%) | 9.7393 | 13.8677 | 18.007 | 22.0925 | 25.9525
|  | Hosting Capacity (A) | 565.9375 | 540.0564 | 514.1064 | 488.4931 | 464.2939
|  | Power Factor | 0.99994 | 0.99957 | 0.99898 | 0.99823 | 0.99731
|  | N-1 Load (A) | 80.3691 | 112.769 | 145.1637 | 178.0367 | 211.1132
|  | N-1 Rating (A) | 627 | 627 | 627 | 627 | 627
|  | Contingency Utilisation (%) | 12.818 | 17.9855 | 23.1521 | 28.395 | 33.6704
|  | N-1 Hosting Capacity (A) | 546.6309 | 514.231 | 481.8363 | 448.9633 | 415.8868
|  | N-1 Power Factor | 0.99994 | 0.99964 | 0.99898 | 0.99866 | 0.99731
|  | N-1 Limiting section | 310-1 | 310-1(11) | 310-1 | 310-1(13) | 310-1
|  | Contingency Scenario | F464 | F464 | F464 | F309 | F309
F310 | 310-2 | Load (A) | 61.0717 | 86.9637 | 112.9233 | 138.5453 | 162.7531
|  | Rating (A) | 792 | 792 | 792 | 792 | 792
|  | Utilisation (%) | 7.7111 | 10.9803 | 14.258 | 17.4931 | 20.5496
|  | Hosting Capacity (A) | 730.9283 | 705.0363 | 679.0767 | 653.4547 | 629.2469
|  | Power Factor | 0.99988 | 0.99967 | 0.99937 | 0.99901 | 0.99856
|  | N-1 Load (A) | 80.3785 | 112.7854 | 145.1867 | 178.0633 | 211.1449
|  | N-1 Rating (A) | 792 | 792 | 792 | 792 | 792
|  | Contingency Utilisation (%) | 10.1488 | 14.2406 | 18.3317 | 22.4827 | 26.6597
|  | N-1 Hosting Capacity (A) | 711.6215 | 679.2146 | 646.8133 | 613.9367 | 580.8551
|  | N-1 Power Factor | 0.99988 | 0.99967 | 0.99937 | 0.99901 | 0.99856
|  | N-1 Limiting section | 310-2 | 310-2 | 310-2 | 310-2 | 310-2
|  | Contingency Scenario | F464 | F464 | F464 | F309 | F309
F3100 | 3100-1 | Load (A) | 64.8118 | 137.9402 | 216.4174 | 298.3253 | 378.9288
|  | Rating (A) | 793 | 793 | 793 | 793 | 793
|  | Utilisation (%) | 8.173 | 17.3947 | 27.291 | 37.6198 | 47.7842
|  | Hosting Capacity (A) | 728.1882 | 655.0598 | 576.5826 | 494.6747 | 414.0712
|  | Power Factor | 0.99907 | 0.9998 | 0.9982 | 0.99529 | 0.99146
F3100 | 3100-2 | Load (A) | 64.8013 | 137.9464 | 216.4412 | 298.3652 | 378.9831
|  | Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Utilisation (%) | 8.3079 | 17.6854 | 27.7489 | 38.252 | 48.5877
|  | Hosting Capacity (A) | 715.1987 | 642.0536 | 563.5588 | 481.6348 | 401.0169
|  | Power Factor | 0.99918 | 0.9998 | 0.9982 | 0.99529 | 0.99146
F311 | 311-1 | Load (A) | 26.1154 | 44.1816 | 62.039 | 79.4113 | 95.4681
|  | Rating (A) | 623 | 623 | 623 | 623 | 623
|  | Utilisation (%) | 4.1919 | 7.0918 | 9.9581 | 12.7466 | 15.3239
|  | Hosting Capacity (A) | 596.8846 | 578.8184 | 560.961 | 543.5887 | 527.5319
|  | Power Factor | 0.99993 | 0.99941 | 0.99844 | 0.9972 | 0.99596
|  | N-1 Load (A) | 86.8094 | 146.9045 | 206.1772 | 263.718 | 316.8728
|  | N-1 Rating (A) | 623 | 623 | 623 | 623 | 623
|  | Contingency Utilisation (%) | 13.9341 | 23.5802 | 33.0943 | 42.3303 | 50.8624
|  | N-1 Hosting Capacity (A) | 536.1906 | 476.0955 | 416.8228 | 359.282 | 306.1272
|  | N-1 Power Factor | 0.99993 | 0.99941 | 0.99844 | 0.9972 | 0.99596
|  | N-1 Limiting section | 311-1 | 311-1 | 311-1 | 311-1 | 311-1
|  | Contingency Scenario | F305 | F305 | F305 | F305 | F305
F320 | 320-1 | Load (A) | 9.6533 | 18.9552 | 44.5615 | 70.1953 | 92.9323
|  | Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Utilisation (%) | 1.379 | 2.7079 | 6.3659 | 10.0306 | 13.276
|  | Hosting Capacity (A) | 690.3467 | 681.0448 | 655.4385 | 629.8047 | 607.0677
|  | Power Factor | 0.76482 | 0.96865 | 0.99834 | 0.99759 | 0.99645
|  | N-1 Load (A) | 28.4046 | 72.9769 | 118.4827 | 162.4937 | 201.2461
|  | N-1 Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Contingency Utilisation (%) | 4.0578 | 10.4253 | 16.9261 | 23.2134 | 28.7494
|  | N-1 Hosting Capacity (A) | 671.5954 | 627.0231 | 581.5173 | 537.5063 | 498.7539
|  | N-1 Power Factor | 0.76482 | 0.9997 | 0.99842 | 0.99759 | 0.99645
|  | N-1 Limiting section | 320-1(4) | 320-1(8) | 320-1(8) | 320-1(1) | 320-1(8)
|  | Contingency Scenario | F327 | F327 | F327 | F327 | F327
F320 | 320-2 | Load (A) | 33.0653 | 9.9609 | 13.9499 | 36.235 | 55.5113
|  | Rating (A) | 495 | 495 | 495 | 495 | 495
|  | Utilisation (%) | 6.6798 | 2.0123 | 2.8182 | 7.3202 | 11.2144
|  | Hosting Capacity (A) | 461.9347 | 485.0391 | 481.0501 | 458.765 | 439.4887
|  | Power Factor | 0.9911 | 0.96922 | 0.99982 | 0.99601 | 0.99373
|  | N-1 Load (A) | 50.7382 | 79.1262 | 134.2948 | 186.5348 | 231.9635
|  | N-1 Rating (A) | 495 | 495 | 495 | 495 | 495
|  | Contingency Utilisation (%) | 10.2501 | 15.9851 | 27.1303 | 37.6838 | 46.8613
|  | N-1 Hosting Capacity (A) | 444.2618 | 415.8738 | 360.7052 | 308.4652 | 263.0365
|  | N-1 Power Factor | 0.9911 | 0.96922 | 0.99982 | 0.99601 | 0.99373
|  | N-1 Limiting section | 320-2(1) | 320-2(1) | 320-2(1) | 320-2(1) | 320-2(1)
|  | Contingency Scenario | F3359 | F327 | F327 | F327 | F327
F320 | 320-3 | Load (A) | 25.6235 | 28.1697 | 30.6375 | 34.0013 | 37.491
|  | Rating (A) | 495 | 495 | 495 | 495 | 495
|  | Utilisation (%) | 5.1765 | 5.692 | 6.1903 | 6.8696 | 7.5744
|  | Hosting Capacity (A) | 469.3765 | 466.8303 | 464.3625 | 460.9987 | 457.509
|  | Power Factor | 0.99098 | 0.99455 | 0.99697 | 0.99841 | 0.99909
|  | N-1 Load (A) | 41.5988 | 50.2784 | 67.5462 | 85.7453 | 102.5479
|  | N-1 Rating (A) | 495 | 495 | 495 | 495 | 495
|  | Contingency Utilisation (%) | 8.4038 | 10.1573 | 13.6457 | 17.3223 | 20.7167
|  | N-1 Hosting Capacity (A) | 453.4012 | 444.7216 | 427.4538 | 409.2547 | 392.4521
|  | N-1 Power Factor | 0.9912 | 0.99455 | 0.99697 | 0.99841 | 0.99909
|  | N-1 Limiting section | 320-3 | 320-3 | 320-3 | 320-3 | 320-3
|  | Contingency Scenario | F3331 | F3329 | F3329 | F3329 | F3329
F321 | 321-1 | Load (A) | 36.7855 | 61.8274 | 87.3267 | 112.3133 | 135.2703
|  | Rating (A) | 509 | 509 | 509 | 509 | 509
|  | Utilisation (%) | 7.227 | 12.1468 | 17.1618 | 22.0727 | 26.5757
|  | Hosting Capacity (A) | 472.2145 | 447.1726 | 421.6733 | 396.6867 | 373.7297
|  | Power Factor | 0.99992 | 0.99963 | 0.99896 | 0.99793 | 0.99735
|  | N-1 Load (A) | 57.4903 | 96.6053 | 136.4566 | 175.4651 | 211.2205
|  | N-1 Rating (A) | 509 | 509 | 509 | 509 | 509
|  | Contingency Utilisation (%) | 11.2948 | 18.9794 | 26.8088 | 34.4725 | 41.4972
|  | N-1 Hosting Capacity (A) | 451.5097 | 412.3947 | 372.5434 | 333.5349 | 297.7795
|  | N-1 Power Factor | 0.99992 | 0.99974 | 0.99897 | 0.99793 | 0.99735
|  | N-1 Limiting section | 321-1 | 321-1 | 321-1(7) | 321-1 | 321-1(7)
|  | Contingency Scenario | F322 | F322 | F322 | F322 | F322
F322 | 322-1 | Load (A) | 38.6807 | 64.9934 | 91.8174 | 118.0865 | 142.2042
|  | Rating (A) | 509 | 509 | 509 | 509 | 509
|  | Utilisation (%) | 7.5994 | 12.7689 | 18.0406 | 23.2037 | 27.938
|  | Hosting Capacity (A) | 470.3193 | 444.0066 | 417.1826 | 390.9135 | 366.7958
|  | Power Factor | 0.99899 | 0.99995 | 0.99992 | 0.99952 | 0.9992
|  | N-1 Load (A) | 58.831 | 98.8504 | 139.6396 | 179.5706 | 216.1758
|  | N-1 Rating (A) | 509 | 509 | 509 | 509 | 509
|  | Contingency Utilisation (%) | 11.5582 | 19.4205 | 27.4341 | 35.2791 | 42.4707
|  | N-1 Hosting Capacity (A) | 450.169 | 410.1496 | 369.3604 | 329.4294 | 292.8242
|  | N-1 Power Factor | 0.99899 | 0.99995 | 0.99992 | 0.99961 | 0.9992
|  | N-1 Limiting section | 322-1 | 322-1 | 322-1 | 322-1(11) | 322-1(11)
|  | Contingency Scenario | F321 | F321 | F321 | F321 | F321
F323 | 323-1 | Load (A) | 19.4748 | 30.4109 | 41.4284 | 52.1551 | 61.9592
|  | Rating (A) | 510 | 510 | 510 | 510 | 510
|  | Utilisation (%) | 3.8186 | 5.9629 | 8.1232 | 10.2265 | 12.1489
|  | Hosting Capacity (A) | 490.5252 | 479.5891 | 468.5716 | 457.8449 | 448.0408
|  | Power Factor | 0.99667 | 0.99934 | 0.99995 | 0.99995 | 0.99969
|  | N-1 Load (A) | 0.46323 | 0.46411 | 0.46489 | 0.4656 | 0.46621
|  | N-1 Rating (A) | 510 | 510 | 510 | 510 | 510
|  | Contingency Utilisation (%) | 0.065799 | 0.065925 | 0.066036 | 0.066137 | 0.066223
|  | N-1 Hosting Capacity (A) | 509.5368 | 509.5359 | 509.5351 | 509.5344 | 509.5338
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 323-1(4) | 323-1(4) | 323-1(4) | 323-1(4) | 323-1(4)
|  | Contingency Scenario | F321 | F322 | F322 | F322 | F322
F323 | 323-2 | Load (A) | 19.4079 | 30.394 | 41.4435 | 52.1965 | 62.0208
|  | Rating (A) | 457 | 457 | 457 | 457 | 457
|  | Utilisation (%) | 4.2468 | 6.6508 | 9.0686 | 11.4216 | 13.5713
|  | Hosting Capacity (A) | 437.5921 | 426.606 | 415.5565 | 404.8035 | 394.9792
|  | Power Factor | 0.99987 | 0.99974 | 0.99955 | 0.99927 | 0.99898
F324 | 324-1 | Load (A) | 14.4744 | 4.374 | 3.1305 | 7.1017 | 10.8569
|  | Rating (A) | 348 | 348 | 348 | 348 | 348
|  | Utilisation (%) | 4.1614 | 1.2569 | 0.89957 | 2.0407 | 3.1198
|  | Hosting Capacity (A) | 333.5256 | 343.626 | 344.8695 | 340.8983 | 337.1431
|  | Power Factor | 0.99194 | 0.7083 | 0.93342 | 0.9433 | 0.94471
|  | N-1 Load (A) | 14.3865
|  | N-1 Rating (A) | 348 | 348 | 348 | 348 | 348
|  | Contingency Utilisation (%) | 4.1341
|  | N-1 Hosting Capacity (A) | 333.6135 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | N-1 Power Factor | 0.99905 | 1 | 1 | 0.99999 | 1
|  | N-1 Limiting section | 324-1(5) | 324-1(3) | 324-1(3) | 324-1(3) | 324-1(3)
|  | Contingency Scenario | F447
F325 | 325-1 | Load (A) | 14.5991 | 7.4623 | 29.8679 | 52.4835 | 74.0383
|  | Rating (A) | 529 | 529 | 529 | 529 | 529
|  | Utilisation (%) | 2.7598 | 1.4106 | 5.6461 | 9.9213 | 13.9959
|  | Hosting Capacity (A) | 514.4009 | 521.5377 | 499.1321 | 476.5165 | 454.9617
|  | Power Factor | 0.99823 | 0.97435 | 0.99581 | 0.99707 | 0.99711
|  | N-1 Load (A) | 42.6781 | 73.7826 | 105.6527 | 137.5162 | 167.6583
|  | N-1 Rating (A) | 529 | 529 | 529 | 529 | 529
|  | Contingency Utilisation (%) | 8.0677 | 13.9476 | 19.9722 | 25.9955 | 31.6934
|  | N-1 Hosting Capacity (A) | 486.3219 | 455.2174 | 423.3473 | 391.4838 | 361.3417
|  | N-1 Power Factor | 0.99823 | 0.97435 | 0.99581 | 0.99707 | 0.99711
|  | N-1 Limiting section | 325-1(2) | 325-1(2) | 325-1(2) | 325-1(2) | 325-1(2)
|  | Contingency Scenario | F326 | F326 | F326 | F326 | F326
F3250 | 3250-1 | Load (A) | 56.856 | 88.1011 | 117.7257 | 145.9273 | 171.6749
|  | Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Utilisation (%) | 7.9742 | 12.3564 | 16.5113 | 20.4667 | 24.0778
|  | Hosting Capacity (A) | 656.144 | 624.8989 | 595.2743 | 567.0727 | 541.3251
|  | Power Factor | 1 | 0.99981 | 0.99943 | 0.99892 | 0.99839
|  | N-1 Load (A) | 111.9878 | 175.7556 | 240.2951 | 301.6999 | 357.8222
|  | N-1 Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Contingency Utilisation (%) | 15.7066 | 24.6501 | 33.702 | 42.3141 | 50.1854
|  | N-1 Hosting Capacity (A) | 601.0122 | 537.2444 | 472.7049 | 411.3001 | 355.1778
|  | N-1 Power Factor | 1 | 0.99981 | 0.99943 | 0.99892 | 0.99839
|  | N-1 Limiting section | 3250-1 | 3250-1 | 3250-1 | 3250-1 | 3250-1
|  | Contingency Scenario | F448 | F497 | F497 | F497 | F497
F326 | 326-1 | Load (A) | 57.3608 | 66.7315 | 76.2606 | 85.6806 | 94.4643
|  | Rating (A) | 322 | 322 | 322 | 322 | 322
|  | Utilisation (%) | 17.8139 | 20.7241 | 23.6834 | 26.6089 | 29.3367
|  | Hosting Capacity (A) | 264.6392 | 255.2685 | 245.7394 | 236.3194 | 227.5357
|  | Power Factor | 1 | 0.99999 | 0.99998 | 0.99999 | 0.99999
|  | N-1 Load (A) | 73.8313 | 80.9679 | 105.9532 | 137.8805 | 168.0807
|  | N-1 Rating (A) | 322 | 322 | 322 | 322 | 322
|  | Contingency Utilisation (%) | 22.929 | 25.1453 | 32.9047 | 42.82 | 52.199
|  | N-1 Hosting Capacity (A) | 248.1687 | 241.0321 | 216.0468 | 184.1195 | 153.9193
|  | N-1 Power Factor | 1 | 0.99999 | 0.99998 | 0.99999 | 0.99999
|  | N-1 Limiting section | 326-1 | 326-1 | 326-1 | 326-1 | 326-1
|  | Contingency Scenario | F329 | F329 | F325 | F325 | F325
F327 | 327-1 | Load (A) | 99.4685 | 152.2234 | 206.4075 | 258.1267 | 303.458
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 12.16 | 18.6092 | 25.2332 | 31.5558 | 37.0975
|  | Hosting Capacity (A) | 718.5315 | 665.7766 | 611.5925 | 559.8733 | 514.542
|  | Power Factor | 0.99879 | 0.99702 | 0.99441 | 0.99119 | 0.98776
F3280 | 3280-1 | Load (A) | 31.3158 | 28.9721 | 26.3198 | 23.4149 | 20.4685
|  | Rating (A) | 725 | 725 | 725 | 725 | 725
|  | Utilisation (%) | 4.3194 | 3.9962 | 3.6303 | 3.2296 | 2.8232
|  | Hosting Capacity (A) | 693.6842 | 696.0279 | 698.6802 | 701.5851 | 704.5315
|  | Power Factor | 0.98533 | 0.98242 | 0.97804 | 0.97137 | 0.96141
|  | N-1 Load (A) | 62.0438 | 57.2663 | 51.8449 | 45.8886 | 39.8029
|  | N-1 Rating (A) | 725 | 725 | 725 | 725 | 725
|  | Contingency Utilisation (%) | 8.5578 | 7.8988 | 7.151 | 6.3295 | 5.4901
|  | N-1 Hosting Capacity (A) | 662.9562 | 667.7337 | 673.1551 | 679.1114 | 685.1971
|  | N-1 Power Factor | 0.98533 | 0.98242 | 0.97804 | 0.97137 | 0.96141
|  | N-1 Limiting section | 3280-1 | 3280-1 | 3280-1 | 3280-1 | 3280-1
|  | Contingency Scenario | F636 | F636 | F636 | F636 | F636
F329 | 329-1 | Load (A) | 37.4707 | 32.3813 | 26.8195 | 20.9272 | 15.1057
|  | Rating (A) | 578 | 578 | 578 | 578 | 578
|  | Utilisation (%) | 6.4828 | 5.6023 | 4.64 | 3.6206 | 2.6134
|  | Hosting Capacity (A) | 540.5293 | 545.6187 | 551.1805 | 557.0728 | 562.8943
|  | Power Factor | 0.99953 | 0.99964 | 0.99976 | 0.9999 | 1
|  | N-1 Load (A) | 66.2362 | 65.8449 | 65.057 | 63.8807 | 62.4526
|  | N-1 Rating (A) | 578 | 578 | 578 | 578 | 578
|  | Contingency Utilisation (%) | 11.4596 | 11.3919 | 11.2555 | 11.052 | 10.8049
|  | N-1 Hosting Capacity (A) | 511.7638 | 512.1551 | 512.943 | 514.1193 | 515.5474
|  | N-1 Power Factor | 0.99953 | 0.99964 | 0.99976 | 0.9999 | 1
|  | N-1 Limiting section | 329-1(2) | 329-1(2) | 329-1(2) | 329-1(2) | 329-1(2)
|  | Contingency Scenario | F326 | F326 | F326 | F326 | F326
F3290 | 3290-1 | Load (A) | 25.6919 | 33.1151 | 40.8692 | 48.8194 | 56.5887
|  | Rating (A) | 853 | 853 | 853 | 853 | 853
|  | Utilisation (%) | 3.0119 | 3.8822 | 4.7912 | 5.7233 | 6.6341
|  | Hosting Capacity (A) | 827.3081 | 819.8849 | 812.1308 | 804.1806 | 796.4113
|  | Power Factor | 0.95541 | 0.97512 | 0.98517 | 0.99081 | 0.99411
|  | N-1 Load (A) | 49.4473 | 64.7014 | 80.4652 | 96.6225 | 112.3957
|  | N-1 Rating (A) | 853 | 853 | 853 | 853 | 853
|  | Contingency Utilisation (%) | 5.7969 | 7.5852 | 9.4332 | 11.3274 | 13.1765
|  | N-1 Hosting Capacity (A) | 803.5527 | 788.2986 | 772.5348 | 756.3775 | 740.6043
|  | N-1 Power Factor | 0.95541 | 0.97512 | 0.98517 | 0.9998 | 0.99969
|  | N-1 Limiting section | 3290-1(2) | 3290-1(2) | 3290-1(2) | 3290-1(6) | 3290-1(6)
|  | Contingency Scenario | F342 | F342 | F342 | F342 | F342
F330 | 330-1 | Load (A) | 12.4948 | 5.7766 | 24.3126 | 42.8344 | 60.4124
|  | Rating (A) | 543 | 543 | 543 | 543 | 543
|  | Utilisation (%) | 2.3011 | 1.0638 | 4.4775 | 7.8885 | 11.1257
|  | Hosting Capacity (A) | 530.5052 | 537.2234 | 518.6874 | 500.1656 | 482.5876
|  | Power Factor | 0.99907 | 0.99109 | 0.99869 | 0.99895 | 0.99888
|  | N-1 Load (A) | 26.8324 | 21.8618 | 38.3827 | 67.6055 | 95.3252
|  | N-1 Rating (A) | 578 | 578 | 578 | 578 | 578
|  | Contingency Utilisation (%) | 4.9415 | 4.0261 | 7.0686 | 12.4504 | 17.5553
|  | N-1 Hosting Capacity (A) | 551.1676 | 556.1382 | 539.6173 | 510.3945 | 482.6748
|  | N-1 Power Factor | 0.99907 | 0.99109 | 0.99869 | 0.99895 | 0.99888
|  | N-1 Limiting section | 330-1 | 330-1 | 330-1 | 330-1 | 330-1
|  | Contingency Scenario | F326 | F329 | F331 | F331 | F331
F3302 | 3302-1 | Load (A) | 120.8195 | 117.763 | 115.3887 | 113.5342 | 112.1525
|  | Rating (A) | 650 | 650 | 650 | 650 | 650
|  | Utilisation (%) | 18.5876 | 18.1174 | 17.7521 | 17.4668 | 17.2542
|  | Hosting Capacity (A) | 529.1805 | 532.237 | 534.6113 | 536.4658 | 537.8475
|  | Power Factor | 0.99919 | 0.9992 | 0.99922 | 0.99924 | 0.99926
|  | N-1 Load (A) | 242.5242 | 236.3574 | 231.5679 | 227.8269 | 225.0394
|  | N-1 Rating (A) | 650 | 650 | 650 | 650 | 650
|  | Contingency Utilisation (%) | 37.3114 | 36.3627 | 35.6258 | 35.0503 | 34.6215
|  | N-1 Hosting Capacity (A) | 407.4758 | 413.6426 | 418.4321 | 422.1731 | 424.9606
|  | N-1 Power Factor | 0.99919 | 0.9992 | 0.99922 | 0.99924 | 0.99926
|  | N-1 Limiting section | 3302-1(1) | 3302-1(1) | 3302-1(1) | 3302-1(1) | 3302-1(1)
|  | Contingency Scenario | F3303 | F3303 | F3303 | F3303 | F3303
F3303 | 3303-1 | Load (A) | 120.5545 | 117.5047 | 115.1357 | 113.2852 | 111.9066
|  | Rating (A) | 600 | 600 | 600 | 600 | 600
|  | Utilisation (%) | 20.0924 | 19.5841 | 19.1893 | 18.8809 | 18.6511
|  | Hosting Capacity (A) | 479.4455 | 482.4953 | 484.8643 | 486.7148 | 488.0934
|  | Power Factor | 0.99918 | 0.9992 | 0.99921 | 0.99923 | 0.99926
|  | N-1 Load (A) | 242.5278 | 236.3608 | 231.571 | 227.8299 | 225.0424
|  | N-1 Rating (A) | 600 | 600 | 600 | 600 | 600
|  | Contingency Utilisation (%) | 40.4213 | 39.3935 | 38.5952 | 37.9717 | 37.5071
|  | N-1 Hosting Capacity (A) | 357.4722 | 363.6392 | 368.429 | 372.1701 | 374.9576
|  | N-1 Power Factor | 0.99918 | 0.9992 | 0.99921 | 0.99923 | 0.99926
|  | N-1 Limiting section | 3303-1(6) | 3303-1(6) | 3303-1(6) | 3303-1(6) | 3303-1(6)
|  | Contingency Scenario | F3302 | F3302 | F3302 | F3302 | F3302
F331 | 331-1 | Load (A) | 12.5617 | 5.7999 | 24.4359 | 43.0552 | 60.7255
|  | Rating (A) | 543 | 430 | 430 | 430 | 430
|  | Utilisation (%) | 2.3134 | 1.3488 | 5.6828 | 10.0128 | 14.1222
|  | Hosting Capacity (A) | 530.4383 | 424.2001 | 405.5641 | 386.9448 | 369.2745
|  | Power Factor | 0.99837 | 0.99376 | 0.99944 | 0.99959 | 0.99954
|  | N-1 Load (A) | 26.9749 | 21.9731 | 38.4636 | 67.7514 | 95.5338
|  | N-1 Rating (A) | 573 | 573 | 573 | 573 | 573
|  | Contingency Utilisation (%) | 4.9678 | 5.11 | 8.945 | 15.7561 | 22.2172
|  | N-1 Hosting Capacity (A) | 546.0251 | 551.0269 | 534.5364 | 505.2486 | 477.4662
|  | N-1 Power Factor | 0.99837 | 0.99376 | 0.99944 | 0.99959 | 0.99954
|  | N-1 Limiting section | 331-1 | 331-1(8) | 331-1(8) | 331-1(8) | 331-1(8)
|  | Contingency Scenario | F326 | F329 | F330 | F330 | F330
F332 | 332-1 | Load (A) | 32.2176 | 13.9564 | 4.8873 | 23.8709 | 42.0238
|  | Rating (A) | 524 | 524 | 524 | 524 | 524
|  | Utilisation (%) | 6.1484 | 2.6634 | 0.93269 | 4.5555 | 8.0198
|  | Hosting Capacity (A) | 491.7824 | 510.0436 | 519.1127 | 500.1291 | 481.9762
|  | Power Factor | 0.99891 | 0.99868 | 0.99939 | 0.99998 | 0.99999
|  | N-1 Load (A) | 60.9596 | 47.3813 | 33.3071 | 50.0047 | 78.8497
|  | N-1 Rating (A) | 524 | 524 | 524 | 524 | 524
|  | Contingency Utilisation (%) | 11.6335 | 9.0422 | 6.3563 | 9.5429 | 15.0477
|  | N-1 Hosting Capacity (A) | 463.0404 | 476.6187 | 490.6929 | 473.9953 | 445.1503
|  | N-1 Power Factor | 0.99891 | 0.99868 | 0.99939 | 0.99998 | 0.99999
|  | N-1 Limiting section | 332-1(2) | 332-1(2) | 332-1(2) | 332-1(2) | 332-1(2)
|  | Contingency Scenario | F326 | F326 | F326 | F325 | F325
F3329 | 3329-1 | Load (A) | 15.8457 | 38.9876 | 63.891 | 89.2109 | 112.0682
|  | Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Utilisation (%) | 2.2637 | 5.5697 | 9.1273 | 12.7444 | 16.0098
|  | Hosting Capacity (A) | 684.1543 | 661.0124 | 636.109 | 610.7891 | 587.9318
|  | Power Factor | 0.81576 | 0.97732 | 0.99429 | 0.99843 | 0.99965
|  | N-1 Load (A) | 37.1754 | 69.0298 | 101.6216 | 133.6539 | 163.292
|  | N-1 Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Contingency Utilisation (%) | 5.3108 | 9.8614 | 14.5174 | 19.0934 | 23.3274
|  | N-1 Hosting Capacity (A) | 662.8246 | 630.9702 | 598.3784 | 566.3461 | 536.708
|  | N-1 Power Factor | 0.81576 | 0.97732 | 0.99429 | 0.99843 | 0.99965
|  | N-1 Limiting section | 3329-1(2) | 3329-1(2) | 3329-1(2) | 3329-1(2) | 3329-1(2)
|  | Contingency Scenario | F3331 | F3331 | F3331 | F3331 | F3331
F3329 | 3329-3 | Load (A) | 13.6359 | 38.2562 | 63.5547 | 89.0671 | 112.0406
|  | Rating (A) | 711 | 711 | 711 | 711 | 711
|  | Utilisation (%) | 1.9162 | 5.3802 | 8.9386 | 12.527 | 15.7589
|  | Hosting Capacity (A) | 697.3641 | 672.7438 | 647.4453 | 621.9329 | 598.9594
|  | Power Factor | 0.94786 | 0.9959 | 0.99947 | 0.99999 | 0.99989
|  | N-1 Load (A) | 36.2488 | 68.6156 | 101.428 | 133.5937 | 163.3254
|  | N-1 Rating (A) | 711 | 711 | 711 | 711 | 711
|  | Contingency Utilisation (%) | 5.0983 | 9.6506 | 14.2655 | 18.7895 | 22.9712
|  | N-1 Hosting Capacity (A) | 674.7512 | 642.3844 | 609.572 | 577.4063 | 547.6746
|  | N-1 Power Factor | 0.94786 | 0.9959 | 0.99947 | 0.99999 | 0.99989
|  | N-1 Limiting section | 3329-1(5) | 3329-1(5) | 3329-1(5) | 3329-1(5) | 3329-1(5)
|  | Contingency Scenario | F3331 | F3331 | F3331 | F3331 | F3331
F333 | 333-1 | Load (A) | 18.7608 | 38.16 | 58.1704 | 77.5858 | 95.944
|  | Rating (A) | 732 | 732 | 732 | 732 | 732
|  | Utilisation (%) | 2.5635 | 5.2139 | 7.9478 | 10.6005 | 13.1087
|  | Hosting Capacity (A) | 713.2392 | 693.84 | 673.8296 | 654.4142 | 636.056
|  | Power Factor | 0.99994 | 0.99977 | 0.99954 | 0.99922 | 0.99884
|  | N-1 Load (A) | 32.8161 | 66.6993 | 101.6167 | 135.4672 | 167.4516
|  | N-1 Rating (A) | 732 | 732 | 732 | 732 | 732
|  | Contingency Utilisation (%) | 4.4831 | 9.1119 | 13.8821 | 18.5065 | 22.8759
|  | N-1 Hosting Capacity (A) | 699.1839 | 665.3007 | 630.3833 | 596.5328 | 564.5484
|  | N-1 Power Factor | 0.99994 | 0.99977 | 0.99954 | 0.99924 | 0.99901
|  | N-1 Limiting section | 333-1(11) | 333-1(11) | 333-1(11) | 333-1(2) | 333-1(4)
|  | Contingency Scenario | F349 | F349 | F349 | F349 | F349
F3330 | 3330-1 | Load (A) | 4.913 | 14.1596 | 26.628 | 39.5151 | 50.9293
|  | Rating (A) | 843 | 717 | 717 | 717 | 717
|  | Utilisation (%) | 0.5828 | 1.9748 | 3.7138 | 5.5112 | 7.1031
|  | Hosting Capacity (A) | 838.087 | 702.8404 | 690.372 | 677.4849 | 666.0707
|  | Power Factor | 0.30853 | 0.98958 | 0.99962 | 0.99979 | 0.99893
|  | N-1 Load (A) | 10.05 | 30.1154 | 53.1191 | 76.598 | 97.5381
|  | N-1 Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Contingency Utilisation (%) | 1.4017 | 4.2002 | 7.4085 | 10.6831 | 13.6036
|  | N-1 Hosting Capacity (A) | 706.95 | 686.8846 | 663.8809 | 640.402 | 619.4619
|  | N-1 Power Factor | 0.44151 | 0.98958 | 0.99962 | 0.99979 | 0.99893
|  | N-1 Limiting section | 3330-1(1) | 3330-1(1) | 3330-1(1) | 3330-1(1) | 3330-1(1)
|  | Contingency Scenario | F320 | F3329 | F3329 | F3329 | F3329
F3330 | 3330-3 | Load (A) | 3.8522 | 14.1596 | 26.628 | 39.5151 | 50.9691
|  | Rating (A) | 843 | 717 | 717 | 717 | 717
|  | Utilisation (%) | 0.46334 | 1.9724 | 3.7134 | 5.5143 | 7.1087
|  | Hosting Capacity (A) | 839.1478 | 702.8404 | 690.372 | 677.4849 | 666.0309
|  | Power Factor | 0.39349 | 0.98958 | 0.99962 | 0.99979 | 0.99828
|  | N-1 Load (A) | 10.0302 | 30.0984 | 53.1125 | 76.5963 | 97.5456
|  | N-1 Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Contingency Utilisation (%) | 1.3989 | 4.1978 | 7.4076 | 10.6829 | 13.6047
|  | N-1 Hosting Capacity (A) | 706.9698 | 686.9016 | 663.8875 | 640.4037 | 619.4544
|  | N-1 Power Factor | 0.44151 | 0.98958 | 0.99962 | 0.99979 | 0.99893
|  | N-1 Limiting section | 3330-1(1) | 3330-1(1) | 3330-1(1) | 3330-1(1) | 3330-1(1)
|  | Contingency Scenario | F320 | F3329 | F3329 | F3329 | F3329
F3331 | 3331-1 | Load (A) | 38.929 | 51.445 | 64.0913 | 75.3443 | 86.7871
|  | Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Utilisation (%) | 5.4294 | 7.175 | 8.9388 | 10.5083 | 12.1042
|  | Hosting Capacity (A) | 678.071 | 665.555 | 652.9087 | 641.6557 | 630.2129
|  | Power Factor | 0.99915 | 0.9987 | 0.99818 | 0.99753 | 0.99697
|  | N-1 Load (A) | 47.3828 | 67.1543 | 90.3606 | 112.2209 | 133.2001
|  | N-1 Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Contingency Utilisation (%) | 6.6085 | 9.366 | 12.6026 | 15.6515 | 18.5774
|  | N-1 Hosting Capacity (A) | 669.6172 | 649.8457 | 626.6394 | 604.7791 | 583.7999
|  | N-1 Power Factor | 0.99915 | 0.9987 | 0.99818 | 0.99753 | 0.99697
|  | N-1 Limiting section | 3331-1 | 3331-1 | 3331-1 | 3331-1 | 3331-1
|  | Contingency Scenario | F320 | F3329 | F3329 | F3329 | F3329
F3331 | 3331-2 | Load (A) | 37.5321 | 37.5193 | 37.5072 | 35.8053 | 35.796
|  | Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Utilisation (%) | 5.2346 | 5.2328 | 5.2311 | 4.9938 | 4.9925
|  | Hosting Capacity (A) | 679.4679 | 679.4807 | 679.4928 | 681.1947 | 681.204
|  | Power Factor | 0.99593 | 0.99592 | 0.99592 | 0.99551 | 0.99551
|  | N-1 Load (A) | 37.5363 | 37.5198 | 37.5077 | 35.807 | 35.8003
|  | N-1 Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Contingency Utilisation (%) | 5.2352 | 5.2329 | 5.2312 | 4.994 | 4.9931
|  | N-1 Hosting Capacity (A) | 679.4637 | 679.4802 | 679.4923 | 681.193 | 681.1997
|  | N-1 Power Factor | 0.99593 | 0.99592 | 0.99592 | 0.99551 | 0.99551
|  | N-1 Limiting section | 3331-2 | 3331-2 | 3331-2 | 3331-2 | 3331-2
|  | Contingency Scenario | F3359 | F312 | F312 | F327 | F327
F3331 | 3331-3 | Load (A) | 2.698 | 14.062 | 26.6175 | 39.5401 | 50.9732
|  | Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Utilisation (%) | 0.37628 | 1.9612 | 3.7123 | 5.5147 | 7.1092
|  | Hosting Capacity (A) | 714.302 | 702.938 | 690.3825 | 677.4599 | 666.0268
|  | Power Factor | 0.56181 | 0.99633 | 0.99999 | 0.99923 | 0.99825
|  | N-1 Load (A) | 9.9451 | 30.0084 | 53.079 | 76.5883 | 97.5464
|  | N-1 Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Contingency Utilisation (%) | 1.3871 | 4.1853 | 7.4029 | 10.6818 | 13.6048
|  | N-1 Hosting Capacity (A) | 707.0549 | 686.9916 | 663.921 | 640.4117 | 619.4536
|  | N-1 Power Factor | 0.56181 | 0.99633 | 0.99999 | 0.99923 | 0.99825
|  | N-1 Limiting section | 3331-3 | 3331-3 | 3331-3 | 3331-3 | 3331-3
|  | Contingency Scenario | F320 | F3329 | F3329 | F3329 | F3329
F334 | 334-1 | Load (A) | 25.3364 | 26.5287 | 26.802 | 28.0192 | 29.1971
|  | Rating (A) | 578 | 578 | 578 | 578 | 578
|  | Utilisation (%) | 4.3835 | 4.5897 | 4.637 | 4.8476 | 5.0514
|  | Hosting Capacity (A) | 552.6636 | 551.4713 | 551.198 | 549.9808 | 548.8029
|  | Power Factor | 0.99982 | 0.99985 | 0.9999 | 0.99994 | 0.99998
|  | N-1 Load (A) | 31.5149 | 39.0897 | 45.9398 | 53.5284 | 60.7247
|  | N-1 Rating (A) | 578 | 578 | 578 | 578 | 578
|  | Contingency Utilisation (%) | 5.4524 | 6.7629 | 7.9481 | 9.261 | 10.506
|  | N-1 Hosting Capacity (A) | 546.4851 | 538.9103 | 532.0602 | 524.4716 | 517.2753
|  | N-1 Power Factor | 0.99982 | 0.99985 | 0.9999 | 0.99994 | 1
|  | N-1 Limiting section | 334-1 | 334-1 | 334-1 | 334-1 | 334-1(2)
|  | Contingency Scenario | F349 | F349 | F349 | F349 | F349
F334 | 334-2 | Load (A) | 16.5839 | 21.6863 | 26.8394 | 31.9324 | 36.7303
|  | Rating (A) | 750 | 750 | 750 | 750 | 750
|  | Utilisation (%) | 2.2119 | 2.8919 | 3.5788 | 4.2578 | 4.8978
|  | Hosting Capacity (A) | 733.4161 | 728.3137 | 723.1606 | 718.0676 | 713.2697
|  | Power Factor | 0.99864 | 0.99955 | 0.9999 | 1 | 0.99993
|  | N-1 Load (A) | 34.4053 | 45.4926 | 56.6644 | 67.6862 | 78.0648
|  | N-1 Rating (A) | 750 | 750 | 750 | 750 | 750
|  | Contingency Utilisation (%) | 4.5874 | 6.0657 | 7.5552 | 9.0248 | 10.4086
|  | N-1 Hosting Capacity (A) | 715.5947 | 704.5074 | 693.3356 | 682.3138 | 671.9352
|  | N-1 Power Factor | 0.99864 | 0.99955 | 1 | 1 | 0.99993
|  | N-1 Limiting section | 334-2(1) | 334-2(1) | 334-2(3) | 334-2(1) | 334-2(1)
|  | Contingency Scenario | F335 | F335 | F335 | F335 | F335
F334 | 334-3 | Load (A) | 41.9197 | 48.2175 | 53.6435 | 59.9517 | 65.9232
|  | Rating (A) | 578 | 578 | 578 | 578 | 578
|  | Utilisation (%) | 7.2525 | 8.3421 | 9.2809 | 10.3723 | 11.4054
|  | Hosting Capacity (A) | 536.0803 | 529.7825 | 524.3565 | 518.0483 | 512.0768
|  | Power Factor | 0.99939 | 0.99968 | 0.99987 | 0.99997 | 1
|  | N-1 Load (A) | 60.2988 | 60.2272 | 71.3002 | 83.4839 | 95.0034
|  | N-1 Rating (A) | 578 | 578 | 578 | 578 | 578
|  | Contingency Utilisation (%) | 10.4323 | 10.4199 | 12.3357 | 14.4436 | 16.4366
|  | N-1 Hosting Capacity (A) | 517.7012 | 517.7728 | 506.6998 | 494.5161 | 482.9966
|  | N-1 Power Factor | 0.99939 | 0.99968 | 0.99987 | 0.99997 | 1
|  | N-1 Limiting section | 334-3 | 334-3 | 334-3 | 334-3 | 334-3
|  | Contingency Scenario | F335 | F335 | F349 | F349 | F349
F3340 | 3340-1 | Load (A) | 29.5921 | 23.9834 | 18.7759 | 13.9681 | 9.7756
|  | Rating (A) | 512 | 512 | 512 | 512 | 512
|  | Utilisation (%) | 5.7797 | 4.6843 | 3.6672 | 2.7281 | 1.9093
|  | Hosting Capacity (A) | 482.4079 | 488.0166 | 493.2241 | 498.0319 | 502.2244
|  | Power Factor | 0.99646 | 0.99659 | 0.99658 | 0.99635 | 0.99568
|  | N-1 Load (A) | 46.9648 | 38.0427 | 29.7597 | 22.1129 | 15.4444
|  | N-1 Rating (A) | 512 | 512 | 512 | 512 | 512
|  | Contingency Utilisation (%) | 9.1728 | 7.4302 | 5.8124 | 4.3189 | 3.0165
|  | N-1 Hosting Capacity (A) | 465.0352 | 473.9573 | 482.2403 | 489.8871 | 496.5556
|  | N-1 Power Factor | 0.99646 | 0.99659 | 0.99658 | 0.99635 | 0.99568
|  | N-1 Limiting section | 3340-1(2) | 3340-1(2) | 3340-1(2) | 3340-1(2) | 3340-1(2)
|  | Contingency Scenario | F336 | F336 | F336 | F336 | F336
F3349 | 3349-1 | Load (A) | 127.5788 | 127.5504 | 127.5213 | 127.4924 | 127.4652
|  | Rating (A) | 689 | 689 | 689 | 689 | 689
|  | Utilisation (%) | 18.5165 | 18.5124 | 18.5082 | 18.504 | 18.5
|  | Hosting Capacity (A) | 561.4212 | 561.4496 | 561.4787 | 561.5076 | 561.5348
|  | Power Factor | 0.99848 | 0.99848 | 0.99848 | 0.99848 | 0.99848
|  | N-1 Load (A) | 127.6798 | 127.6215 | 127.5622 | 127.5077 | 127.4833
|  | N-1 Rating (A) | 689 | 689 | 689 | 689 | 689
|  | Contingency Utilisation (%) | 18.5312 | 18.5227 | 18.5141 | 18.5062 | 18.5027
|  | N-1 Hosting Capacity (A) | 561.3202 | 561.3785 | 561.4378 | 561.4923 | 561.5167
|  | N-1 Power Factor | 0.99848 | 0.99848 | 0.99848 | 0.99848 | 0.99848
|  | N-1 Limiting section | 3349-1 | 3349-1 | 3349-1 | 3349-1 | 3349-1
|  | Contingency Scenario | F548 | F548 | F548 | F596 | F596
F335 | 335-2 | Load (A) | 17.88 | 23.8901 | 29.9538 | 35.9579 | 41.6174
|  | Rating (A) | 750 | 750 | 750 | 750 | 750
|  | Utilisation (%) | 2.3847 | 3.1857 | 3.994 | 4.7947 | 5.5495
|  | Hosting Capacity (A) | 732.12 | 726.1099 | 720.0462 | 714.0421 | 708.3826
|  | Power Factor | 0.99897 | 0.99973 | 0.99997 | 0.99996 | 0.99985
|  | N-1 Load (A) | 34.464 | 45.5999 | 56.8321 | 67.9394 | 78.3995
|  | N-1 Rating (A) | 750 | 750 | 750 | 750 | 750
|  | Contingency Utilisation (%) | 4.5952 | 6.08 | 7.5776 | 9.0586 | 10.4533
|  | N-1 Hosting Capacity (A) | 715.536 | 704.4001 | 693.1679 | 682.0606 | 671.6005
|  | N-1 Power Factor | 0.99871 | 0.99973 | 0.99997 | 0.99996 | 0.99985
|  | N-1 Limiting section | 335-2(2) | 335-2(1) | 335-2(1) | 335-2(1) | 335-2(1)
|  | Contingency Scenario | F334 | F334 | F334 | F334 | F334
F335 | 335-3 | Load (A) | 18.3742 | 12.1038 | 5.2613 | 3.0405 | 8.1668
|  | Rating (A) | 485 | 485 | 485 | 485 | 485
|  | Utilisation (%) | 3.7885 | 2.4956 | 1.0848 | 0.62691 | 1.6839
|  | Hosting Capacity (A) | 466.6258 | 472.8962 | 479.7387 | 481.9595 | 476.8332
|  | Power Factor | 0.996 | 0.98786 | 0.90947 | 0.51292 | 0.92542
|  | N-1 Load (A) | 60.4049 | 60.3751 | 58.6346 | 58.6091 | 58.589
|  | N-1 Rating (A) | 485 | 485 | 485 | 485 | 485
|  | Contingency Utilisation (%) | 12.4546 | 12.4485 | 12.0896 | 12.0844 | 12.0802
|  | N-1 Hosting Capacity (A) | 424.5951 | 424.6249 | 426.3654 | 426.3909 | 426.411
|  | N-1 Power Factor | 0.996 | 0.98786 | 0.90947 | 0.51292 | 0.92542
|  | N-1 Limiting section | 335-3 | 335-3 | 335-3 | 335-3 | 335-3
|  | Contingency Scenario | F334 | F334 | F334 | F334 | F334
F3350 | 3350-1 | Load (A) | 5.9638 | 5.9641 | 5.9645 | 5.9648 | 5.9652
|  | Rating (A) | 639 | 639 | 639 | 639 | 639
|  | Utilisation (%) | 0.9333 | 0.93336 | 0.93341 | 0.93347 | 0.93352
|  | Hosting Capacity (A) | 633.0362 | 633.0359 | 633.0355 | 633.0352 | 633.0348
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 129.0645 | 129.0566 | 129.0488 | 129.0411 | 129.0342
|  | N-1 Rating (A) | 639 | 639 | 639 | 639 | 639
|  | Contingency Utilisation (%) | 20.1979 | 20.1967 | 20.1954 | 20.1942 | 20.1931
|  | N-1 Hosting Capacity (A) | 509.9355 | 509.9434 | 509.9512 | 509.9589 | 509.9658
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 3350-1 | 3350-1 | 3350-1 | 3350-1 | 3350-1
|  | Contingency Scenario | F547 | F547 | F547 | F547 | F547
F3351 | 3351-1 | Load (A) | 4.9531 | 4.9534 | 4.9537 | 4.954 | 4.9543
|  | Rating (A) | 639 | 639 | 639 | 639 | 639
|  | Utilisation (%) | 0.7782 | 0.77825 | 0.7783 | 0.77834 | 0.77838
|  | Hosting Capacity (A) | 634.0469 | 634.0466 | 634.0463 | 634.046 | 634.0457
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 127.3139 | 127.3061 | 127.2984 | 127.2909 | 127.284
|  | N-1 Rating (A) | 639 | 639 | 639 | 639 | 639
|  | Contingency Utilisation (%) | 19.9239 | 19.9227 | 19.9215 | 19.9203 | 19.9192
|  | N-1 Hosting Capacity (A) | 511.6861 | 511.6939 | 511.7016 | 511.7091 | 511.716
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 3351-1 | 3351-1 | 3351-1 | 3351-1 | 3351-1
|  | Contingency Scenario | F3349 | F3349 | F3349 | F3349 | F3349
F3356 | 3356-1 | Load (A) | 35.5979 | 35.5979 | 33.9043 | 33.9043 | 33.9043
|  | Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Utilisation (%) | 5.0854 | 5.0854 | 4.8435 | 4.8435 | 4.8435
|  | Hosting Capacity (A) | 664.4021 | 664.4021 | 666.0957 | 666.0957 | 666.0957
|  | Power Factor | 0.99954 | 0.99954 | 0.9995 | 0.9995 | 0.9995
F3359 | 3359-2 | Load (A) | 18.0714 | 4.1801 | 26.8691 | 48.6903 | 67.8017
|  | Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Utilisation (%) | 2.5816 | 0.59715 | 3.8384 | 6.9558 | 9.686
|  | Hosting Capacity (A) | 681.9286 | 695.8199 | 673.1309 | 651.3097 | 632.1983
|  | Power Factor | 0.99143 | 0.99768 | 0.99578 | 0.99659 | 0.99734
|  | N-1 Load (A) | 50.7375 | 69.1698 | 114.8573 | 158.5681 | 196.8173
|  | N-1 Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Contingency Utilisation (%) | 7.2482 | 9.8814 | 16.4082 | 22.6526 | 28.1168
|  | N-1 Hosting Capacity (A) | 649.2625 | 630.8302 | 585.1427 | 541.4319 | 503.1827
|  | N-1 Power Factor | 0.99143 | 0.99768 | 0.99578 | 0.99659 | 0.99734
|  | N-1 Limiting section | 3359-2 | 3359-2 | 3359-2 | 3359-2 | 3359-2
|  | Contingency Scenario | F320 | F327 | F327 | F327 | F327
F3359 | 3359-3 | Load (A) | 18.1392 | 4.1801 | 26.8288 | 48.6524 | 67.7678
|  | Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Utilisation (%) | 2.5913 | 0.59651 | 3.8327 | 6.9503 | 9.6811
|  | Hosting Capacity (A) | 681.8608 | 695.8199 | 673.1712 | 651.3476 | 632.2322
|  | Power Factor | 0.98773 | 0.99768 | 0.99727 | 0.99735 | 0.99782
|  | N-1 Load (A) | 50.7235 | 69.1347 | 114.8297 | 158.5488 | 196.8057
|  | N-1 Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Contingency Utilisation (%) | 7.2462 | 9.8764 | 16.4042 | 22.6498 | 28.1151
|  | N-1 Hosting Capacity (A) | 649.2765 | 630.8653 | 585.1703 | 541.4512 | 503.1943
|  | N-1 Power Factor | 0.99143 | 0.99768 | 0.99727 | 0.99659 | 0.99734
|  | N-1 Limiting section | 3359-2 | 3359-2 | 3359-3 | 3359-2 | 3359-2
|  | Contingency Scenario | F320 | F327 | F327 | F327 | F327
F3359 | 3359-4 | Load (A) | 18.5542 | 4.7156 | 26.7849 | 48.599 | 67.7176
|  | Rating (A) | 762 | 762 | 762 | 762 | 762
|  | Utilisation (%) | 2.4349 | 0.61884 | 3.5151 | 6.3786 | 8.8876
|  | Hosting Capacity (A) | 743.4458 | 757.2844 | 735.2151 | 713.401 | 694.2824
|  | Power Factor | 0.96572 | 0.88441 | 0.99886 | 0.99836 | 0.99844
|  | N-1 Load (A) | 50.7125 | 69.0883 | 114.7913 | 158.5213 | 196.7886
|  | N-1 Rating (A) | 762 | 762 | 762 | 762 | 762
|  | Contingency Utilisation (%) | 6.6552 | 9.0667 | 15.0645 | 20.8033 | 25.8253
|  | N-1 Hosting Capacity (A) | 711.2875 | 692.9117 | 647.2087 | 603.4787 | 565.2114
|  | N-1 Power Factor | 0.96572 | 0.88441 | 0.99903 | 0.99836 | 0.99843
|  | N-1 Limiting section | 3359-4 | 3359-4 | 3359-4 | 3359-4 | 3359-4(2)
|  | Contingency Scenario | F320 | F327 | F327 | F327 | F327
F3359 | 3359-7 | Load (A) | 18.0224 | 4.1801 | 26.8288 | 48.725 | 67.8321
|  | Rating (A) | 703 | 700 | 700 | 703 | 703
|  | Utilisation (%) | 2.5636 | 0.60119 | 3.8277 | 6.931 | 9.6489
|  | Hosting Capacity (A) | 684.9776 | 695.8199 | 673.1712 | 654.275 | 635.1679
|  | Power Factor | 0.99399 | 0.99768 | 0.99727 | 0.99618 | 0.99725
|  | N-1 Load (A) | 50.7523 | 69.2011 | 114.8814 | 158.5847 | 196.8272
|  | N-1 Rating (A) | 703 | 703 | 703 | 703 | 703
|  | Contingency Utilisation (%) | 7.2194 | 9.8437 | 16.3416 | 22.5583 | 27.9982
|  | N-1 Hosting Capacity (A) | 652.2477 | 633.7989 | 588.1186 | 544.4153 | 506.1728
|  | N-1 Power Factor | 0.99399 | 0.98681 | 0.9945 | 0.99618 | 0.99725
|  | N-1 Limiting section | 3359-7(2) | 3359-7(2) | 3359-7(2) | 3359-7(2) | 3359-7(2)
|  | Contingency Scenario | F320 | F327 | F327 | F327 | F327
F336 | 336-1 | Load (A) | 33.9261 | 27.5641 | 21.6784 | 16.2824 | 11.6473
|  | Rating (A) | 455 | 455 | 455 | 455 | 455
|  | Utilisation (%) | 7.4563 | 6.058 | 4.7645 | 3.5785 | 2.5598
|  | Hosting Capacity (A) | 421.0739 | 427.4359 | 433.3216 | 438.7176 | 443.3527
|  | Power Factor | 0.99317 | 0.98949 | 0.98319 | 0.97106 | 0.94548
|  | N-1 Load (A) | 50.01 | 40.5495 | 31.7798 | 23.7074 | 16.7127
|  | N-1 Rating (A) | 455 | 455 | 455 | 455 | 455
|  | Contingency Utilisation (%) | 10.9912 | 8.912 | 6.9846 | 5.2104 | 3.6731
|  | N-1 Hosting Capacity (A) | 404.99 | 414.4505 | 423.2202 | 431.2926 | 438.2873
|  | N-1 Power Factor | 0.99317 | 0.98949 | 0.98319 | 0.97106 | 0.94548
|  | N-1 Limiting section | 336-1(2) | 336-1(2) | 336-1(2) | 336-1(2) | 336-1(2)
|  | Contingency Scenario | F3340 | F3340 | F3340 | F3340 | F3340
F3364 | 3364-1 | Load (A) | 58.7423 | 78.0678 | 97.5631 | 116.8653 | 135.0515
|  | Rating (A) | 725 | 725 | 725 | 725 | 725
|  | Utilisation (%) | 8.1024 | 10.7743 | 13.463 | 16.1194 | 18.6278
|  | Hosting Capacity (A) | 666.2577 | 646.9322 | 627.4369 | 608.1347 | 589.9485
|  | Power Factor | 0.99887 | 0.99983 | 0.99928 | 0.99835 | 0.9978
|  | N-1 Load (A) | 115.9712 | 154.4134 | 193.1154 | 231.4856 | 267.875
|  | N-1 Rating (A) | 824 | 824 | 824 | 824 | 824
|  | Contingency Utilisation (%) | 15.996 | 21.2984 | 26.6366 | 31.929 | 36.9483
|  | N-1 Hosting Capacity (A) | 708.0288 | 669.5866 | 630.8846 | 592.5144 | 556.125
|  | N-1 Power Factor | 0.99957 | 0.99925 | 0.99884 | 0.99835 | 0.9978
|  | N-1 Limiting section | 3364-1(9) | 3364-1(9) | 3364-1(9) | 3364-1(9) | 3364-1(9)
|  | Contingency Scenario | F303 | F303 | F303 | F303 | F303
F337 | 337-1 | Load (A) | 27.6603 | 22.3997 | 17.5156 | 13.0069 | 9.0761
|  | Rating (A) | 490 | 490 | 490 | 490 | 490
|  | Utilisation (%) | 5.645 | 4.5714 | 3.5746 | 2.6545 | 1.8523
|  | Hosting Capacity (A) | 462.3397 | 467.6003 | 472.4844 | 476.9931 | 480.9239
|  | Power Factor | 1 | 0.99998 | 0.99986 | 0.99955 | 0.99879
|  | N-1 Load (A) | 43.9848 | 35.614 | 27.843 | 20.6693 | 14.4141
|  | N-1 Rating (A) | 490 | 490 | 490 | 490 | 490
|  | Contingency Utilisation (%) | 8.9765 | 7.2682 | 5.6823 | 4.2182 | 2.9417
|  | N-1 Hosting Capacity (A) | 446.0152 | 454.386 | 462.157 | 469.3307 | 475.5859
|  | N-1 Power Factor | 1 | 0.99998 | 0.99986 | 0.99955 | 0.99879
|  | N-1 Limiting section | 337-1(3) | 337-1(3) | 337-1(3) | 337-1(3) | 337-1(3)
|  | Contingency Scenario | F336 | F336 | F336 | F336 | F336
F3370 | 3370-1 | Load (A) | 30.606 | 30.606 | 28.905 | 28.905 | 28.905
|  | Rating (A) | 772 | 772 | 772 | 772 | 772
|  | Utilisation (%) | 3.9645 | 3.9645 | 3.7442 | 3.7442 | 3.7442
|  | Hosting Capacity (A) | 741.394 | 741.394 | 743.095 | 743.095 | 743.095
|  | Power Factor | 0.99995 | 0.99995 | 0.99994 | 0.99994 | 0.99994
F3374 | 3374-1 | Load (A) | 3.9164 | 3.3036 | 3.0183 | 2.6572 | 2.7375
|  | Rating (A) | 704 | 704 | 704 | 704 | 704
|  | Utilisation (%) | 0.5563 | 0.4718 | 0.4315 | 0.38058 | 0.39189
|  | Hosting Capacity (A) | 700.0836 | 700.6964 | 700.9817 | 701.3428 | 701.2625
|  | Power Factor | 0.96712 | 0.95942 | 0.95153 | 0.93702 | 0.94071
|  | N-1 Load (A) | 26.598 | 26.665 | 26.7334 | 26.806 | 26.8947
|  | N-1 Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Contingency Utilisation (%) | 3.7997 | 3.8093 | 3.8191 | 3.8294 | 3.8421
|  | N-1 Hosting Capacity (A) | 673.402 | 673.335 | 673.2666 | 673.194 | 673.1053
|  | N-1 Power Factor | 0.99956 | 0.99941 | 0.99932 | 0.9991 | 0.99915
|  | N-1 Limiting section | 3374-1 | 3374-1 | 3374-1 | 3374-1 | 3374-1
|  | Contingency Scenario | F556 | F556 | F556 | F556 | F556
F3377 | 3377-1 | Load (A) | 75.3325 | 74.4799 | 73.6356 | 73.6356 | 72.7749
|  | Rating (A) | 640 | 640 | 640 | 640 | 640
|  | Utilisation (%) | 11.772 | 11.6387 | 11.5056 | 11.5056 | 11.3724
|  | Hosting Capacity (A) | 564.6675 | 565.5201 | 566.3644 | 566.3644 | 567.2251
|  | Power Factor | 0.99942 | 0.99938 | 0.99923 | 0.99923 | 0.99929
|  | N-1 Load (A) | 151.5156 | 149.7906 | 148.0659 | 148.0659 | 146.3413
|  | N-1 Rating (A) | 640 | 640 | 640 | 640 | 640
|  | Contingency Utilisation (%) | 23.6743 | 23.4048 | 23.1353 | 23.1353 | 22.8658
|  | N-1 Hosting Capacity (A) | 488.4844 | 490.2094 | 491.9341 | 491.9341 | 493.6587
|  | N-1 Power Factor | 0.99973 | 0.99974 | 0.99934 | 0.99934 | 0.99936
|  | N-1 Limiting section | 3377-1(6) | 3377-1(6) | 3377-1(8) | 3377-1(8) | 3377-1(8)
|  | Contingency Scenario | F3378 | F3378 | F3378 | F3378 | F3378
F3378 | 3378-1 | Load (A) | 76.0891 | 75.2234 | 74.3578 | 74.3578 | 73.5054
|  | Rating (A) | 640 | 640 | 640 | 640 | 640
|  | Utilisation (%) | 11.8889 | 11.7542 | 11.6197 | 11.6197 | 11.4852
|  | Hosting Capacity (A) | 563.9109 | 564.7766 | 565.6422 | 565.6422 | 566.4946
|  | Power Factor | 0.99934 | 0.99935 | 0.99937 | 0.99937 | 0.99921
|  | N-1 Load (A) | 151.514 | 149.7891 | 148.0644 | 148.0644 | 146.3399
|  | N-1 Rating (A) | 640 | 640 | 640 | 640 | 640
|  | Contingency Utilisation (%) | 23.6741 | 23.4046 | 23.1351 | 23.1351 | 22.8656
|  | N-1 Hosting Capacity (A) | 488.486 | 490.2109 | 491.9356 | 491.9356 | 493.6601
|  | N-1 Power Factor | 0.99934 | 0.99935 | 0.99937 | 0.99937 | 0.99938
|  | N-1 Limiting section | 3378-1 | 3378-1 | 3378-1 | 3378-1 | 3378-1
|  | Contingency Scenario | F3377 | F3377 | F3377 | F3377 | F3377
F3379 | 3379-1 | Load (A) | 275.4406 | 275.4406 | 275.4406 | 275.4406 | 275.4406
|  | Rating (A) | 609 | 609 | 609 | 609 | 609
|  | Utilisation (%) | 45.2283 | 45.2283 | 45.2283 | 45.2283 | 45.2283
|  | Hosting Capacity (A) | 333.5594 | 333.5594 | 333.5594 | 333.5594 | 333.5594
|  | Power Factor | 0.99942 | 0.99942 | 0.99942 | 0.99942 | 0.99942
F338 | 338-1 | Load (A) | 2.1432 | 2.1432 | 2.1432 | 2.1432 | 2.1432
|  | Rating (A) | 348 | 348 | 348 | 348 | 348
|  | Utilisation (%) | 0.61586 | 0.61586 | 0.61586 | 0.61586 | 0.61586
|  | Hosting Capacity (A) | 345.8568 | 345.8568 | 345.8568 | 345.8568 | 345.8568
|  | Power Factor | 1 | 1 | 1 | 1 | 1
F3380 | 3380-1 | Load (A) | 271.9544 | 271.9544 | 271.9544 | 271.9544 | 271.9544
|  | Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Utilisation (%) | 38.8506 | 38.8506 | 38.8506 | 38.8506 | 38.8506
|  | Hosting Capacity (A) | 428.0456 | 428.0456 | 428.0456 | 428.0456 | 428.0456
|  | Power Factor | 0.99967 | 0.99967 | 0.99967 | 0.99967 | 0.99967
F3384 | 3384-1 | Load (A) | 75.2488 | 73.5374 | 72.6818 | 72.6818 | 71.8262
|  | Rating (A) | 779 | 779 | 779 | 779 | 779
|  | Utilisation (%) | 9.6597 | 9.44 | 9.3301 | 9.3301 | 9.2203
|  | Hosting Capacity (A) | 703.7512 | 705.4626 | 706.3182 | 706.3182 | 707.1738
|  | Power Factor | 0.99932 | 0.99935 | 0.99936 | 0.99936 | 0.99938
|  | N-1 Load (A) | 150.6417 | 147.1971 | 145.4754 | 145.4755 | 143.7542
|  | N-1 Rating (A) | 779 | 779 | 779 | 779 | 779
|  | Contingency Utilisation (%) | 19.3378 | 18.8957 | 18.6746 | 18.6746 | 18.4537
|  | N-1 Hosting Capacity (A) | 628.3583 | 631.8029 | 633.5246 | 633.5245 | 635.2458
|  | N-1 Power Factor | 0.99932 | 0.99935 | 0.99936 | 0.99936 | 0.99938
|  | N-1 Limiting section | 3384-1 | 3384-1 | 3384-1 | 3384-1 | 3384-1
|  | Contingency Scenario | F3385 | F3385 | F3385 | F3385 | F3385
F3385 | 3385-1 | Load (A) | 74.8801 | 73.177 | 72.3256 | 72.3256 | 71.4742
|  | Rating (A) | 779 | 779 | 779 | 779 | 779
|  | Utilisation (%) | 9.6123 | 9.3937 | 9.2844 | 9.2844 | 9.1751
|  | Hosting Capacity (A) | 704.1199 | 705.823 | 706.6744 | 706.6744 | 707.5258
|  | Power Factor | 0.99931 | 0.99934 | 0.99936 | 0.99936 | 0.99937
|  | N-1 Load (A) | 150.6459 | 147.201 | 145.4792 | 145.4792 | 143.7578
|  | N-1 Rating (A) | 779 | 779 | 779 | 779 | 779
|  | Contingency Utilisation (%) | 19.3384 | 18.8961 | 18.6751 | 18.6751 | 18.4541
|  | N-1 Hosting Capacity (A) | 628.3541 | 631.799 | 633.5208 | 633.5208 | 635.2422
|  | N-1 Power Factor | 0.99931 | 0.99934 | 0.99936 | 0.99936 | 0.99937
|  | N-1 Limiting section | 3385-1 | 3385-1 | 3385-1 | 3385-1 | 3385-1
|  | Contingency Scenario | F3384 | F3384 | F3384 | F3384 | F3384
F3387 | 3387-1 | Load (A) | 130.7108 | 130.6999 | 130.6682 | 130.6448 | 130.6217
|  | Rating (A) | 610 | 610 | 610 | 610 | 610
|  | Utilisation (%) | 21.4295 | 21.4262 | 21.4226 | 21.4187 | 21.415
|  | Hosting Capacity (A) | 479.2892 | 479.3001 | 479.3318 | 479.3552 | 479.3783
|  | Power Factor | 0.99998 | 0.99991 | 0.99998 | 0.99998 | 0.99998
|  | N-1 Load (A) | 130.8705 | 130.8289 | 130.7838 | 130.7363 | 130.6895
|  | N-1 Rating (A) | 610 | 610 | 610 | 610 | 610
|  | Contingency Utilisation (%) | 21.4542 | 21.4474 | 21.44 | 21.4322 | 21.4245
|  | N-1 Hosting Capacity (A) | 479.1295 | 479.1711 | 479.2162 | 479.2637 | 479.3105
|  | N-1 Power Factor | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998
|  | N-1 Limiting section | 3387-1 | 3387-1 | 3387-1 | 3387-1 | 3387-1
|  | Contingency Scenario | F591 | F591 | F591 | F591 | F590
F339 | 339/2-1 | Load (A) | 10.4805 | 7.5989 | 4.6442 | 1.7012 | 1.3126
|  | Rating (A) | 155 | 155 | 155 | 155 | 155
|  | Utilisation (%) | 6.7616 | 4.9025 | 2.9963 | 1.0976 | 0.84684
|  | Hosting Capacity (A) | 144.5195 | 147.4011 | 150.3558 | 153.2988 | 153.6874
|  | Power Factor | 0.99835 | 0.99697 | 0.9928 | 0.95525 | 0.94321
F339 | 339/2-2 | Load (A) | 3.1499 | 5.9619 | 8.8525 | 11.7664 | 14.5637
|  | Rating (A) | 200 | 200 | 200 | 200 | 200
|  | Utilisation (%) | 1.575 | 2.9809 | 4.4262 | 5.8832 | 7.2818
|  | Hosting Capacity (A) | 196.8501 | 194.0381 | 191.1475 | 188.2336 | 185.4363
|  | Power Factor | 0.99948 | 0.99981 | 0.99986 | 0.99986 | 0.99985
F339 | 339/2-3 | Load (A) | 13.6204 | 13.5456 | 13.4711 | 13.3989 | 13.3323
|  | Rating (A) | 155 | 155 | 155 | 155 | 155
|  | Utilisation (%) | 8.7873 | 8.7391 | 8.691 | 8.6445 | 8.6015
|  | Hosting Capacity (A) | 141.3796 | 141.4544 | 141.5289 | 141.6011 | 141.6677
|  | Power Factor | 0.9994 | 0.99941 | 0.99941 | 0.99941 | 0.99942
F339 | 339/2-4 | Load (A) | 13.6284 | 13.5536 | 13.4791 | 13.407 | 13.3404
|  | Rating (A) | 160 | 160 | 160 | 160 | 160
|  | Utilisation (%) | 8.5177 | 8.471 | 8.4245 | 8.3794 | 8.3378
|  | Hosting Capacity (A) | 146.3716 | 146.4464 | 146.5209 | 146.593 | 146.6596
|  | Power Factor | 0.99882 | 0.99882 | 0.99882 | 0.99882 | 0.99882
F339 | 339-1 | Load (A) | 7.7084 | 21.4475 | 35.6761 | 49.9702 | 63.58
|  | Rating (A) | 742 | 742 | 742 | 742 | 742
|  | Utilisation (%) | 1.0389 | 2.8905 | 4.8081 | 6.7345 | 8.5687
|  | Hosting Capacity (A) | 734.2916 | 720.5525 | 706.3239 | 692.0298 | 678.42
|  | Power Factor | 0.97911 | 0.99886 | 0.99999 | 0.99955 | 0.99879
F339 | 339-2 | Load (A) | 7.6533 | 21.4353 | 35.6883 | 50.0028 | 63.6275
|  | Rating (A) | 210 | 210 | 210 | 210 | 210
|  | Utilisation (%) | 3.6444 | 10.2073 | 16.9944 | 23.8108 | 30.2988
|  | Hosting Capacity (A) | 202.3467 | 188.5647 | 174.3117 | 159.9972 | 146.3725
|  | Power Factor | 0.98613 | 0.99941 | 0.99981 | 0.9995 | 0.9988
F3390 | 3390-1 | Load (A) | 9.1134 | 8.4931 | 15.8486 | 25.3692 | 34.2616
|  | Rating (A) | 728 | 728 | 728 | 728 | 728
|  | Utilisation (%) | 1.2518 | 1.1666 | 2.177 | 3.4848 | 4.7063
|  | Hosting Capacity (A) | 718.8866 | 719.5069 | 712.1514 | 702.6308 | 693.7384
|  | Power Factor | 0.56114 | 0.4428 | 0.87767 | 0.95736 | 0.98034
|  | N-1 Load (A) | 14.8534 | 12.9587 | 22.6321 | 36.8472 | 49.9964
|  | N-1 Rating (A) | 728 | 728 | 728 | 728 | 728
|  | Contingency Utilisation (%) | 2.0403 | 1.78 | 3.1088 | 5.0614 | 6.8676
|  | N-1 Hosting Capacity (A) | 713.1466 | 715.0413 | 705.3679 | 691.1528 | 678.0036
|  | N-1 Power Factor | 0.56114 | 0.4428 | 0.87767 | 0.95736 | 0.98034
|  | N-1 Limiting section | 3390-1(2) | 3390-1(2) | 3390-1(2) | 3390-1(2) | 3390-1(2)
|  | Contingency Scenario | F480 | F3393 | F507B | F507B | F507B
F3393 | 3393-1 | Load (A) | 45.3816 | 44.1114 | 42.7695 | 41.4022 | 40.0955
|  | Rating (A) | 610 | 610 | 610 | 610 | 610
|  | Utilisation (%) | 7.4396 | 7.2314 | 7.0114 | 6.7872 | 6.573
|  | Hosting Capacity (A) | 564.6184 | 565.8886 | 567.2305 | 568.5978 | 569.9045
|  | Power Factor | 0.99981 | 0.99987 | 0.99993 | 0.99988 | 0.99979
|  | N-1 Load (A) | 95.1808 | 93.5913 | 91.9626 | 90.3042 | 88.6915
|  | N-1 Rating (A) | 610 | 610 | 610 | 610 | 610
|  | Contingency Utilisation (%) | 15.6034 | 15.3428 | 15.0758 | 14.804 | 14.5396
|  | N-1 Hosting Capacity (A) | 514.8192 | 516.4087 | 518.0374 | 519.6958 | 521.3085
|  | N-1 Power Factor | 0.99981 | 0.99987 | 0.99993 | 0.99988 | 0.99979
|  | N-1 Limiting section | 3393-1(1) | 3393-1(1) | 3393-1(1) | 3393-1(1) | 3393-1(1)
|  | Contingency Scenario | F480 | F480 | F480 | F480 | F480
F3394 | 3394-1 | Load (A) | 95.0102 | 93.4212 | 91.7928 | 90.1349 | 88.5225
|  | Rating (A) | 610 | 610 | 610 | 610 | 610
|  | Utilisation (%) | 15.5755 | 15.3149 | 15.048 | 14.7762 | 14.5119
|  | Hosting Capacity (A) | 514.9898 | 516.5788 | 518.2072 | 519.8651 | 521.4775
|  | Power Factor | 0.99856 | 0.9986 | 0.99865 | 0.99869 | 0.99873
F3395 | 3395-1 | Load (A) | 33.7378 | 67.4746 | 65.7878 | 65.7878 | 65.7878
|  | Rating (A) | 704 | 704 | 704 | 704 | 704
|  | Utilisation (%) | 4.7923 | 9.5845 | 9.3449 | 9.3449 | 9.3449
|  | Hosting Capacity (A) | 670.2622 | 636.5254 | 638.2122 | 638.2122 | 638.2122
|  | Power Factor | 0.99996 | 0.99999 | 0.99999 | 0.99999 | 0.99999
F340 | 340-1 | Load (A) | 6.0792 | 2.6537 | 2.9922 | 6.5431 | 10.1703
|  | Rating (A) | 349 | 349 | 349 | 349 | 349
|  | Utilisation (%) | 1.7419 | 0.76038 | 0.85736 | 1.8748 | 2.9141
|  | Hosting Capacity (A) | 342.9208 | 346.3463 | 346.0078 | 342.4569 | 338.8297
|  | Power Factor | 0.94587 | 0.66602 | 0.7586 | 0.95766 | 0.9844
|  | N-1 Load (A) | 12.8714 | 5.2266 | 6.0023 | 13.863 | 21.7187
|  | N-1 Rating (A) | 349 | 349 | 349 | 349 | 349
|  | Contingency Utilisation (%) | 3.6881 | 1.4976 | 1.7198 | 3.9722 | 6.2231
|  | N-1 Hosting Capacity (A) | 336.1286 | 343.7734 | 342.9977 | 335.137 | 327.2813
|  | N-1 Power Factor | 0.94587 | 0.66602 | 0.7586 | 0.95766 | 0.9844
|  | N-1 Limiting section | 340-1(1) | 340-1(1) | 340-1(1) | 340-1(1) | 340-1(1)
|  | Contingency Scenario | F351 | F351 | F351 | F351 | F351
F340 | 340-4 | Load (A) | 6.0792 | 2.6537 | 2.9922 | 6.5431 | 10.1703
|  | Rating (A) | 349 | 349 | 349 | 349 | 349
|  | Utilisation (%) | 1.7416 | 0.75966 | 0.85673 | 1.8745 | 2.9139
|  | Hosting Capacity (A) | 342.9208 | 346.3463 | 346.0078 | 342.4569 | 338.8297
|  | Power Factor | 0.94587 | 0.66602 | 0.7586 | 0.95766 | 0.9844
|  | N-1 Load (A) | 12.8705 | 5.2243 | 6.0003 | 13.8622 | 21.7182
|  | N-1 Rating (A) | 349 | 349 | 349 | 349 | 349
|  | Contingency Utilisation (%) | 3.6878 | 1.4969 | 1.7193 | 3.972 | 6.223
|  | N-1 Hosting Capacity (A) | 336.1295 | 343.7757 | 342.9997 | 335.1378 | 327.2818
|  | N-1 Power Factor | 0.94587 | 0.66602 | 0.7586 | 0.95766 | 0.9844
|  | N-1 Limiting section | 340-1(1) | 340-1(1) | 340-1(1) | 340-1(1) | 340-1(1)
|  | Contingency Scenario | F351 | F351 | F351 | F351 | F351
F340 | 340-5 | Load (A) | 3.3879 | 3.3885 | 3.3891 | 3.3896 | 3.3902
|  | Rating (A) | 328 | 328 | 328 | 328 | 328
|  | Utilisation (%) | 1.0329 | 1.0331 | 1.0333 | 1.0334 | 1.0336
|  | Hosting Capacity (A) | 324.6121 | 324.6115 | 324.6109 | 324.6104 | 324.6098
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) |  | 3.3885 | 3.3898 | 3.391 | 3.3922
|  | N-1 Rating (A) | 328 | 328 | 328 | 328 | 328
|  | Contingency Utilisation (%) |  | 1.0331 | 1.0335 | 1.0339 | 1.0342
|  | N-1 Hosting Capacity (A) |  | 324.6115 | 324.6102 | 324.609 | 324.6078
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 340-2 | 340-5(1) | 340-5(1) | 340-5(1) | 340-5(1)
|  | Contingency Scenario |  | F351 | F351 | F351 | F351
F340 | 340-6 | Load (A) | 1.5436 | 1.5439 | 1.5442 | 1.5444 | 1.5447
|  | Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Utilisation (%) | 0.22052 | 0.22056 | 0.2206 | 0.22063 | 0.22067
|  | Hosting Capacity (A) | 698.4564 | 698.4561 | 698.4558 | 698.4556 | 698.4553
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) |  |  | 1.5445 | 1.5451 | 1.5456
|  | N-1 Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Contingency Utilisation (%) |  |  | 0.22064 | 0.22072 | 0.2208
|  | N-1 Hosting Capacity (A) |  |  | 698.4555 | 698.4549 | 698.4544
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 340-2 | 340-2 | 340-6 | 340-6 | 340-6
|  | Contingency Scenario |  |  | F351 | F351 | F351
F340 | 340-7 | Load (A) | 1.5377 | 1.5379 | 1.5382 | 1.5385 | 1.5387
|  | Rating (A) | 208 | 208 | 208 | 208 | 208
|  | Utilisation (%) | 0.73926 | 0.73939 | 0.73952 | 0.73964 | 0.73976
|  | Hosting Capacity (A) | 206.4623 | 206.4621 | 206.4618 | 206.4615 | 206.4613
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) |  |  | 1.5385 | 1.5391 | 1.5396
|  | N-1 Rating (A) | 208 | 208 | 208 | 208 | 208
|  | Contingency Utilisation (%) |  |  | 0.73968 | 0.73995 | 0.7402
|  | N-1 Hosting Capacity (A) |  |  | 206.4615 | 206.4609 | 206.4604
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 340-2 | 340-2 | 340-7 | 340-7 | 340-7
|  | Contingency Scenario |  |  | F351 | F351 | F351
F340 | 340-9 | Load (A) | 6.013 | 2.4979 | 2.9018 | 6.5221 | 10.2035
|  | Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Utilisation (%) | 1.4927 | 0.62085 | 0.72004 | 1.623 | 2.5319
|  | Hosting Capacity (A) | 396.987 | 400.5021 | 400.0982 | 396.4779 | 392.7965
|  | Power Factor | 0.95621 | 0.70749 | 0.7831 | 0.96071 | 0.98137
|  | N-1 Load (A) | 12.3915 | 3.8353 | 4.8469 | 13.4267 | 21.4684
|  | N-1 Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Contingency Utilisation (%) | 3.0748 | 0.95169 | 1.2027 | 3.3317 | 5.3271
|  | N-1 Hosting Capacity (A) | 390.6085 | 399.1647 | 398.1531 | 389.5733 | 381.5316
|  | N-1 Power Factor | 0.95534 | 0.70523 | 0.7831 | 0.95831 | 0.98137
|  | N-1 Limiting section | 340-9 | 340-9 | 340-9 | 340-9 | 340-9
|  | Contingency Scenario | F351 | F351 | F351 | F351 | F351
F3400 | 3400-1 | Load (A) | 58.155 | 80.363 | 102.8654 | 125.1797 | 146.4078
|  | Rating (A) | 694 | 694 | 694 | 694 | 694
|  | Utilisation (%) | 8.3797 | 11.584 | 14.8221 | 18.0374 | 21.0962
|  | Hosting Capacity (A) | 635.845 | 613.637 | 591.1346 | 568.8203 | 547.5922
|  | Power Factor | 0.99755 | 0.99953 | 0.99865 | 0.99802 | 0.99731
|  | N-1 Load (A) | 116.1044 | 160.8086 | 205.7388 | 250.3471 | 292.7792
|  | N-1 Rating (A) | 765 | 765 | 765 | 765 | 765
|  | Contingency Utilisation (%) | 16.7297 | 23.1713 | 29.6454 | 36.0731 | 42.1872
|  | N-1 Hosting Capacity (A) | 648.8956 | 604.1914 | 559.2612 | 514.6529 | 472.2208
|  | N-1 Power Factor | 0.99954 | 0.99916 | 0.99865 | 0.99802 | 0.99731
|  | N-1 Limiting section | 3400-1(2) | 3400-1(2) | 3400-1(2) | 3400-1(2) | 3400-1(2)
|  | Contingency Scenario | F3405 | F3405 | F3405 | F3405 | F3405
F3402 | 3402-1 | Load (A) | 13.2271 | 7.5096 | 4.4761 | 7.1206 | 11.6691
|  | Rating (A) | 687 | 687 | 687 | 687 | 687
|  | Utilisation (%) | 1.9253 | 1.0931 | 0.65154 | 1.0365 | 1.6986
|  | Hosting Capacity (A) | 673.7729 | 679.4904 | 682.5239 | 679.8794 | 675.3309
|  | Power Factor | 0.94309 | 0.80483 | 1 | 0.77965 | 0.92562
|  | N-1 Load (A) | 25.2883 | 12.7552 | 12.7552 | 11.8241 | 21.987
|  | N-1 Rating (A) | 739 | 739 | 739 | 739 | 739
|  | Contingency Utilisation (%) | 3.681 | 1.8567 |  | 1.7211 | 3.2004
|  | N-1 Hosting Capacity (A) | 713.7117 | 726.2448 | 726.2448 | 727.1759 | 717.013
|  | N-1 Power Factor | 0.94309 | 0.80483 |  | 0.77965 | 0.92562
|  | N-1 Limiting section | 3402-1(1) | 3402-1(1) | 3402-1(1) | 3402-1(1) | 3402-1(1)
|  | Contingency Scenario | F3403 | F3403 | F3404 | F3403 | F3403
F3403 | 3403-1 | Load (A) | 13.2602 | 7.5223 | 4.474 | 7.1318 | 11.6971
|  | Rating (A) | 687 | 687 | 687 | 687 | 687
|  | Utilisation (%) | 1.9302 | 1.095 | 0.65124 | 1.0381 | 1.7026
|  | Hosting Capacity (A) | 673.7398 | 679.4777 | 682.526 | 679.8682 | 675.3029
|  | Power Factor | 0.94345 | 0.80579 | 1 | 0.78067 | 0.92606
|  | N-1 Load (A) | 25.2859 | 12.7502 | 12.7502 | 11.8187 | 21.9841
|  | N-1 Rating (A) | 739 | 739 | 739 | 739 | 739
|  | Contingency Utilisation (%) | 3.6806 | 1.8559 | 1.8559 | 1.7203 | 3.2
|  | N-1 Hosting Capacity (A) | 713.7141 | 726.2498 | 726.2498 | 727.1813 | 717.0159
|  | N-1 Power Factor | 0.94345 | 0.80579 |  | 0.78067 | 0.92606
|  | N-1 Limiting section | 3403-1(1) | 3403-1(1) | 3403-1(1) | 3403-1(1) | 3403-1(1)
|  | Contingency Scenario | F3402 | F3402 | F3403 | F3402 | F3402
F3405 | 3405-1 | Load (A) | 58.2216 | 80.4857 | 102.9838 | 125.3238 | 146.5763
|  | Rating (A) | 694 | 694 | 694 | 694 | 694
|  | Utilisation (%) | 8.3893 | 11.5974 | 14.8392 | 18.0582 | 21.1205
|  | Hosting Capacity (A) | 635.7784 | 613.5143 | 591.0162 | 568.6762 | 547.4237
|  | Power Factor | 0.99756 | 0.99916 | 0.99865 | 0.99803 | 0.99731
|  | N-1 Load (A) | 116.1045 | 160.8088 | 205.7391 | 250.3475 | 292.7797
|  | N-1 Rating (A) | 765 | 765 | 765 | 765 | 765
|  | Contingency Utilisation (%) | 16.7298 | 23.1713 | 29.6454 | 36.0731 | 42.1873
|  | N-1 Hosting Capacity (A) | 648.8955 | 604.1912 | 559.2609 | 514.6525 | 472.2203
|  | N-1 Power Factor | 0.99955 | 0.99916 | 0.99865 | 0.99803 | 0.99731
|  | N-1 Limiting section | 3405-1(2) | 3405-1(2) | 3405-1(2) | 3405-1(2) | 3405-1(2)
|  | Contingency Scenario | F3400 | F3400 | F3400 | F3400 | F3400
F341 | 3004-1 | Load (A) | 14.325 | 21.3862 | 28.5496 | 36.1217 | 43.0052
|  | Rating (A) | 127 | 127 | 127 | 127 | 127
|  | Utilisation (%) | 11.2795 | 16.8395 | 22.48 | 28.4423 | 33.8624
|  | Hosting Capacity (A) | 112.675 | 105.6138 | 98.4504 | 90.8783 | 83.9948
|  | Power Factor | 0.99955 | 0.99997 | 0.99995 | 0.99977 | 0.99953
|  | N-1 Load (A) | 15.2992 | 22.6561 | 30.0444 | 37.3002 | 44.1348
|  | N-1 Rating (A) | 127 | 127 | 127 | 127 | 127
|  | Contingency Utilisation (%) | 12.0466 | 17.8394 | 23.657 | 29.3703 | 34.7518
|  | N-1 Hosting Capacity (A) | 111.7008 | 104.3439 | 96.9556 | 89.6998 | 82.8652
|  | N-1 Power Factor | 0.99955 | 0.99997 | 0.99995 | 0.99977 | 0.99953
|  | N-1 Limiting section | 3004-1(4) | 3004-1(4) | 3004-1(4) | 3004-1(4) | 3004-1(4)
|  | Contingency Scenario | F429 | F429 | F429 | F429 | F429
F341 | 3005-1 | Load (A) | 14.4247 | 21.6174 | 28.9605 | 36.7823 | 43.9299
|  | Rating (A) | 582 | 582 | 582 | 582 | 582
|  | Utilisation (%) | 2.4785 | 3.7143 | 4.976 | 6.32 | 7.5481
|  | Hosting Capacity (A) | 567.5753 | 560.3826 | 553.0395 | 545.2177 | 538.0701
|  | Power Factor | 0.99968 | 0.99966 | 0.99958 | 0.99943 | 0.99927
|  | N-1 Load (A) | 15.4233 | 22.934 | 30.5251 | 38.0286 | 45.1441
|  | N-1 Rating (A) | 582 | 582 | 582 | 582 | 582
|  | Contingency Utilisation (%) | 2.65 | 3.9405 | 5.2449 | 6.5341 | 7.7567
|  | N-1 Hosting Capacity (A) | 566.5767 | 559.066 | 551.4749 | 543.9714 | 536.8559
|  | N-1 Power Factor | 0.99968 | 0.99966 | 0.99958 | 0.99943 | 0.99927
|  | N-1 Limiting section | 3005-1(1) | 3005-1(1) | 3005-1(1) | 3005-1(1) | 3005-1(1)
|  | Contingency Scenario | F429 | F429 | F429 | F429 | F429
F341 | 341-1 | Load (A) | 94.2544 | 84.8821 | 75.4432 | 66.833 | 57.8251
|  | Rating (A) | 211 | 211 | 211 | 211 | 211
|  | Utilisation (%) | 44.6703 | 40.2285 | 35.7551 | 31.6744 | 27.4052
|  | Hosting Capacity (A) | 116.7456 | 126.1179 | 135.5568 | 144.167 | 153.1749
|  | Power Factor | 0.99782 | 0.99824 | 0.99891 | 0.99955 | 0.99997
|  | N-1 Load (A) | 242.2668 | 219.936 | 198.5089 | 178.2701 | 157.9361
|  | N-1 Rating (A) | 211 | 211 | 211 | 211 | 211
|  | Contingency Utilisation (%) | 114.8184 | 104.2351 | 94.08 | 84.4882 | 74.8512
|  | N-1 Hosting Capacity (A) | -31.2668 | -8.936 | 12.4911 | 32.7299 | 53.0639
|  | N-1 Power Factor | 0.99782 | 0.99824 | 0.99891 | 0.99955 | 0.99997
|  | N-1 Limiting section | 341-1(1) | 341-1(1) | 341-1(1) | 341-1(1) | 341-1(1)
|  | Contingency Scenario | F429 | F429 | F429 | F429 | F429
F341 | 341-2 | Load (A) | 123.841 | 129.3042 | 134.9737 | 141.4658 | 146.8534
|  | Rating (A) | 410 | 410 | 410 | 410 | 410
|  | Utilisation (%) | 30.2051 | 31.5376 | 32.9204 | 34.5038 | 35.8179
|  | Hosting Capacity (A) | 286.159 | 280.6958 | 275.0263 | 268.5342 | 263.1466
|  | Power Factor | 0.99922 | 0.99946 | 0.99966 | 0.99974 | 0.99979
|  | N-1 Load (A) | 274.5967 | 267.8036 | 261.9373 | 257.0636 | 251.1188
|  | N-1 Rating (A) | 463 | 463 | 463 | 463 | 463
|  | Contingency Utilisation (%) | 66.9748 | 65.318 | 63.8872 | 62.6984 | 61.2485
|  | N-1 Hosting Capacity (A) | 188.4033 | 195.1964 | 201.0627 | 205.9364 | 211.8812
|  | N-1 Power Factor | 0.99922 | 0.99946 | 0.99966 | 0.99974 | 0.99979
|  | N-1 Limiting section | 341-2 | 341-2 | 341-2 | 341-2 | 341-2
|  | Contingency Scenario | F429 | F429 | F429 | F429 | F429
F341 | 341-3 | Load (A) | 29.8782 | 44.6278 | 59.6505 | 74.6864 | 89.0492
|  | Rating (A) | 210 | 210 | 210 | 210 | 210
|  | Utilisation (%) | 14.2277 | 21.2513 | 28.405 | 35.565 | 42.4044
|  | Hosting Capacity (A) | 180.1218 | 165.3722 | 150.3495 | 135.3136 | 120.9508
|  | Power Factor | 0.99806 | 0.99961 | 0.99998 | 0.99993 | 0.99968
|  | N-1 Load (A) | 32.2938 | 47.8731 | 63.5764 | 79.0525 | 93.6811
|  | N-1 Rating (A) | 210 | 210 | 210 | 210 | 210
|  | Contingency Utilisation (%) | 15.378 | 22.7967 | 30.2745 | 37.644 | 44.6101
|  | N-1 Hosting Capacity (A) | 177.7062 | 162.1269 | 146.4236 | 130.9475 | 116.3189
|  | N-1 Power Factor | 0.99806 | 0.99961 | 0.99998 | 0.99993 | 0.99968
|  | N-1 Limiting section | 341-3 | 341-3 | 341-3 | 341-3 | 341-3
|  | Contingency Scenario | F429 | F429 | F429 | F429 | F429
F341 | 341-4 | Load (A) | 28.7951 | 43.0133 | 57.4941 | 72.8649 | 86.8776
|  | Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Utilisation (%) | 4.0161 | 5.9991 | 8.0187 | 10.1625 | 12.1168
|  | Hosting Capacity (A) | 688.2049 | 673.9867 | 659.5059 | 644.1351 | 630.1224
|  | Power Factor | 0.99813 | 0.99962 | 0.99998 | 0.99994 | 0.99971
|  | N-1 Load (A) | 30.7537 | 45.5925 | 60.5489 | 75.2882 | 89.2204
|  | N-1 Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Contingency Utilisation (%) | 4.2892 | 6.3588 | 8.4448 | 10.5004 | 12.4436
|  | N-1 Hosting Capacity (A) | 686.2463 | 671.4075 | 656.4511 | 641.7118 | 627.7796
|  | N-1 Power Factor | 0.99813 | 0.99962 | 0.99998 | 0.99994 | 0.99971
|  | N-1 Limiting section | 341-4 | 341-4 | 341-4 | 341-4 | 341-4
|  | Contingency Scenario | F429 | F429 | F429 | F429 | F429
F342 | 342-1 | Load (A) | 24.8508 | 32.5878 | 40.5752 | 48.7109 | 56.6312
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 4.4938 | 5.8929 | 7.3373 | 8.8085 | 10.2407
|  | Hosting Capacity (A) | 528.1492 | 520.4122 | 512.4248 | 504.2891 | 496.3688
|  | Power Factor | 0.99352 | 0.99685 | 0.99844 | 0.99926 | 0.99969
|  | N-1 Load (A) | 49.3903 | 64.9191 | 80.9511 | 97.2633 | 113.1377
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 8.9313 | 11.7394 | 14.6385 | 17.5883 | 20.4589
|  | N-1 Hosting Capacity (A) | 503.6097 | 488.0809 | 472.0489 | 455.7367 | 439.8623
|  | N-1 Power Factor | 0.99352 | 0.99685 | 0.99999 | 0.99999 | 0.99995
|  | N-1 Limiting section | 342-1(2) | 342-1(2) | 342-1(6) | 342-1(6) | 342-1(6)
|  | Contingency Scenario | F3290 | F3290 | F3290 | F3290 | F3290
F3426 | 3426-1 | Load (A) | 24.1467 | 4.8617 | 17.5126 | 40.8277 | 64.698
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 2.9519 | 0.59434 | 2.1409 | 4.9912 | 7.9093
|  | Hosting Capacity (A) | 793.8533 | 813.1383 | 800.4874 | 777.1723 | 753.302
|  | Power Factor | 0.99755 | 0.89812 | 0.99183 | 0.99895 | 0.99988
|  | N-1 Load (A) | 41.2252 | 8.1063 | 29.7895 | 69.6115 | 110.3305
|  | N-1 Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Contingency Utilisation (%) | 5.0398 | 0.99099 | 3.6418 | 8.51 | 13.4878
|  | N-1 Hosting Capacity (A) | 776.7748 | 809.8937 | 788.2105 | 748.3885 | 707.6695
|  | N-1 Power Factor | 0.99755 | 0.89812 | 0.99183 | 0.99895 | 0.99988
|  | N-1 Limiting section | 3426-1(3) | 3426-1(3) | 3426-1(3) | 3426-1(3) | 3426-1(3)
|  | Contingency Scenario | F443 | F443 | F443 | F443 | F443
F3429 | 3429-1 | Load (A) | 27.6501 | 12.7418 | 2.9072 | 18.9283 | 34.5781
|  | Rating (A) | 735 | 735 | 735 | 735 | 735
|  | Utilisation (%) | 3.7619 | 1.7336 | 0.39554 | 2.5753 | 4.7045
|  | Hosting Capacity (A) | 707.3499 | 722.2582 | 732.0928 | 716.0717 | 700.4219
|  | Power Factor | 0.99966 | 0.99945 | 0.99277 | 0.99961 | 0.99963
|  | N-1 Load (A) | 54.8461 | 25.2542 | 5.7606 | 37.4857 | 68.4816
|  | N-1 Rating (A) | 790 | 790 | 790 | 790 | 790
|  | Contingency Utilisation (%) | 7.4621 | 3.4359 | 0.78376 | 5.1001 | 9.3172
|  | N-1 Hosting Capacity (A) | 735.1539 | 764.7458 | 784.2394 | 752.5143 | 721.5184
|  | N-1 Power Factor | 0.99966 | 0.99945 | 0.99277 | 0.99961 | 0.99963
|  | N-1 Limiting section | 3429-1 | 3429-1 | 3429-1 | 3429-1 | 3429-1
|  | Contingency Scenario | F3430 | F3430 | F3430 | F3430 | F3430
F343 | 343-1 | Load (A) | 64.4406 | 119.2174 | 175.399 | 231.4637 | 284.0725
|  | Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Utilisation (%) | 8.2616 | 15.2843 | 22.487 | 29.6748 | 36.4196
|  | Hosting Capacity (A) | 715.5594 | 660.7826 | 604.601 | 548.5363 | 495.9275
|  | Power Factor | 0.99999 | 0.99988 | 0.99918 | 0.99808 | 0.99671
|  | N-1 Load (A) | 100.765 | 195.1815 | 292.1797 | 389.0711 | 480.1346
|  | N-1 Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Contingency Utilisation (%) | 12.9186 | 25.0233 | 37.4589 | 49.8809 | 61.5557
|  | N-1 Hosting Capacity (A) | 679.235 | 584.8185 | 487.8203 | 390.9289 | 299.8654
|  | N-1 Power Factor | 0.99999 | 0.99988 | 0.99918 | 0.99808 | 0.99671
|  | N-1 Limiting section | 343-1(1) | 343-1(1) | 343-1(1) | 343-1(1) | 343-1(1)
|  | Contingency Scenario | F346 | F346 | F346 | F346 | F346
F343 | 343-2 | Load (A) | 6.9207 | 30.6291 | 55.4646 | 80.6477 | 104.6887
|  | Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Utilisation (%) | 0.88727 | 3.9268 | 7.1108 | 10.3394 | 13.4216
|  | Hosting Capacity (A) | 773.0793 | 749.3709 | 724.5354 | 699.3523 | 675.3113
|  | Power Factor | 0.99657 | 0.99852 | 0.99824 | 0.99732 | 0.99609
|  | N-1 Load (A) | 43.2503 | 106.6505 | 172.3724 | 238.4627 | 301.0402
|  | N-1 Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Contingency Utilisation (%) | 5.5449 | 13.6731 | 22.099 | 30.5721 | 38.5949
|  | N-1 Hosting Capacity (A) | 736.7497 | 673.3495 | 607.6276 | 541.5373 | 478.9598
|  | N-1 Power Factor | 0.99657 | 0.99852 | 0.99824 | 0.99732 | 0.99609
|  | N-1 Limiting section | 343-2 | 343-2 | 343-2 | 343-2 | 343-2
|  | Contingency Scenario | F346 | F346 | F346 | F346 | F346
F343 | 343-3 | Load (A) | 57.5474 | 88.625 | 119.9667 | 150.8623 | 179.4247
|  | Rating (A) | 495 | 495 | 495 | 495 | 495
|  | Utilisation (%) | 11.6257 | 17.9041 | 24.2367 | 30.4774 | 36.251
|  | Hosting Capacity (A) | 437.4526 | 406.375 | 375.0333 | 344.1377 | 315.5753
|  | Power Factor | 0.9999 | 0.99999 | 0.9997 | 0.99941 | 0.99802
F3430 | 3430-1 | Load (A) | 27.1173 | 12.4965 | 2.8528 | 18.5639 | 33.912
|  | Rating (A) | 735 | 735 | 735 | 735 | 735
|  | Utilisation (%) | 3.6894 | 1.7002 | 0.38814 | 2.5257 | 4.6139
|  | Hosting Capacity (A) | 707.8827 | 722.5035 | 732.1472 | 716.4361 | 701.088
|  | Power Factor | 0.99964 | 0.99941 | 0.99226 | 0.9996 | 0.99962
|  | N-1 Load (A) | 54.8497 | 25.2549 | 5.7606 | 37.4858 | 68.4614
|  | N-1 Rating (A) | 790 | 790 | 790 | 790 | 790
|  | Contingency Utilisation (%) | 7.4625 | 3.436 | 0.78376 | 5.1001 | 9.3145
|  | N-1 Hosting Capacity (A) | 735.1503 | 764.7451 | 784.2394 | 752.5142 | 721.5386
|  | N-1 Power Factor | 0.99964 | 0.99941 | 0.99226 | 0.9996 | 0.99962
|  | N-1 Limiting section | 3430-1 | 3430-1 | 3430-1 | 3430-1 | 3430-1
|  | Contingency Scenario | F3429 | F3429 | F3429 | F3429 | F3429
F344 | 344-1 | Load (A) | 34.9448 | 47.9535 | 61.8986 | 75.0978 | 87.5623
|  | Rating (A) | 155 | 155 | 200 | 200 | 200
|  | Utilisation (%) | 22.5484 | 30.9412 | 30.9493 | 37.5489 | 43.7811
|  | Hosting Capacity (A) | 120.0552 | 107.0465 | 138.1014 | 124.9022 | 112.4377
|  | Power Factor | 1 | 0.99985 | 0.99968 | 0.99925 | 0.99873
F3440 | 3440-1 | Load (A) | 97.3028 | 89.0462 | 80.5874 | 72.1101 | 64.1214
|  | Rating (A) | 544 | 544 | 544 | 544 | 544
|  | Utilisation (%) | 17.8865 | 16.3688 | 14.8139 | 13.2555 | 11.787
|  | Hosting Capacity (A) | 446.6972 | 454.9538 | 463.4126 | 471.8899 | 479.8786
|  | Power Factor | 0.99978 | 0.99972 | 0.99966 | 0.99958 | 0.99949
|  | N-1 Load (A) | 117.4078 | 107.4469 | 97.2428 | 87.017 | 77.3811
|  | N-1 Rating (A) | 544 | 544 | 544 | 544 | 544
|  | Contingency Utilisation (%) | 21.5823 | 19.7513 | 17.8755 | 15.9958 | 14.2245
|  | N-1 Hosting Capacity (A) | 426.5922 | 436.5531 | 446.7572 | 456.983 | 466.6189
|  | N-1 Power Factor | 0.99978 | 0.99972 | 0.99966 | 0.99958 | 0.99949
|  | N-1 Limiting section | 3440-1 | 3440-1 | 3440-1 | 3440-1 | 3440-1
|  | Contingency Scenario | F459A | F459A | F459A | F459A | F459A
F345 | 345-1 | Load (A) | 12.5291 | 19.8836 | 27.3504 | 34.9069 | 42.1839
|  | Rating (A) | 208 | 208 | 208 | 208 | 208
|  | Utilisation (%) | 6.0236 | 9.5594 | 13.1496 | 16.7827 | 20.2812
|  | Hosting Capacity (A) | 195.4709 | 188.1164 | 180.6496 | 173.0931 | 165.8161
|  | Power Factor | 0.99779 | 0.99931 | 0.99965 | 0.99952 | 0.99935
F346 | 346-1 | Load (A) | 36.3848 | 76.1995 | 117.2978 | 158.5067 | 197.3788
|  | Rating (A) | 976 | 976 | 976 | 976 | 976
|  | Utilisation (%) | 3.7279 | 7.8073 | 12.0182 | 16.2404 | 20.2232
|  | Hosting Capacity (A) | 939.6152 | 899.8005 | 858.7022 | 817.4933 | 778.6212
|  | Power Factor | 0.99996 | 0.99981 | 0.9991 | 0.99802 | 0.99667
|  | N-1 Load (A) | 43.2771 | 106.7519 | 172.581 | 238.819 | 301.5534
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 4.4341 | 10.9377 | 17.6825 | 24.4692 | 30.8969
|  | N-1 Hosting Capacity (A) | 756.7229 | 693.2481 | 627.419 | 561.181 | 498.4466
|  | N-1 Power Factor | 0.99996 | 0.99981 | 0.9991 | 0.99802 | 0.99667
|  | N-1 Limiting section | 346-1 | 346-1 | 346-1 | 346-1 | 346-1
|  | Contingency Scenario | F343 | F343 | F343 | F343 | F343
F346 | 346-2 | Load (A) | 36.3834 | 76.2013 | 117.3016 | 158.5122 | 197.3859
|  | Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Utilisation (%) | 4.6645 | 9.7694 | 15.0387 | 20.3221 | 25.3059
|  | Hosting Capacity (A) | 743.6166 | 703.7987 | 662.6984 | 621.4878 | 582.6141
|  | Power Factor | 1 | 0.99981 | 0.9991 | 0.99802 | 0.99667
|  | N-1 Load (A) | 43.2782 | 106.7547 | 172.5856 | 238.8253 | 301.5614
|  | N-1 Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Contingency Utilisation (%) | 5.5485 | 13.6865 | 22.1264 | 30.6186 | 38.6617
|  | N-1 Hosting Capacity (A) | 736.7218 | 673.2453 | 607.4144 | 541.1747 | 478.4386
|  | N-1 Power Factor | 1 | 0.99981 | 0.9991 | 0.99802 | 0.99667
|  | N-1 Limiting section | 346-2 | 346-2 | 346-2 | 346-2 | 346-2
|  | Contingency Scenario | F343 | F343 | F343 | F343 | F343
F3460 | 3460-1 | Load (A) | 50.9977 | 47.2421 | 43.2809 | 39.2058 | 35.2967
|  | Rating (A) | 802 | 802 | 802 | 802 | 802
|  | Utilisation (%) | 6.3588 | 5.8905 | 5.3966 | 4.8885 | 4.4011
|  | Hosting Capacity (A) | 751.0023 | 754.7579 | 758.7191 | 762.7942 | 766.7033
|  | Power Factor | 0.99843 | 0.99792 | 0.99722 | 0.99625 | 0.99496
|  | N-1 Load (A) | 101.9708 | 94.4076 | 86.4335 | 78.234 | 70.3619
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 12.7146 | 11.7715 | 10.7772 | 9.7549 | 8.7733
|  | N-1 Hosting Capacity (A) | 698.0292 | 705.5924 | 713.5665 | 721.766 | 729.6381
|  | N-1 Power Factor | 0.99843 | 0.99792 | 0.99722 | 0.99625 | 0.99496
|  | N-1 Limiting section | 3460-1 | 3460-1 | 3460-1 | 3460-1 | 3460-1
|  | Contingency Scenario | F3461 | F3461 | F3461 | F3461 | F3461
F3461 | 3461-1 | Load (A) | 51.0764 | 47.315 | 43.3476 | 39.2661 | 35.3509
|  | Rating (A) | 802 | 802 | 802 | 802 | 802
|  | Utilisation (%) | 6.3686 | 5.8996 | 5.4049 | 4.896 | 4.4078
|  | Hosting Capacity (A) | 750.9236 | 754.685 | 758.6524 | 762.7339 | 766.6491
|  | Power Factor | 0.99843 | 0.99792 | 0.99722 | 0.99625 | 0.99497
|  | N-1 Load (A) | 101.9708 | 94.4076 | 86.4334 | 78.2338 | 70.3617
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 12.7146 | 11.7715 | 10.7772 | 9.7548 | 8.7733
|  | N-1 Hosting Capacity (A) | 698.0292 | 705.5924 | 713.5666 | 721.7662 | 729.6383
|  | N-1 Power Factor | 0.99843 | 0.99792 | 0.99722 | 0.99625 | 0.99497
|  | N-1 Limiting section | 3461-1 | 3461-1 | 3461-1 | 3461-1 | 3461-1
|  | Contingency Scenario | F3460 | F3460 | F3460 | F3460 | F3460
F347 | 347-1 | Load (A) | 28.1222 | 44.0323 | 60.1861 | 76.2005 | 91.3205
|  | Rating (A) | 412 | 412 | 412 | 412 | 412
|  | Utilisation (%) | 6.8258 | 10.6911 | 14.6131 | 18.5021 | 22.1719
|  | Hosting Capacity (A) | 383.8778 | 367.9677 | 351.8139 | 335.7995 | 320.6795
|  | Power Factor | 0.99825 | 0.99996 | 0.99917 | 0.99821 | 0.99727
|  | N-1 Load (A) | 63.5335 | 99.3545 | 135.4112 | 171.0005 | 204.4582
|  | N-1 Rating (A) | 412 | 412 | 412 | 412 | 412
|  | Contingency Utilisation (%) | 15.4208 | 24.1152 | 32.8668 | 41.505 | 49.6258
|  | N-1 Hosting Capacity (A) | 348.4665 | 312.6455 | 276.5888 | 240.9995 | 207.5418
|  | N-1 Power Factor | 0.99825 | 0.99976 | 0.99919 | 0.99821 | 0.9976
|  | N-1 Limiting section | 347-1(1) | 347-1(9) | 347-1(7) | 347-1(3) | 347-1(9)
|  | Contingency Scenario | F348 | F348 | F348 | F348 | F348
F347 | 347-2 | Load (A) | 28.1317 | 44.1305 | 60.3111 | 76.355 | 91.4942
|  | Rating (A) | 357 | 357 | 357 | 357 | 357
|  | Utilisation (%) | 7.88 | 12.3615 | 16.8939 | 21.388 | 25.6286
|  | Hosting Capacity (A) | 328.8683 | 312.8695 | 296.6889 | 280.645 | 265.5058
|  | Power Factor | 0.99795 | 0.99804 | 0.99771 | 0.99712 | 0.99643
|  | N-1 Load (A) | 63.5245 | 99.3994 | 135.4831 | 171.0993 | 204.5825
|  | N-1 Rating (A) | 357 | 357 | 357 | 357 | 357
|  | Contingency Utilisation (%) | 17.794 | 27.843 | 37.9505 | 47.927 | 57.306
|  | N-1 Hosting Capacity (A) | 293.4755 | 257.6006 | 221.5169 | 185.9007 | 152.4175
|  | N-1 Power Factor | 0.99795 | 0.99804 | 0.99771 | 0.99712 | 0.99643
|  | N-1 Limiting section | 347-2 | 347-2 | 347-2 | 347-2 | 347-2
|  | Contingency Scenario | F348 | F348 | F348 | F348 | F348
F347 | 347-3 | Load (A) | 1.7313 | 1.7346 | 1.7377 | 1.7407 | 1.7433
|  | Rating (A) | 412 | 412 | 412 | 412 | 412
|  | Utilisation (%) | 0.42023 | 0.42101 | 0.42177 | 0.42249 | 0.42314
|  | Hosting Capacity (A) | 410.2687 | 410.2654 | 410.2623 | 410.2593 | 410.2567
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 35.3279 | 56.2394 | 76.8712 | 96.7336 | 114.7455
|  | N-1 Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Contingency Utilisation (%) | 8.7662 | 13.9552 | 19.0747 | 24.0034 | 28.4728
|  | N-1 Hosting Capacity (A) | 367.6721 | 346.7606 | 326.1288 | 306.2664 | 288.2545
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 347-3(1) | 347-3(1) | 347-3(1) | 347-3(1) | 347-3(1)
|  | Contingency Scenario | F608 | F608 | F608 | F608 | F608
F348 | 348-1 | Load (A) | 35.8515 | 56.2361 | 76.8682 | 97.3255 | 116.6288
|  | Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Utilisation (%) | 8.8961 | 13.9544 | 19.074 | 24.1502 | 28.9402
|  | Hosting Capacity (A) | 367.1485 | 346.7639 | 326.1318 | 305.6745 | 286.3712
|  | Power Factor | 0.99954 | 1 | 0.99982 | 0.99937 | 0.99874
|  | N-1 Load (A) | 63.7118 | 99.8321 | 136.236 | 172.2377 | 206.1287
|  | N-1 Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Contingency Utilisation (%) | 15.8094 | 24.7722 | 33.8055 | 42.7389 | 51.1486
|  | N-1 Hosting Capacity (A) | 339.2882 | 303.1679 | 266.764 | 230.7623 | 196.8713
|  | N-1 Power Factor | 0.99963 | 1 | 0.99982 | 0.99937 | 0.99874
|  | N-1 Limiting section | 348-1(1) | 348-1(1) | 348-1(1) | 348-1(1) | 348-1(1)
|  | Contingency Scenario | F347 | F347 | F347 | F347 | F347
F349 | 349-1 | Load (A) | 20.2678 | 41.22 | 62.8327 | 83.8029 | 103.6314
|  | Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Utilisation (%) | 2.8268 | 5.749 | 8.7633 | 11.688 | 14.4535
|  | Hosting Capacity (A) | 696.7322 | 675.78 | 654.1673 | 633.1971 | 613.3686
|  | Power Factor | 0.99957 | 0.99954 | 0.99939 | 0.99914 | 0.99884
|  | N-1 Load (A) | 33.5755 | 68.2499 | 103.9856 | 138.632 | 171.3703
|  | N-1 Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Contingency Utilisation (%) | 4.6828 | 9.5188 | 14.5029 | 19.335 | 23.901
|  | N-1 Hosting Capacity (A) | 683.4245 | 648.7501 | 613.0144 | 578.368 | 545.6297
|  | N-1 Power Factor | 0.99957 | 0.99954 | 0.99939 | 0.99914 | 0.99884
|  | N-1 Limiting section | 349-1 | 349-1 | 349-1 | 349-1 | 349-1
|  | Contingency Scenario | F333 | F333 | F333 | F333 | F333
F350 | 350-1 | Load (A) | 92.4499 | 135.9466 | 180.2696 | 224.3764 | 265.9728
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 11.3019 | 16.6194 | 22.0378 | 27.4299 | 32.515
|  | Hosting Capacity (A) | 725.5501 | 682.0534 | 637.7304 | 593.6236 | 552.0272
|  | Power Factor | 0.99983 | 0.9987 | 0.99697 | 0.99483 | 0.99243
|  | N-1 Load (A) | 167.5476 | 246.3752 | 326.4815 | 406.1093 | 481.2014
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 20.4826 | 30.1192 | 39.9122 | 49.6466 | 58.8266
|  | N-1 Hosting Capacity (A) | 632.4524 | 553.6248 | 473.5185 | 393.8907 | 318.7986
|  | N-1 Power Factor | 0.99983 | 0.9987 | 0.99697 | 0.99483 | 0.99243
|  | N-1 Limiting section | 350-1(1) | 350-1(1) | 350-1(1) | 350-1(1) | 350-1(1)
|  | Contingency Scenario | F412 | F412 | F412 | F412 | F412
F351 | 351-1 | Load (A) | 6.8771 | 2.7777 | 3.187 | 7.4015 | 11.6083
|  | Rating (A) | 355 | 355 | 355 | 355 | 355
|  | Utilisation (%) | 1.9372 | 0.78245 | 0.89775 | 2.0849 | 3.2699
|  | Hosting Capacity (A) | 348.1229 | 352.2223 | 351.813 | 347.5985 | 343.3917
|  | Power Factor | 0.96554 | 0.74376 | 0.80686 | 0.96767 | 0.98771
|  | N-1 Load (A) | 12.3909 | 3.8313 | 4.8443 | 13.4288 | 21.4739
|  | N-1 Rating (A) | 355 | 355 | 355 | 355 | 355
|  | Contingency Utilisation (%) | 3.4904 | 1.0792 | 1.3646 | 3.7827 | 6.049
|  | N-1 Hosting Capacity (A) | 342.6091 | 351.1687 | 350.1557 | 341.5712 | 333.5261
|  | N-1 Power Factor | 0.96554 | 0.74376 | 0.80686 | 0.96767 | 0.98771
|  | N-1 Limiting section | 351-1(1) | 351-1(1) | 351-1(1) | 351-1(1) | 351-1(1)
|  | Contingency Scenario | F340 | F340 | F340 | F340 | F340
F354 | 354-1 | Load (A) | 64.5738 | 52.6501 | 38.0545 | 20.2555 | 2.1198
|  | Rating (A) | 497 | 497 | 497 | 497 | 497
|  | Utilisation (%) | 12.9927 | 10.5936 | 7.6568 | 4.0755 | 0.42652
|  | Hosting Capacity (A) | 432.4262 | 444.3499 | 458.9455 | 476.7445 | 494.8802
|  | Power Factor | 0.99903 | 0.9988 | 0.99815 | 0.99479 | 0.40371
|  | N-1 Load (A) | 116.0622 | 99.5459 | 78.5615 | 51.9771 | 22.6374
|  | N-1 Rating (A) | 517 | 517 | 517 | 517 | 517
|  | Contingency Utilisation (%) | 23.3526 | 20.0293 | 15.8071 | 10.4582 | 4.5548
|  | N-1 Hosting Capacity (A) | 400.9378 | 417.4541 | 438.4385 | 465.0229 | 494.3626
|  | N-1 Power Factor | 0.99903 | 0.9988 | 0.99815 | 0.99479 | 0.40371
|  | N-1 Limiting section | 354-1(2) | 354-1(2) | 354-1(2) | 354-1(2) | 354-1(2)
|  | Contingency Scenario | F355 | F355 | F355 | F355 | F355
F355 | 355-1 | Load (A) | 51.3243 | 46.7863 | 40.4658 | 31.7799 | 21.7854
|  | Rating (A) | 495 | 495 | 495 | 495 | 495
|  | Utilisation (%) | 10.3685 | 9.4518 | 8.1749 | 6.4202 | 4.4011
|  | Hosting Capacity (A) | 443.6757 | 448.2137 | 454.5342 | 463.2201 | 473.2146
|  | Power Factor | 0.99999 | 0.99999 | 0.99987 | 0.99946 | 0.99814
|  | N-1 Load (A) | 116.1939 | 99.6243 | 78.5914 | 51.9706 | 31.936
|  | N-1 Rating (A) | 495 | 495 | 495 | 495 | 495
|  | Contingency Utilisation (%) | 23.4735 | 20.1261 | 15.8771 | 10.4991 | 6.4517
|  | N-1 Hosting Capacity (A) | 378.8061 | 395.3757 | 416.4086 | 443.0294 | 463.064
|  | N-1 Power Factor | 0.99999 | 0.99999 | 0.99987 | 0.99946 | 0.99814
|  | N-1 Limiting section | 355-1(4) | 355-1(4) | 355-1(4) | 355-1(4) | 355-1(4)
|  | Contingency Scenario | F354 | F354 | F354 | F354 | F361
F3550 | 3550-1 | Load (A) | 63.0355 | 99.7209 | 136.9952 | 174.0697 | 209.1495
|  | Rating (A) | 746 | 746 | 746 | 746 | 746
|  | Utilisation (%) | 8.4498 | 13.3674 | 18.364 | 23.3337 | 28.0361
|  | Hosting Capacity (A) | 682.9645 | 646.2791 | 609.0048 | 571.9303 | 536.8505
|  | Power Factor | 0.99276 | 0.99752 | 0.9991 | 0.99974 | 0.99966
|  | N-1 Load (A) | 87.7576 | 139.0012 | 191.0332 | 242.8603 | 291.7737
|  | N-1 Rating (A) | 746 | 746 | 746 | 746 | 746
|  | Contingency Utilisation (%) | 11.7638 | 18.6329 | 25.6077 | 32.555 | 39.1118
|  | N-1 Hosting Capacity (A) | 658.2424 | 606.9988 | 554.9668 | 503.1397 | 454.2263
|  | N-1 Power Factor | 0.99276 | 0.99752 | 0.9991 | 0.99974 | 0.99966
|  | N-1 Limiting section | 3550-1(6) | 3550-1(6) | 3550-1(6) | 3550-1(6) | 3550-1(6)
|  | Contingency Scenario | F425 | F425 | F425 | F425 | F425
F357 | 357-1 | Load (A) | 35.3598 | 50.6176 | 65.8551 | 80.6162 | 94.1478
|  | Rating (A) | 505 | 505 | 505 | 505 | 505
|  | Utilisation (%) | 7.0019 | 10.0233 | 13.0406 | 15.9636 | 18.6431
|  | Hosting Capacity (A) | 469.6402 | 454.3824 | 439.1449 | 424.3838 | 410.8522
|  | Power Factor | 0.99428 | 0.99885 | 0.99995 | 0.99972 | 0.99902
|  | N-1 Load (A) | 82.4278 | 118.0359 | 153.4541 | 187.6393 | 218.9323
|  | N-1 Rating (A) | 505 | 505 | 505 | 505 | 505
|  | Contingency Utilisation (%) | 16.3223 | 23.3734 | 30.387 | 37.1563 | 43.3529
|  | N-1 Hosting Capacity (A) | 422.5722 | 386.9641 | 351.5459 | 317.3607 | 286.0677
|  | N-1 Power Factor | 0.99428 | 0.99885 | 0.99995 | 0.99972 | 0.99902
|  | N-1 Limiting section | 357-1(5) | 357-1(5) | 357-1(5) | 357-1(5) | 357-1(5)
|  | Contingency Scenario | F445 | F445 | F445 | F445 | F445
F357 | 357-3 | Load (A) | 35.2412 | 50.5994 | 65.9574 | 80.802 | 94.3986
|  | Rating (A) | 710 | 710 | 710 | 710 | 710
|  | Utilisation (%) | 4.9635 | 7.1267 | 9.2898 | 11.3806 | 13.2956
|  | Hosting Capacity (A) | 674.7588 | 659.4006 | 644.0426 | 629.198 | 615.6014
|  | Power Factor | 0.99714 | 0.99893 | 0.99857 | 0.9981 | 0.9976
|  | N-1 Load (A) | 82.3472 | 118.0184 | 153.5149 | 187.7948 | 219.1715
|  | N-1 Rating (A) | 710 | 710 | 710 | 710 | 710
|  | Contingency Utilisation (%) | 11.5982 | 16.6223 | 21.6218 | 26.45 | 30.8692
|  | N-1 Hosting Capacity (A) | 627.6528 | 591.9816 | 556.4851 | 522.2052 | 490.8285
|  | N-1 Power Factor | 0.99714 | 0.99893 | 0.99857 | 0.9981 | 0.9976
|  | N-1 Limiting section | 357-3(2) | 357-3 | 357-3 | 357-3 | 357-3
|  | Contingency Scenario | F445 | F445 | F445 | F445 | F445
F3570 | 3570-1 | Load (A) | 30.8619 | 30.4203 | 30.5101 | 30.9109 | 31.2413
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 5.5808 | 5.501 | 5.5172 | 5.5897 | 5.6494
|  | Hosting Capacity (A) | 522.1381 | 522.5797 | 522.4899 | 522.0891 | 521.7587
|  | Power Factor | 0.99733 | 0.99801 | 0.99863 | 0.99912 | 0.99944
|  | N-1 Load (A) | 65.2926 | 74.3227 | 107.2644 | 140.9124 | 173.0947
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 11.807 | 13.4399 | 19.3968 | 25.4814 | 31.301
|  | N-1 Hosting Capacity (A) | 734.7074 | 725.6773 | 692.7356 | 659.0876 | 626.9053
|  | N-1 Power Factor | 0.99733 | 0.99801 | 0.99863 | 0.99912 | 0.99944
|  | N-1 Limiting section | 3570-1 | 3570-1 | 3570-1 | 3570-1 | 3570-1
|  | Contingency Scenario | F484 | F374 | F374 | F374 | F374
F3580 | 3580-1 | Load (A) | 23.8488 | 30.4813 | 37.1743 | 43.8023 | 50.045
|  | Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Utilisation (%) | 3.3262 | 4.2512 | 5.1847 | 6.1091 | 6.9798
|  | Hosting Capacity (A) | 693.1512 | 686.5187 | 679.8257 | 673.1977 | 666.955
|  | Power Factor | 0.99922 | 0.99848 | 0.99764 | 0.99674 | 0.99581
|  | N-1 Load (A) | 89.4281 | 119.8177 | 150.1509 | 179.8571 | 207.581
|  | N-1 Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Contingency Utilisation (%) | 12.4725 | 16.711 | 20.9415 | 25.0847 | 28.9513
|  | N-1 Hosting Capacity (A) | 627.5719 | 597.1823 | 566.8491 | 537.1429 | 509.419
|  | N-1 Power Factor | 0.99922 | 0.99848 | 0.99764 | 0.99674 | 0.99581
|  | N-1 Limiting section | 3580-1 | 3580-1 | 3580-1 | 3580-1 | 3580-1
|  | Contingency Scenario | F465 | F465 | F465 | F465 | F465
F3580 | 3580-2 | Load (A) | 23.8291 | 30.4386 | 37.1133 | 43.7255 | 49.9547
|  | Rating (A) | 527 | 527 | 527 | 527 | 527
|  | Utilisation (%) | 4.5217 | 5.7758 | 7.0424 | 8.2971 | 9.4791
|  | Hosting Capacity (A) | 503.1709 | 496.5614 | 489.8867 | 483.2745 | 477.0453
|  | Power Factor | 0.99997 | 0.99972 | 0.99901 | 0.9981 | 0.99711
|  | N-1 Load (A) | 89.3991 | 119.7768 | 150.0978 | 179.7931 | 207.5067
|  | N-1 Rating (A) | 527 | 527 | 527 | 527 | 527
|  | Contingency Utilisation (%) | 16.9638 | 22.728 | 28.4816 | 34.1163 | 39.3751
|  | N-1 Hosting Capacity (A) | 437.6009 | 407.2232 | 376.9022 | 347.2069 | 319.4933
|  | N-1 Power Factor | 0.99997 | 0.99972 | 0.99901 | 0.9981 | 0.99711
|  | N-1 Limiting section | 3580-2(1) | 3580-2(1) | 3580-2(1) | 3580-2(1) | 3580-2(1)
|  | Contingency Scenario | F465 | F465 | F465 | F465 | F465
F3590 | 3590-1 | Load (A) | 2.5697 | 22.5238 | 43.9591 | 64.8463 | 84.2485
|  | Rating (A) | 766 | 766 | 766 | 766 | 766
|  | Utilisation (%) | 0.33547 | 2.9404 | 5.7388 | 8.4656 | 10.9985
|  | Hosting Capacity (A) | 763.4303 | 743.4762 | 722.0409 | 701.1537 | 681.7515
|  | Power Factor | 0.25841 | 0.99657 | 0.99942 | 0.99919 | 0.99894
|  | N-1 Load (A) | 33.3333 | 53.1323 | 91.5841 | 128.9764 | 163.7257
|  | N-1 Rating (A) | 766 | 766 | 766 | 766 | 766
|  | Contingency Utilisation (%) | 4.3516 | 6.9363 | 11.9562 | 16.8377 | 21.3741
|  | N-1 Hosting Capacity (A) | 732.6667 | 712.8677 | 674.4159 | 637.0236 | 602.2743
|  | N-1 Power Factor | 0.25841 | 0.99961 | 0.99942 | 0.99919 | 0.99894
|  | N-1 Limiting section | 3590-1(3) | 3590-1(1) | 3590-1(1) | 3590-1(1) | 3590-1(1)
|  | Contingency Scenario | F3591 | F405 | F405 | F405 | F405
F3591 | 3591-1 | Load (A) | 33.6715 | 34.973 | 36.6549 | 38.5449 | 40.5117
|  | Rating (A) | 807 | 807 | 807 | 807 | 807
|  | Utilisation (%) | 4.1724 | 4.3337 | 4.5421 | 4.7763 | 5.02
|  | Hosting Capacity (A) | 773.3285 | 772.027 | 770.3451 | 768.4551 | 766.4883
|  | Power Factor | 0.99983 | 0.9992 | 0.99806 | 0.9964 | 0.99434
|  | N-1 Load (A) | 47.0962 | 65.6335 | 84.2826 | 102.7101 | 120.0638
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 5.836 | 8.133 | 10.4439 | 12.7274 | 14.8778
|  | N-1 Hosting Capacity (A) | 752.9038 | 734.3665 | 715.7174 | 697.2899 | 679.9362
|  | N-1 Power Factor | 0.99983 | 0.9992 | 0.99806 | 0.9964 | 0.99434
|  | N-1 Limiting section | 3591-1(1) | 3591-1(1) | 3591-1(1) | 3591-1(1) | 3591-1(1)
|  | Contingency Scenario | F405 | F405 | F405 | F405 | F405
F3601 | 3601-1 | Load (A) | 7.185 | 3.3902 | 1.5868 | 2.7575 | 4.6196
|  | Rating (A) | 713 | 713 | 800 | 713 | 713
|  | Utilisation (%) | 1.0111 | 0.48319 | 0.19835 | 0.38675 | 0.64791
|  | Hosting Capacity (A) | 705.815 | 709.6098 | 798.4132 | 710.2425 | 708.3804
|  | Power Factor | 0.99761 | 0.98725 | 1 | 0.95107 | 0.98274
|  | N-1 Load (A) | 14.6646 | 6.887 | 1.6933 | 5.4598 | 9.3411
|  | N-1 Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Contingency Utilisation (%) | 2.0567 | 0.96591 | 0.21166 | 0.76576 | 1.3101
|  | N-1 Hosting Capacity (A) | 698.3354 | 706.113 | 711.3067 | 707.5402 | 703.6589
|  | N-1 Power Factor | 0.99425 | 0.97152 | 1 | 0.95107 | 0.99199
|  | N-1 Limiting section | 3601-1(8) | 3601-1(8) | 3601-1(1) | 3601-1(8) | 3601-1(10)
|  | Contingency Scenario | F426 | F426 | F426 | F426 | F426
F361 | 361-1 | Load (A) | 29.0111 | 11.1956 | 8.7104 | 30.5614 | 52.6744
|  | Rating (A) | 631 | 631 | 631 | 631 | 631
|  | Utilisation (%) | 4.5976 | 1.7743 | 1.3804 | 4.8433 | 8.3478
|  | Hosting Capacity (A) | 601.9889 | 619.8044 | 622.2896 | 600.4386 | 578.3256
|  | Power Factor | 0.99929 | 0.99872 | 0.99984 | 0.99999 | 1
|  | N-1 Load (A) | 64.1592 | 39.8355 | 30.6248 | 52.0843 | 89.7584
|  | N-1 Rating (A) | 631 | 631 | 631 | 631 | 631
|  | Contingency Utilisation (%) | 10.1679 | 6.3131 | 4.8534 | 8.2542 | 14.2248
|  | N-1 Hosting Capacity (A) | 566.8408 | 591.1645 | 600.3752 | 578.9157 | 541.2416
|  | N-1 Power Factor | 0.99929 | 0.99872 | 0.99984 | 0.99999 | 1
|  | N-1 Limiting section | 361-1(1) | 361-1(1) | 361-1(1) | 361-1(1) | 361-1(1)
|  | Contingency Scenario | F354 | F354 | F355 | F411 | F411
F362 | 362-1 | Load (A) | 8.4503 | 14.6965 | 21.5895 | 28.5915 | 35.255
|  | Rating (A) | 357 | 357 | 357 | 357 | 357
|  | Utilisation (%) | 2.367 | 4.1219 | 6.0503 | 8.0103 | 9.8753
|  | Hosting Capacity (A) | 348.5497 | 342.3035 | 335.4105 | 328.4085 | 321.745
|  | Power Factor | 0.84009 | 0.96582 | 0.99037 | 0.99739 | 0.99948
|  | N-1 Load (A) | 21.024 | 35.9414 | 51.3546 | 66.4402 | 80.2239
|  | N-1 Rating (A) | 357 | 357 | 357 | 357 | 357
|  | Contingency Utilisation (%) | 5.8891 | 10.0676 | 14.385 | 18.6107 | 22.4717
|  | N-1 Hosting Capacity (A) | 335.976 | 321.0586 | 305.6454 | 290.5598 | 276.7761
|  | N-1 Power Factor | 0.84009 | 0.96466 | 0.98997 | 0.99739 | 0.99952
|  | N-1 Limiting section | 362-1(7) | 362-1(7) | 362-1(7) | 362-1(2) | 362-1(2)
|  | Contingency Scenario | F3960 | F3960 | F3960 | F3960 | F3960
F362 | 362-2 | Load (A) | 6.6014 | 6.7311 | 7.305 | 8.2401 | 9.3731
|  | Rating (A) | 708 | 708 | 708 | 708 | 708
|  | Utilisation (%) | 0.9324 | 0.95072 | 1.0318 | 1.1639 | 1.3239
|  | Hosting Capacity (A) | 701.3986 | 701.2689 | 700.695 | 699.7599 | 698.6269
|  | Power Factor | 0.84394 | 0.65999 | 0.43994 | 0.23103 | 1
|  | N-1 Load (A) | 17.5217 | 25.6053 | 33.4613 | 40.7984 | 47.1374
|  | N-1 Rating (A) | 708 | 708 | 708 | 708 | 708
|  | Contingency Utilisation (%) | 2.4748 | 3.6166 | 4.7262 | 5.7625 | 6.6578
|  | N-1 Hosting Capacity (A) | 690.4783 | 682.3947 | 674.5387 | 667.2016 | 660.8626
|  | N-1 Power Factor | 0.84394 | 0.65999 | 0.43994 | 0.23103 | 1
|  | N-1 Limiting section | 362-2 | 362-2 | 362-2 | 362-2 | 362-2
|  | Contingency Scenario | F3960 | F3960 | F3960 | F3960 | F3960
F362 | 362-3 | Load (A) | 7.7027 | 12.2023 | 19.884 | 28.0068 | 35.8728
|  | Rating (A) | 818 | 708 | 708 | 708 | 708
|  | Utilisation (%) | 0.94212 | 1.7235 | 2.8085 | 3.9558 | 5.0668
|  | Hosting Capacity (A) | 810.2973 | 695.7977 | 688.116 | 679.9932 | 672.1272
|  | Power Factor | 0.92088 | 0.7982 | 0.91296 | 0.94979 | 0.96602
|  | N-1 Load (A) | 10.1744 | 21.1802 | 35.4313 | 50.2197 | 64.4376
|  | N-1 Rating (A) | 708 | 708 | 708 | 708 | 708
|  | Contingency Utilisation (%) | 1.4371 | 2.9915 | 5.0044 | 7.0932 | 9.1014
|  | N-1 Hosting Capacity (A) | 697.8256 | 686.8198 | 672.5687 | 657.7803 | 643.5624
|  | N-1 Power Factor | 0.22817 | 0.7982 | 0.91296 | 0.94979 | 0.96602
|  | N-1 Limiting section | 362-3 | 362-3 | 362-3 | 362-3 | 362-3
|  | Contingency Scenario | F363 | F363 | F363 | F363 | F363
F363 | 363-1 | Load (A) | 8.114 | 14.1869 | 20.9191 | 27.7773 | 34.3105
|  | Rating (A) | 351 | 351 | 351 | 351 | 351
|  | Utilisation (%) | 2.3117 | 4.0419 | 5.9598 | 7.9138 | 9.7751
|  | Hosting Capacity (A) | 342.886 | 336.8131 | 330.0809 | 323.2227 | 316.6895
|  | Power Factor | 0.83708 | 0.96791 | 0.99243 | 0.9986 | 0.99995
|  | N-1 Load (A) | 19.7374 | 33.8424 | 48.4696 | 62.8091 | 75.93
|  | N-1 Rating (A) | 351 | 351 | 351 | 351 | 351
|  | Contingency Utilisation (%) | 5.6232 | 9.6417 | 13.809 | 17.8943 | 21.6325
|  | N-1 Hosting Capacity (A) | 331.2626 | 317.1576 | 302.5304 | 288.1909 | 275.07
|  | N-1 Power Factor | 0.83708 | 0.96791 | 0.99243 | 0.9986 | 0.99995
|  | N-1 Limiting section | 363-1(4) | 363-1(4) | 363-1(4) | 363-1(4) | 363-1(4)
|  | Contingency Scenario | F3960 | F3960 | F3960 | F3960 | F3960
F363 | 363-2 | Load (A) | 4.5913 | 4.704 | 4.7767 | 4.8044 | 4.7833
|  | Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Utilisation (%) | 1.1393 | 1.1673 | 1.1853 | 1.1922 | 1.1869
|  | Hosting Capacity (A) | 398.4087 | 398.296 | 398.2233 | 398.1956 | 398.2167
|  | Power Factor | 0.89651 | 0.91445 | 0.93088 | 0.94596 | 0.95924
|  | N-1 Load (A) | 14.6775 | 22.8735 | 30.8668 | 38.4056 | 45.0235
|  | N-1 Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Contingency Utilisation (%) | 3.642 | 5.6758 | 7.6593 | 9.5299 | 11.1721
|  | N-1 Hosting Capacity (A) | 388.3225 | 380.1265 | 372.1332 | 364.5944 | 357.9765
|  | N-1 Power Factor | 0.89651 | 0.91445 | 0.93088 | 0.94596 | 0.95924
|  | N-1 Limiting section | 363-2(1) | 363-2(1) | 363-2(1) | 363-2(1) | 363-2(1)
|  | Contingency Scenario | F3960 | F3960 | F3960 | F3960 | F3960
F363 | 363-3 | Load (A) | 5.5163 | 10.1817 | 16.5396 | 23.2429 | 29.7268
|  | Rating (A) | 374 | 374 | 374 | 374 | 374
|  | Utilisation (%) | 1.475 | 2.7224 | 4.4224 | 6.2147 | 7.9483
|  | Hosting Capacity (A) | 368.4837 | 363.8183 | 357.4604 | 350.7571 | 344.2732
|  | Power Factor | 0.48419 | 0.92509 | 0.98562 | 0.99755 | 0.99989
|  | N-1 Load (A) | 10.9009 | 21.5041 | 35.4825 | 50.0251 | 63.9768
|  | N-1 Rating (A) | 374 | 374 | 374 | 374 | 374
|  | Contingency Utilisation (%) | 2.9147 | 5.7498 | 9.4873 | 13.3757 | 17.1061
|  | N-1 Hosting Capacity (A) | 363.0991 | 352.4959 | 338.5175 | 323.9749 | 310.0232
|  | N-1 Power Factor | 0.48419 | 0.92509 | 0.98562 | 0.99755 | 0.99989
|  | N-1 Limiting section | 363-3(2) | 363-3(2) | 363-3(2) | 363-3(2) | 363-3(2)
|  | Contingency Scenario | F362 | F362 | F362 | F362 | F362
F364 | 364-1 | Load (A) | 32.1742 | 39.5386 | 51.239 | 54.5624 | 53.5639
|  | Rating (A) | 155 | 155 | 155 | 155 | 155
|  | Utilisation (%) | 20.7576 | 25.5088 | 33.0574 | 35.2015 | 34.5574
|  | Hosting Capacity (A) | 122.8258 | 115.4614 | 103.761 | 100.4376 | 101.4361
|  | Power Factor | 0.97847 | 0.98101 | 0.98322 | 0.98465 | 0.98574
|  | N-1 Load (A) | 47.4976 | 58.2352 | 76.044 | 80.2749 | 77.5482
|  | N-1 Rating (A) | 155 | 155 | 155 | 155 | 155
|  | Contingency Utilisation (%) | 30.6436 | 37.5711 | 49.0606 | 51.7902 | 50.0311
|  | N-1 Hosting Capacity (A) | 107.5024 | 96.7648 | 78.956 | 74.7251 | 77.4518
|  | N-1 Power Factor | 0.97847 | 0.98101 | 0.98322 | 0.98465 | 0.98574
|  | N-1 Limiting section | 364-1(1) | 364-1(1) | 364-1(1) | 364-1(1) | 364-1(1)
|  | Contingency Scenario | F366 | F366 | F366 | F366 | F366
F3640 | 3640-1 | Load (A) | 38.1028 | 61.2607 | 84.6166 | 110.4283 | 134.3999
|  | Rating (A) | 734 | 734 | 713 | 713 | 713
|  | Utilisation (%) | 5.1911 | 8.3461 | 11.8677 | 15.4878 | 18.8499
|  | Hosting Capacity (A) | 695.8972 | 672.7393 | 628.3834 | 602.5717 | 578.6001
|  | Power Factor | 0.82209 | 0.94134 | 0.99496 | 0.9985 | 0.99973
|  | N-1 Load (A) | 66.818 | 116.935 | 170.3137 | 222.889 | 271.6201
|  | N-1 Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Contingency Utilisation (%) | 9.1033 | 16.4004 | 23.8869 | 31.2607 | 38.0954
|  | N-1 Hosting Capacity (A) | 646.182 | 596.065 | 542.6863 | 490.111 | 441.3799
|  | N-1 Power Factor | 0.82209 | 0.9847 | 0.99496 | 0.9985 | 0.99973
|  | N-1 Limiting section | 3640-1 | 3640-1(3) | 3640-1(3) | 3640-1(3) | 3640-1(3)
|  | Contingency Scenario | F394 | F394 | F394 | F394 | F394
F3641 | 3641-1 | Load (A) | 40.4388 | 75.3601 | 104.3508 | 127.9863 | 146.1018
|  | Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Utilisation (%) | 5.6716 | 10.5694 | 14.6355 | 17.9504 | 20.4911
|  | Hosting Capacity (A) | 672.5612 | 637.6399 | 608.6492 | 585.0137 | 566.8982
|  | Power Factor | 0.9942 | 0.99929 | 0.99837 | 0.99728 | 0.99636
|  | N-1 Load (A) | 80.6139 | 150.8282 | 208.6458 | 255.7038 | 291.7557
|  | N-1 Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Contingency Utilisation (%) | 11.3063 | 21.154 | 29.2631 | 35.8631 | 40.9195
|  | N-1 Hosting Capacity (A) | 632.3861 | 562.1718 | 504.3542 | 457.2962 | 421.2443
|  | N-1 Power Factor | 0.9942 | 0.99929 | 0.99837 | 0.99728 | 0.99636
|  | N-1 Limiting section | 3641-1(1) | 3641-1(3) | 3641-1(3) | 3641-1(3) | 3641-1(3)
|  | Contingency Scenario | F3642 | F3642 | F3642 | F3642 | F3642
F3642 | 3642-1 | Load (A) | 40.7608 | 75.9511 | 105.1696 | 128.991 | 147.2489
|  | Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Utilisation (%) | 5.7168 | 10.6523 | 14.7503 | 18.0913 | 20.652
|  | Hosting Capacity (A) | 672.2392 | 637.0489 | 607.8304 | 584.009 | 565.7511
|  | Power Factor | 0.99407 | 0.9993 | 0.99839 | 0.9973 | 0.99638
|  | N-1 Load (A) | 80.6208 | 150.8349 | 208.6587 | 255.7227 | 291.7797
|  | N-1 Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Contingency Utilisation (%) | 11.3073 | 21.155 | 29.2649 | 35.8657 | 40.9228
|  | N-1 Hosting Capacity (A) | 632.3792 | 562.1651 | 504.3413 | 457.2773 | 421.2203
|  | N-1 Power Factor | 0.99407 | 0.9993 | 0.99839 | 0.9973 | 0.99638
|  | N-1 Limiting section | 3642-1(3) | 3642-1(1) | 3642-1(1) | 3642-1(1) | 3642-1(1)
|  | Contingency Scenario | F3641 | F3641 | F3641 | F3641 | F3641
F365 | 365-1 | Load (A) | 89.1612 | 108.0739 | 141.7326 | 146.4961 | 136.8867
|  | Rating (A) | 746 | 746 | 746 | 746 | 746
|  | Utilisation (%) | 11.9519 | 14.4871 | 18.999 | 19.6375 | 18.3494
|  | Hosting Capacity (A) | 656.8388 | 637.9261 | 604.2674 | 599.5039 | 609.1133
|  | Power Factor | 1 | 0.99974 | 0.99882 | 0.99845 | 0.99847
|  | N-1 Load (A) | 173.2043 | 210.4077 | 277.0693 | 286.6153 | 267.5733
|  | N-1 Rating (A) | 746 | 746 | 746 | 746 | 746
|  | Contingency Utilisation (%) | 23.2177 | 28.2048 | 37.1407 | 38.4203 | 35.8677
|  | N-1 Hosting Capacity (A) | 572.7957 | 535.5923 | 468.9307 | 459.3847 | 478.4267
|  | N-1 Power Factor | 1 | 0.99974 | 0.99882 | 0.99845 | 0.99847
|  | N-1 Limiting section | 365-1(1) | 365-1(1) | 365-1(1) | 365-1(1) | 365-1(1)
|  | Contingency Scenario | F366 | F366 | F366 | F366 | F366
F365 | 365-3 | Load (A) | 89.1596 | 108.0896 | 141.7715 | 146.5425 | 136.9351
|  | Rating (A) | 804 | 804 | 804 | 804 | 804
|  | Utilisation (%) | 11.0895 | 13.444 | 17.6333 | 18.2267 | 17.0317
|  | Hosting Capacity (A) | 714.8404 | 695.9104 | 662.2285 | 657.4575 | 667.0649
|  | Power Factor | 0.99998 | 0.9999 | 0.99953 | 0.99933 | 0.99925
|  | N-1 Load (A) | 173.2288 | 210.4521 | 277.1379 | 286.6917 | 267.6513
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 21.5459 | 26.1756 | 34.4699 | 35.6582 | 33.29
|  | N-1 Hosting Capacity (A) | 626.7712 | 589.5479 | 522.8621 | 513.3083 | 532.3487
|  | N-1 Power Factor | 0.99998 | 0.9999 | 0.99953 | 0.99933 | 0.99925
|  | N-1 Limiting section | 365-3 | 365-3 | 365-3 | 365-3 | 365-3
|  | Contingency Scenario | F366 | F366 | F366 | F366 | F366
F366 | 366-1 | Load (A) | 97.3429 | 117.9987 | 154.7567 | 159.9606 | 149.4699
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 11.9001 | 14.4253 | 18.9189 | 19.5551 | 18.2726
|  | Hosting Capacity (A) | 720.6571 | 700.0013 | 663.2433 | 658.0394 | 668.5301
|  | Power Factor | 0.99998 | 0.99974 | 0.99883 | 0.99847 | 0.99848
|  | N-1 Load (A) | 175.2216 | 212.8016 | 280.0484 | 289.6665 | 270.4633
|  | N-1 Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Contingency Utilisation (%) | 21.4207 | 26.0149 | 34.2358 | 35.4116 | 33.064
|  | N-1 Hosting Capacity (A) | 642.7784 | 605.1984 | 537.9516 | 528.3335 | 547.5367
|  | N-1 Power Factor | 0.99998 | 0.99974 | 0.99883 | 0.99847 | 0.99848
|  | N-1 Limiting section | 366-1 | 366-1 | 366-1 | 366-1 | 366-1
|  | Contingency Scenario | F365 | F365 | F365 | F365 | F365
F366 | 366-2 | Load (A) | 97.3412 | 118.0009 | 154.7638 | 159.9693 | 149.4791
|  | Rating (A) | 758 | 758 | 758 | 758 | 758
|  | Utilisation (%) | 12.8418 | 15.5674 | 20.4174 | 21.1041 | 19.7202
|  | Hosting Capacity (A) | 660.6588 | 639.9991 | 603.2362 | 598.0307 | 608.5209
|  | Power Factor | 0.99997 | 0.99996 | 0.99965 | 0.99948 | 0.99941
|  | N-1 Load (A) | 175.2253 | 212.8092 | 280.0607 | 289.6804 | 270.4777
|  | N-1 Rating (A) | 758 | 758 | 758 | 758 | 758
|  | Contingency Utilisation (%) | 23.1168 | 28.0751 | 36.9473 | 38.2164 | 35.6831
|  | N-1 Hosting Capacity (A) | 582.7747 | 545.1908 | 477.9393 | 468.3196 | 487.5223
|  | N-1 Power Factor | 0.99997 | 0.99996 | 0.99965 | 0.99948 | 0.99941
|  | N-1 Limiting section | 366-2 | 366-2 | 366-2 | 366-2 | 366-2
|  | Contingency Scenario | F365 | F365 | F365 | F365 | F365
F367 | 367-1 | Load (A) | 64.7376 | 52.5744 | 42.1517 | 28.9681 | 19.3493
|  | Rating (A) | 530 | 530 | 530 | 530 | 530
|  | Utilisation (%) | 12.2146 | 9.9197 | 7.9532 | 5.4657 | 3.6508
|  | Hosting Capacity (A) | 465.2624 | 477.4256 | 487.8483 | 501.0319 | 510.6507
|  | Power Factor | 0.99924 | 0.99866 | 0.9973 | 0.99504 | 0.98413
|  | N-1 Load (A) | 133.2667 | 112.4287 | 95.0113 | 95.8335 | 111.9898
|  | N-1 Rating (A) | 530 | 530 | 530 | 530 | 530
|  | Contingency Utilisation (%) | 25.1447 | 21.213 | 17.9267 | 18.0818 | 21.1301
|  | N-1 Hosting Capacity (A) | 396.7333 | 417.5713 | 434.9887 | 434.1665 | 418.0102
|  | N-1 Power Factor | 0.99924 | 0.99866 | 0.9973 | 0.99504 | 0.98413
|  | N-1 Limiting section | 367-1 | 367-1 | 367-1 | 367-1 | 367-1
|  | Contingency Scenario | F368 | F368 | F368 | F420 | F420
F3670 | 3670-1 | Load (A) | 88.1591 | 75.1864 | 61.5206 | 47.3364 | 33.2771
|  | Rating (A) | 710 | 710 | 710 | 710 | 710
|  | Utilisation (%) | 12.4168 | 10.5896 | 8.6649 | 6.6671 | 4.6869
|  | Hosting Capacity (A) | 621.8409 | 634.8136 | 648.4794 | 662.6636 | 676.7229
|  | Power Factor | 0.99932 | 0.99891 | 0.99836 | 0.99762 | 0.99663
|  | N-1 Load (A) | 132.8384 | 113.25 | 92.6197 | 90.6524 | 89.6508
|  | N-1 Rating (A) | 710 | 710 | 710 | 710 | 710
|  | Contingency Utilisation (%) | 18.7096 | 15.9507 | 13.045 | 12.7679 | 12.6269
|  | N-1 Hosting Capacity (A) | 577.1616 | 596.75 | 617.3803 | 619.3476 | 620.3492
|  | N-1 Power Factor | 0.99981 | 0.99965 | 0.99836 | 0.99935 | 0.99938
|  | N-1 Limiting section | 3670-1(2) | 3670-1(2) | 3670-1(3) | 3670-1(2) | 3670-1(2)
|  | Contingency Scenario | F3671 | F3671 | F3671 | F389 | F389
F3671 | 3671-1 | Load (A) | 70.0466 | 59.7173 | 48.8374 | 37.5467 | 26.3603
|  | Rating (A) | 708 | 708 | 708 | 708 | 708
|  | Utilisation (%) | 9.8936 | 8.4346 | 6.8979 | 5.3032 | 3.7232
|  | Hosting Capacity (A) | 637.9534 | 648.2827 | 659.1626 | 670.4533 | 681.6397
|  | Power Factor | 0.99875 | 0.99845 | 0.99821 | 0.99813 | 0.99848
|  | N-1 Load (A) | 121.4893 | 103.5537 | 84.67 | 72.0563 | 71.2601
|  | N-1 Rating (A) | 708 | 708 | 708 | 708 | 708
|  | Contingency Utilisation (%) | 17.1595 | 14.6262 | 11.959 | 10.1774 | 10.065
|  | N-1 Hosting Capacity (A) | 586.5107 | 604.4463 | 623.33 | 635.9437 | 636.7399
|  | N-1 Power Factor | 0.99875 | 0.99845 | 0.99821 | 0.99813 | 0.99848
|  | N-1 Limiting section | 3671-1(4) | 3671-1(4) | 3671-1(4) | 3671-1(4) | 3671-1(4)
|  | Contingency Scenario | F3670 | F3670 | F3670 | F389 | F389
F368 | 368-1 | Load (A) | 68.6909 | 60.0413 | 53.0642 | 43.7754 | 37.3755
|  | Rating (A) | 529 | 529 | 529 | 529 | 529
|  | Utilisation (%) | 12.985 | 11.35 | 10.031 | 8.282 | 7.074
|  | Hosting Capacity (A) | 460.3091 | 468.9587 | 475.9358 | 485.2246 | 491.6245
|  | Power Factor | 0.99759 | 0.99665 | 0.99511 | 0.99495 | 0.99193
|  | N-1 Load (A) | 177.4027 | 173.9046 | 173.8923 | 169.6697 | 169.6697
|  | N-1 Rating (A) | 529 | 529 | 529 | 529 | 529
|  | Contingency Utilisation (%) | 33.5355 | 32.8742 | 32.8719 | 32.0737 | 32.0737
|  | N-1 Hosting Capacity (A) | 351.5973 | 355.0954 | 355.1077 | 359.3303 | 359.3303
|  | N-1 Power Factor | 0.99759 | 0.99668 | 0.9953 | 0.99495 | 0.99193
|  | N-1 Limiting section | 368-1(13) | 368-1 | 368-1 | 368-1 | 368-1
|  | Contingency Scenario | F420 | F420 | F420 | F420 | F420
F369 | 369-1 | Load (A) | 27.9082 | 21.007 | 13.9212 | 6.8085 | 0.82291
|  | Rating (A) | 499 | 499 | 499 | 499 | 499
|  | Utilisation (%) | 5.5928 | 4.2098 | 2.7898 | 1.3644 | 0.16491
|  | Hosting Capacity (A) | 471.0918 | 477.993 | 485.0788 | 492.1915 | 498.1771
|  | Power Factor | 0.99897 | 0.99867 | 0.99769 | 0.99203 | 1
|  | N-1 Load (A) | 56.4363 | 42.4567 | 28.1214 | 13.7468 | 1.6736
|  | N-1 Rating (A) | 499 | 499 | 499 | 499 | 499
|  | Contingency Utilisation (%) | 11.3099 | 8.5084 | 5.6355 | 2.7549 | 0.3354
|  | N-1 Hosting Capacity (A) | 442.5637 | 456.5433 | 470.8786 | 485.2532 | 497.3264
|  | N-1 Power Factor | 0.99897 | 0.99867 | 0.99769 | 0.99203 | 1
|  | N-1 Limiting section | 369-1(3) | 369-1(3) | 369-1(3) | 369-1(3) | 369-1(3)
|  | Contingency Scenario | F370 | F370 | F370 | F370 | F370
F370 | 370-1 | Load (A) | 28.4061 | 21.3811 | 14.1683 | 6.9286 | 0.85152
|  | Rating (A) | 499 | 499 | 499 | 499 | 499
|  | Utilisation (%) | 5.6926 | 4.2848 | 2.8393 | 1.3885 | 0.17065
|  | Hosting Capacity (A) | 470.5939 | 477.6189 | 484.8317 | 492.0714 | 498.1485
|  | Power Factor | 0.99912 | 0.99883 | 0.99788 | 0.99225 | 1
|  | N-1 Load (A) | 56.4374 | 42.4574 | 28.1216 | 13.7467 | 1.6737
|  | N-1 Rating (A) | 499 | 499 | 499 | 499 | 499
|  | Contingency Utilisation (%) | 11.3101 | 8.5085 | 5.6356 | 2.7549 | 0.33541
|  | N-1 Hosting Capacity (A) | 442.5626 | 456.5426 | 470.8784 | 485.2533 | 497.3263
|  | N-1 Power Factor | 0.99912 | 0.99883 | 0.99788 | 0.99225 | 1
|  | N-1 Limiting section | 370-1(3) | 370-1(3) | 370-1(3) | 370-1(3) | 370-1(3)
|  | Contingency Scenario | F369 | F369 | F369 | F369 | F369
F3700 | 3700-1 | Load (A) | 36.641 | 55.7866 | 75.1872 | 94.4092 | 112.5021
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 4.4793 | 6.8199 | 9.1916 | 11.5415 | 13.7533
|  | Hosting Capacity (A) | 781.359 | 762.2134 | 742.8128 | 723.5908 | 705.4979
|  | Power Factor | 0.99992 | 0.99935 | 0.99854 | 0.99758 | 0.99655
|  | N-1 Load (A) | 76.2388 | 116.007 | 156.2506 | 196.0638 | 233.531
|  | N-1 Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Contingency Utilisation (%) | 9.3201 | 14.1818 | 19.1015 | 23.9687 | 28.549
|  | N-1 Hosting Capacity (A) | 741.7612 | 701.993 | 661.7494 | 621.9362 | 584.469
|  | N-1 Power Factor | 0.99992 | 0.99935 | 0.99854 | 0.99758 | 0.99655
|  | N-1 Limiting section | 3700-1(2) | 3700-1(2) | 3700-1(2) | 3700-1(2) | 3700-1(2)
|  | Contingency Scenario | F3701 | F3701 | F3701 | F3701 | F3701
F3700 | 3700-3 | Load (A) | 36.641 | 55.7866 | 75.1872 | 94.4092 | 112.5193
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 4.4797 | 6.8208 | 9.193 | 11.5433 | 13.7554
|  | Hosting Capacity (A) | 781.359 | 762.2134 | 742.8128 | 723.5908 | 705.4807
|  | Power Factor | 0.99992 | 0.99935 | 0.99854 | 0.99758 | 0.99678
|  | N-1 Load (A) | 76.2443 | 116.0159 | 156.2627 | 196.0789 | 233.5488
|  | N-1 Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Contingency Utilisation (%) | 9.3208 | 14.1829 | 19.103 | 23.9705 | 28.5512
|  | N-1 Hosting Capacity (A) | 741.7557 | 701.9841 | 661.7373 | 621.9211 | 584.4512
|  | N-1 Power Factor | 0.99992 | 0.99935 | 0.99854 | 0.99758 | 0.99655
|  | N-1 Limiting section | 3700-1(2) | 3700-1(2) | 3700-1(2) | 3700-1(2) | 3700-1(2)
|  | Contingency Scenario | F3701 | F3701 | F3701 | F3701 | F3701
F3700 | 3700-5 | Load (A) | 36.641 | 55.7866 | 75.1872 | 94.4402 | 112.5193
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 4.4803 | 6.822 | 9.1946 | 11.5452 | 13.7578
|  | Hosting Capacity (A) | 781.359 | 762.2134 | 742.8128 | 723.5598 | 705.4807
|  | Power Factor | 0.99992 | 0.99935 | 0.99854 | 0.99771 | 0.99678
|  | N-1 Load (A) | 76.2508 | 116.0256 | 156.2755 | 196.0948 | 233.5674
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 9.3216 | 14.1841 | 19.1046 | 23.9725 | 28.5535
|  | N-1 Hosting Capacity (A) | 723.7492 | 683.9744 | 643.7245 | 603.9052 | 566.4326
|  | N-1 Power Factor | 0.99992 | 0.99935 | 0.99854 | 0.99758 | 0.99655
|  | N-1 Limiting section | 3700-1(2) | 3700-1(2) | 3700-1(2) | 3700-1(2) | 3700-1(2)
|  | Contingency Scenario | F3701 | F3701 | F3701 | F3701 | F3701
F3701 | 3701-1 | Load (A) | 39.6868 | 60.4039 | 81.3969 | 102.1963 | 121.7739
|  | Rating (A) | 529 | 529 | 529 | 529 | 529
|  | Utilisation (%) | 7.5022 | 11.4185 | 15.3869 | 19.3188 | 23.0196
|  | Hosting Capacity (A) | 489.3132 | 468.5961 | 447.6031 | 426.8037 | 407.2261
|  | Power Factor | 0.99993 | 0.99993 | 0.99958 | 0.99901 | 0.99833
|  | N-1 Load (A) | 76.2428 | 116.0199 | 156.2898 | 196.1494 | 233.6625
|  | N-1 Rating (A) | 529 | 529 | 529 | 529 | 529
|  | Contingency Utilisation (%) | 14.4126 | 21.9319 | 29.5444 | 37.0793 | 44.1706
|  | N-1 Hosting Capacity (A) | 452.7572 | 412.9801 | 372.7102 | 332.8506 | 295.3375
|  | N-1 Power Factor | 0.99993 | 0.99993 | 0.99958 | 0.99901 | 0.99833
|  | N-1 Limiting section | 3701-1(4) | 3701-1(4) | 3701-1(4) | 3701-1(4) | 3701-1(4)
|  | Contingency Scenario | F3700 | F3700 | F3700 | F3700 | F3700
F3702 | 3702-1 | Load (A) | 20.4389 | 20.4276 | 20.4169 | 20.4072 | 20.3988
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 2.4986 | 2.4973 | 2.496 | 2.4948 | 2.4937
|  | Hosting Capacity (A) | 797.5611 | 797.5724 | 797.5831 | 797.5928 | 797.6012
|  | Power Factor | 0.99972 | 0.99972 | 0.99972 | 0.99972 | 0.99972
F3702 | 3702-3 | Load (A) | 20.435 | 20.4237 | 20.413 | 20.4033 | 20.3949
|  | Rating (A) | 271 | 271 | 271 | 271 | 271
|  | Utilisation (%) | 7.5406 | 7.5364 | 7.5325 | 7.5289 | 7.5258
|  | Hosting Capacity (A) | 250.565 | 250.5763 | 250.587 | 250.5967 | 250.6051
|  | Power Factor | 0.99989 | 0.99989 | 0.99989 | 0.99989 | 0.99989
F3702 | 3702-4 | Load (A) | 18.6847 | 18.6743 | 18.6644 | 18.6554 | 18.6477
|  | Rating (A) | 355 | 355 | 355 | 355 | 355
|  | Utilisation (%) | 5.2633 | 5.2604 | 5.2576 | 5.2551 | 5.2529
|  | Hosting Capacity (A) | 336.3153 | 336.3257 | 336.3356 | 336.3446 | 336.3523
|  | Power Factor | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992
F3702 | 3702-5 | Load (A) | 1.7509 | 1.75 | 1.7491 | 1.7483 | 1.7477
|  | Rating (A) | 207 | 207 | 207 | 207 | 207
|  | Utilisation (%) | 0.84583 | 0.84539 | 0.84498 | 0.8446 | 0.84428
|  | Hosting Capacity (A) | 205.2491 | 205.25 | 205.2509 | 205.2517 | 205.2523
|  | Power Factor | 0.99925 | 0.99924 | 0.99924 | 0.99924 | 0.99924
F3702 | 3702-6 | Load (A) | 1.7564 | 1.7555 | 1.7547 | 1.7539 | 1.7532
|  | Rating (A) | 231 | 231 | 231 | 231 | 231
|  | Utilisation (%) | 0.76035 | 0.75996 | 0.75959 | 0.75926 | 0.75897
|  | Hosting Capacity (A) | 229.2436 | 229.2445 | 229.2453 | 229.2461 | 229.2468
|  | Power Factor | 0.9961 | 0.99609 | 0.99608 | 0.99607 | 0.99607
F371 | 371-1 | Load (A) | 46.9789 | 82.8447 | 119.6814 | 156.8172 | 192.464
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 5.7431 | 10.1277 | 14.631 | 19.1708 | 23.5286
|  | Hosting Capacity (A) | 771.0211 | 735.1553 | 698.3186 | 661.1828 | 625.536
|  | Power Factor | 0.99976 | 0.99942 | 0.99878 | 0.99793 | 0.99689
|  | N-1 Load (A) | 117.0338 | 163.9684 | 211.7388 | 259.7032 | 305.7744
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 14.3073 | 20.045 | 25.8849 | 31.7486 | 37.3807
|  | N-1 Hosting Capacity (A) | 682.9662 | 636.0316 | 588.2612 | 540.2968 | 494.2256
|  | N-1 Power Factor | 0.99976 | 0.99942 | 0.99878 | 0.99793 | 0.99689
|  | N-1 Limiting section | 371-1(2) | 371-1(2) | 371-1(2) | 371-1(2) | 371-1(2)
|  | Contingency Scenario | F484 | F484 | F484 | F484 | F484
F372 | 372-1 | Load (A) | 9.9013 | 38.8751 | 70.0675 | 101.8748 | 132.4681
|  | Rating (A) | 611 | 611 | 611 | 611 | 611
|  | Utilisation (%) | 1.6205 | 6.3625 | 11.4677 | 16.6735 | 21.6805
|  | Hosting Capacity (A) | 601.0987 | 572.1249 | 540.9325 | 509.1252 | 478.5319
|  | Power Factor | 0.83011 | 0.99355 | 0.99898 | 0.99853 | 0.99799
|  | N-1 Load (A) | 20.6286 | 74.9133 | 135.7411 | 197.3461 | 256.592
|  | N-1 Rating (A) | 686 | 686 | 686 | 686 | 686
|  | Contingency Utilisation (%) | 3.3762 | 12.2608 | 22.2162 | 32.2989 | 41.9954
|  | N-1 Hosting Capacity (A) | 665.3714 | 611.0867 | 550.2589 | 488.6539 | 429.408
|  | N-1 Power Factor | 0.83011 | 0.99355 | 0.99898 | 0.99853 | 0.99799
|  | N-1 Limiting section | 372-1 | 372-1 | 372-1 | 372-1 | 372-1
|  | Contingency Scenario | F371 | F413 | F413 | F413 | F413
F373 | 373-1 | Load (A) | 6.2884 | 33.2353 | 61.178 | 89.422 | 116.5369
|  | Rating (A) | 715 | 715 | 715 | 715 | 715
|  | Utilisation (%) | 0.88441 | 4.6516 | 8.5564 | 12.5106 | 16.3033
|  | Hosting Capacity (A) | 708.7116 | 681.7647 | 653.822 | 625.578 | 598.4631
|  | Power Factor | 0.99661 | 0.99762 | 0.99696 | 0.99595 | 0.99483
|  | N-1 Load (A) | 30.2921 | 75.4029 | 121.8849 | 168.7774 | 213.7277
|  | N-1 Rating (A) | 715 | 715 | 715 | 715 | 715
|  | Contingency Utilisation (%) | 4.2367 | 10.5459 | 17.0468 | 23.6052 | 29.892
|  | N-1 Hosting Capacity (A) | 684.7079 | 639.5971 | 593.1151 | 546.2226 | 501.2723
|  | N-1 Power Factor | 0.99113 | 0.99713 | 0.99696 | 0.9964 | 0.99483
|  | N-1 Limiting section | 373-1(2) | 373-1(2) | 373-1(2) | 373-1(2) | 373-1(10)
|  | Contingency Scenario | F371 | F371 | F371 | F371 | F371
F374 | 374-1 | Load (A) | 12.2905 | 44.0843 | 77.0985 | 110.5768 | 142.6919
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 1.5025 | 5.3893 | 9.4252 | 13.518 | 17.444
|  | Hosting Capacity (A) | 805.7095 | 773.9157 | 740.9015 | 707.4232 | 675.3081
|  | Power Factor | 0.99944 | 0.99991 | 0.99967 | 0.99918 | 0.99855
|  | N-1 Load (A) | 43.0132 | 84.18 | 134.8463 | 186.0269 | 235.0925
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 5.2583 | 10.291 | 16.4849 | 22.7417 | 28.7399
|  | N-1 Hosting Capacity (A) | 756.9868 | 715.82 | 665.1537 | 613.9731 | 564.9075
|  | N-1 Power Factor | 0.99944 | 0.99991 | 0.99967 | 0.99918 | 0.99855
|  | N-1 Limiting section | 374-1(1) | 374-1(1) | 374-1(1) | 374-1(1) | 374-1(1)
|  | Contingency Scenario | F3570 | F371 | F371 | F371 | F371
F375 | 375-1 | Load (A) | 23.2738 | 36.3033 | 49.409 | 62.3407 | 74.4727
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 4.209 | 6.5648 | 8.9347 | 11.2732 | 13.467
|  | Hosting Capacity (A) | 529.7262 | 516.6967 | 503.591 | 490.6593 | 478.5273
|  | Power Factor | 0.99987 | 0.99987 | 0.99941 | 0.99883 | 0.9982
|  | N-1 Load (A) | 88.8323 | 125.5979 | 162.3031 | 198.2607 | 231.814
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 16.0637 | 22.7121 | 29.3496 | 35.8518 | 41.9194
|  | N-1 Hosting Capacity (A) | 464.1677 | 427.4021 | 390.6969 | 354.7393 | 321.186
|  | N-1 Power Factor | 0.99987 | 0.99987 | 0.99941 | 0.99883 | 0.9982
|  | N-1 Limiting section | 375-1(1) | 375-1(1) | 375-1(1) | 375-1(1) | 375-1(1)
|  | Contingency Scenario | F465 | F465 | F465 | F465 | F465
F375 | 375-2 | Load (A) | 23.2738 | 36.3053 | 49.4113 | 62.351 | 74.4727
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 4.2085 | 6.5665 | 8.9378 | 11.2772 | 13.4719
|  | Hosting Capacity (A) | 529.7262 | 516.6947 | 503.5887 | 490.649 | 478.5273
|  | Power Factor | 0.99987 | 0.99984 | 0.9994 | 0.99885 | 0.9982
|  | N-1 Load (A) | 88.8455 | 125.6179 | 162.3295 | 198.293 | 231.8517
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 16.0661 | 22.7157 | 29.3543 | 35.8577 | 41.9262
|  | N-1 Hosting Capacity (A) | 464.1545 | 427.3821 | 390.6705 | 354.707 | 321.1483
|  | N-1 Power Factor | 0.99998 | 0.99971 | 0.99941 | 0.99885 | 0.99833
|  | N-1 Limiting section | 375-2(4) | 375-2(4) | 375-1(1) | 375-2(4) | 375-2(4)
|  | Contingency Scenario | F465 | F465 | F465 | F465 | F465
F3751 | 3751-1 | Load (A) | 263.6259 | 242.9857 | 221.1989 | 198.4874 | 175.9126
|  | Rating (A) | 606 | 606 | 606 | 606 | 606
|  | Utilisation (%) | 43.5026 | 40.0966 | 36.5015 | 32.7537 | 29.0285
|  | Hosting Capacity (A) | 342.3741 | 363.0143 | 384.8011 | 407.5126 | 430.0874
|  | Power Factor | 0.99894 | 0.99894 | 0.99879 | 0.99849 | 0.99798
|  | N-1 Load (A) | 435.6444 | 401.4495 | 365.3837 | 327.8166 | 290.4696
|  | N-1 Rating (A) | 695 | 695 | 695 | 695 | 695
|  | Contingency Utilisation (%) | 71.8885 | 66.2458 | 60.2943 | 54.0951 | 47.9323
|  | N-1 Hosting Capacity (A) | 259.3556 | 293.5505 | 329.6163 | 367.1834 | 404.5304
|  | N-1 Power Factor | 0.99894 | 0.99894 | 0.99879 | 0.99849 | 0.99798
|  | N-1 Limiting section | 3751-1 | 3751-1 | 3751-1 | 3751-1 | 3751-1
|  | Contingency Scenario | F3755 | F3755 | F3755 | F3755 | F3755
F3754 | 3754-1 | Load (A) | 251.8401 | 251.7556 | 251.6745 | 251.593 | 251.5151
|  | Rating (A) | 687 | 687 | 687 | 687 | 687
|  | Utilisation (%) | 36.6579 | 36.6457 | 36.6339 | 36.622 | 36.6106
|  | Hosting Capacity (A) | 435.1599 | 435.2444 | 435.3255 | 435.407 | 435.4849
|  | Power Factor | 0.99884 | 0.99885 | 0.99885 | 0.99885 | 0.99885
|  | N-1 Load (A) | 507.3076 | 507.1334 | 506.9661 | 506.798 | 506.6369
|  | N-1 Rating (A) | 687 | 687 | 687 | 687 | 687
|  | Contingency Utilisation (%) | 73.8439 | 73.8185 | 73.7942 | 73.7697 | 73.7463
|  | N-1 Hosting Capacity (A) | 179.6924 | 179.8666 | 180.0339 | 180.202 | 180.3631
|  | N-1 Power Factor | 0.99884 | 0.99885 | 0.99885 | 0.99885 | 0.99885
|  | N-1 Limiting section | 3754-1 | 3754-1 | 3754-1 | 3754-1 | 3754-1
|  | Contingency Scenario | F3757 | F3757 | F3757 | F3757 | F3757
F3755 | 3755-1 | Load (A) | 263.4836 | 242.8545 | 221.0794 | 198.3801 | 175.8173
|  | Rating (A) | 606 | 606 | 606 | 606 | 606
|  | Utilisation (%) | 43.4791 | 40.075 | 36.4817 | 32.736 | 29.0128
|  | Hosting Capacity (A) | 342.5164 | 363.1455 | 384.9206 | 407.6199 | 430.1827
|  | Power Factor | 0.99894 | 0.99895 | 0.99879 | 0.99849 | 0.99798
|  | N-1 Load (A) | 435.5621 | 401.3736 | 365.3144 | 327.7542 | 290.414
|  | N-1 Rating (A) | 695 | 695 | 695 | 695 | 695
|  | Contingency Utilisation (%) | 71.8749 | 66.2333 | 60.2829 | 54.0848 | 47.9231
|  | N-1 Hosting Capacity (A) | 259.4379 | 293.6264 | 329.6856 | 367.2458 | 404.586
|  | N-1 Power Factor | 0.99894 | 0.99895 | 0.99879 | 0.99849 | 0.99798
|  | N-1 Limiting section | 3755-1 | 3755-1 | 3755-1 | 3755-1 | 3755-1
|  | Contingency Scenario | F3751 | F3751 | F3751 | F3751 | F3751
F3756 | 3756-1 | Load (A) | 69.1685 | 61.8118 | 54.0916 | 46.0818 | 38.1642
|  | Rating (A) | 715 | 715 | 715 | 715 | 715
|  | Utilisation (%) | 9.6744 | 8.6455 | 7.5653 | 6.4456 | 5.3382
|  | Hosting Capacity (A) | 645.8315 | 653.1882 | 660.9084 | 668.9182 | 676.8358
|  | Power Factor | 0.99954 | 0.99934 | 0.99929 | 0.99933 | 0.99945
|  | N-1 Load (A) | 113.825 | 102.9388 | 91.4994 | 79.6293 | 67.8707
|  | N-1 Rating (A) | 715 | 715 | 715 | 715 | 715
|  | Contingency Utilisation (%) | 15.9196 | 14.397 | 12.7971 | 11.137 | 9.4924
|  | N-1 Hosting Capacity (A) | 601.175 | 612.0612 | 623.5006 | 635.3707 | 647.1293
|  | N-1 Power Factor | 0.99954 | 0.99934 | 0.99931 | 0.99933 | 0.99945
|  | N-1 Limiting section | 3756-1(1) | 3756-1(1) | 3756-1(1) | 3756-1(1) | 3756-1(1)
|  | Contingency Scenario | F3751 | F3751 | F3751 | F3751 | F3751
F3756 | 3756-2 | Load (A) | 66.4243 | 81.1656 | 96.1823 | 111.3126 | 125.8714
|  | Rating (A) | 532 | 532 | 532 | 532 | 532
|  | Utilisation (%) | 12.4858 | 15.2567 | 18.0794 | 20.9234 | 23.66
|  | Hosting Capacity (A) | 465.5757 | 450.8344 | 435.8177 | 420.6874 | 406.1286
|  | Power Factor | 0.99831 | 0.99947 | 0.99957 | 0.9996 | 0.99958
|  | N-1 Load (A) | 115.3878 | 126.3507 | 137.3337 | 148.2538 | 158.6101
|  | N-1 Rating (A) | 532 | 532 | 532 | 532 | 532
|  | Contingency Utilisation (%) | 21.6894 | 23.7501 | 25.8146 | 27.8673 | 29.8139
|  | N-1 Hosting Capacity (A) | 416.6122 | 405.6493 | 394.6663 | 383.7462 | 373.3899
|  | N-1 Power Factor | 0.99831 | 0.99947 | 0.99957 | 0.9996 | 0.99958
|  | N-1 Limiting section | 3756-2(1) | 3756-2(1) | 3756-2(1) | 3756-2(1) | 3756-2(1)
|  | Contingency Scenario | F3751 | F3751 | F3751 | F3751 | F3751
F3756 | 3756-3 | Load (A) | 135.5781 | 142.9758 | 150.2674 | 157.392 | 164.0341
|  | Rating (A) | 636 | 636 | 636 | 636 | 636
|  | Utilisation (%) | 21.3173 | 22.4805 | 23.627 | 24.7472 | 25.7915
|  | Hosting Capacity (A) | 500.4219 | 493.0242 | 485.7326 | 478.608 | 471.9659
|  | Power Factor | 0.99897 | 0.99937 | 0.99943 | 0.99947 | 0.99949
|  | N-1 Load (A) | 229.2048 | 229.2872 | 228.8311 | 227.881 | 226.4764
|  | N-1 Rating (A) | 636 | 636 | 636 | 636 | 636
|  | Contingency Utilisation (%) | 36.0385 | 36.0514 | 35.9797 | 35.8303 | 35.6095
|  | N-1 Hosting Capacity (A) | 406.7952 | 406.7128 | 407.1689 | 408.119 | 409.5236
|  | N-1 Power Factor | 0.99897 | 0.99937 | 0.99943 | 0.99947 | 0.99949
|  | N-1 Limiting section | 3756-3(1) | 3756-3(1) | 3756-3(1) | 3756-3(1) | 3756-3(1)
|  | Contingency Scenario | F3751 | F3751 | F3751 | F3751 | F3751
F3756 | 3756-4 | Load (A) | 135.5776 | 142.9754 | 150.2671 | 157.3916 | 164.0337
|  | Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Utilisation (%) | 18.909 | 19.9408 | 20.9578 | 21.9514 | 22.8778
|  | Hosting Capacity (A) | 581.4224 | 574.0246 | 566.7329 | 559.6084 | 552.9663
|  | Power Factor | 0.99897 | 0.99937 | 0.99943 | 0.99947 | 0.99949
|  | N-1 Load (A) | 229.2046 | 229.287 | 228.8309 | 227.8808 | 226.4762
|  | N-1 Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Contingency Utilisation (%) | 31.9672 | 31.9787 | 31.915 | 31.7825 | 31.5866
|  | N-1 Hosting Capacity (A) | 487.7954 | 487.713 | 488.1691 | 489.1192 | 490.5238
|  | N-1 Power Factor | 0.99897 | 0.99937 | 0.99943 | 0.99947 | 0.99949
|  | N-1 Limiting section | 3756-4 | 3756-4 | 3756-4 | 3756-4 | 3756-4
|  | Contingency Scenario | F3751 | F3751 | F3751 | F3751 | F3751
F3757 | 3757-1 | Load (A) | 251.9006 | 251.8162 | 251.735 | 251.6534 | 251.5755
|  | Rating (A) | 687 | 687 | 687 | 687 | 687
|  | Utilisation (%) | 36.6668 | 36.6545 | 36.6427 | 36.6308 | 36.6194
|  | Hosting Capacity (A) | 435.0994 | 435.1838 | 435.265 | 435.3466 | 435.4245
|  | Power Factor | 0.99884 | 0.99884 | 0.99884 | 0.99885 | 0.99885
|  | N-1 Load (A) | 507.3019 | 507.1277 | 506.9605 | 506.7923 | 506.6313
|  | N-1 Rating (A) | 687 | 687 | 687 | 687 | 687
|  | Contingency Utilisation (%) | 73.8431 | 73.8177 | 73.7934 | 73.7689 | 73.7455
|  | N-1 Hosting Capacity (A) | 179.6981 | 179.8723 | 180.0395 | 180.2077 | 180.3687
|  | N-1 Power Factor | 0.99884 | 0.99884 | 0.99884 | 0.99885 | 0.99885
|  | N-1 Limiting section | 3757-1 | 3757-1 | 3757-1 | 3757-1 | 3757-1
|  | Contingency Scenario | F3754 | F3754 | F3754 | F3754 | F3754
F376 | 376-1 | Load (A) | 5.0197 | 9.3299 | 13.663 | 17.9099 | 21.8518
|  | Rating (A) | 290 | 290 | 290 | 290 | 290
|  | Utilisation (%) | 1.7309 | 3.2172 | 4.7114 | 6.1758 | 7.5351
|  | Hosting Capacity (A) | 284.9803 | 280.6701 | 276.337 | 272.0901 | 268.1482
|  | Power Factor | 0.99052 | 0.99768 | 0.9992 | 0.99971 | 0.99991
|  | N-1 Load (A) |  |  | 13.6552 | 17.9094 | 21.8566
|  | N-1 Rating (A) | 290 | 290 | 290 | 290 | 290
|  | Contingency Utilisation (%) |  |  | 4.6605 | 6.1124 | 7.4596
|  | N-1 Hosting Capacity (A) |  |  | 276.3448 | 272.0906 | 268.1434
|  | N-1 Power Factor | 1 | 1 | 0.99989 | 0.99999 | 1
|  | N-1 Limiting section | 376-1(5) | 376-1(5) | 376-1(3) | 376-1(3) | 376-1(3)
|  | Contingency Scenario |  |  | F3844 | F3844 | F3844
F377 | 377-1 | Load (A) | 4.884 | 10.8993 | 24.7443 | 38.8075 | 52.1637
|  | Rating (A) | 821 | 821 | 821 | 821 | 821
|  | Utilisation (%) | 0.59489 | 1.3276 | 3.0139 | 4.7269 | 6.3537
|  | Hosting Capacity (A) | 816.116 | 810.1007 | 796.2557 | 782.1925 | 768.8363
|  | Power Factor | 0.71871 | 0.95143 | 0.99197 | 0.99755 | 0.99915
|  | N-1 Load (A) | 8.2263 | 30.8962 | 55.7086 | 80.5229 | 103.9797
|  | N-1 Rating (A) | 959 | 959 | 959 | 959 | 959
|  | Contingency Utilisation (%) | 1.002 | 3.7632 | 6.7855 | 9.8079 | 12.665
|  | N-1 Hosting Capacity (A) | 950.7737 | 928.1038 | 903.2914 | 878.4771 | 855.0203
|  | N-1 Power Factor | 0.71871 | 0.95143 | 0.99197 | 0.99755 | 0.99915
|  | N-1 Limiting section | 377-1 | 377-1 | 377-1 | 377-1 | 377-1
|  | Contingency Scenario | F531 | F487 | F487 | F487 | F487
F377 | 377-3 | Load (A) | 4.6165 | 10.7836 | 24.6972 | 38.7817 | 52.1488
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 0.56437 | 1.3183 | 3.0192 | 4.741 | 6.3752
|  | Hosting Capacity (A) | 813.3835 | 807.2164 | 793.3028 | 779.2183 | 765.8512
|  | Power Factor | 0.76035 | 0.96164 | 0.99386 | 0.99821 | 0.99943
|  | N-1 Load (A) | 8.1237 | 30.8565 | 55.6918 | 80.5168 | 103.9802
|  | N-1 Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Contingency Utilisation (%) | 0.99312 | 3.7722 | 6.8083 | 9.8431 | 12.7115
|  | N-1 Hosting Capacity (A) | 809.8763 | 787.1435 | 762.3082 | 737.4832 | 714.0198
|  | N-1 Power Factor | 0.76035 | 0.96164 | 0.99386 | 0.99821 | 0.99943
|  | N-1 Limiting section | 377-3 | 377-3 | 377-3 | 377-3 | 377-3
|  | Contingency Scenario | F531 | F487 | F487 | F487 | F487
F377 | 377-4 | Load (A) | 4.0906 | 10.5482 | 24.6034 | 38.7313 | 52.1208
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 0.73972 | 1.9118 | 4.4508 | 7.0047 | 9.4256
|  | Hosting Capacity (A) | 548.9094 | 542.4518 | 528.3966 | 514.2687 | 500.8792
|  | Power Factor | 0.85785 | 0.98285 | 0.9974 | 0.99929 | 0.99981
|  | N-1 Load (A) | 7.9602 | 30.7838 | 55.6609 | 80.5058 | 103.9821
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 1.4395 | 5.5667 | 10.0653 | 14.558 | 18.8033
|  | N-1 Hosting Capacity (A) | 545.0398 | 522.2162 | 497.3391 | 472.4942 | 449.0179
|  | N-1 Power Factor | 0.87121 | 0.98285 | 0.99709 | 0.99929 | 0.99981
|  | N-1 Limiting section | 377-4 | 377-4 | 377-4(2) | 377-4 | 377-4
|  | Contingency Scenario | F531 | F487 | F487 | F487 | F487
F378 | 378-1 | Load (A) | 15.791 | 26.0718 | 36.6281 | 47.222 | 57.3051
|  | Rating (A) | 432 | 432 | 432 | 432 | 432
|  | Utilisation (%) | 3.6553 | 6.0351 | 8.4787 | 10.931 | 13.2651
|  | Hosting Capacity (A) | 416.209 | 405.9282 | 395.3719 | 384.778 | 374.6949
|  | Power Factor | 0.98655 | 0.994 | 0.99671 | 0.9981 | 0.99889
|  | N-1 Load (A) | 26.9151 | 45.1615 | 63.8812 | 82.6601 | 100.6031
|  | N-1 Rating (A) | 432 | 432 | 432 | 432 | 432
|  | Contingency Utilisation (%) | 6.2304 | 10.454 | 14.7873 | 19.1343 | 23.2877
|  | N-1 Hosting Capacity (A) | 405.0849 | 386.8385 | 368.1188 | 349.3399 | 331.3969
|  | N-1 Power Factor | 0.98655 | 0.994 | 0.99671 | 0.9981 | 0.99889
|  | N-1 Limiting section | 378-1 | 378-1 | 378-1 | 378-1 | 378-1
|  | Contingency Scenario | F384 | F384 | F384 | F384 | F384
F378 | 378-2 | Load (A) | 4.9892 | 7.6206 | 10.2687 | 12.8678 | 15.256
|  | Rating (A) | 442 | 442 | 442 | 442 | 442
|  | Utilisation (%) | 1.1288 | 1.7241 | 2.3232 | 2.9113 | 3.4516
|  | Hosting Capacity (A) | 437.0108 | 434.3794 | 431.7313 | 429.1322 | 426.744
|  | Power Factor | 0.99996 | 0.99996 | 0.99995 | 0.99994 | 0.99992
F378 | 378-3 | Load (A) | 10.8151 | 18.4655 | 26.3752 | 34.3704 | 42.0648
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 1.3221 | 2.2574 | 3.2244 | 4.2018 | 5.1424
|  | Hosting Capacity (A) | 807.1849 | 799.5345 | 791.6248 | 783.6296 | 775.9352
|  | Power Factor | 0.97877 | 0.99033 | 0.99439 | 0.99647 | 0.99769
|  | N-1 Load (A) | 21.9163 | 37.5464 | 53.6353 | 69.8458 | 85.4325
|  | N-1 Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Contingency Utilisation (%) | 2.6793 | 4.59 | 6.5569 | 8.5386 | 10.4441
|  | N-1 Hosting Capacity (A) | 796.0837 | 780.4536 | 764.3647 | 748.1542 | 732.5675
|  | N-1 Power Factor | 0.97877 | 0.99033 | 0.99439 | 0.99647 | 0.99769
|  | N-1 Limiting section | 378-3 | 378-3 | 378-3 | 378-3 | 378-3
|  | Contingency Scenario | F384 | F384 | F384 | F384 | F384
F378 | 378-5 | Load (A) | 10.5823 | 18.2859 | 26.2261 | 34.2441 | 41.9571
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 1.2937 | 2.2354 | 3.2061 | 4.1863 | 5.1292
|  | Hosting Capacity (A) | 807.4177 | 799.7141 | 791.7739 | 783.7559 | 776.0429
|  | Power Factor | 0.99986 | 0.99949 | 0.9994 | 0.99945 | 0.99954
|  | N-1 Load (A) | 21.8409 | 37.5267 | 53.6482 | 69.867 | 85.4615
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 2.67 | 4.5876 | 6.5585 | 8.5412 | 10.4476
|  | N-1 Hosting Capacity (A) | 778.1591 | 762.4733 | 746.3518 | 730.133 | 714.5385
|  | N-1 Power Factor | 0.99986 | 0.99033 | 0.99439 | 0.99647 | 0.99954
|  | N-1 Limiting section | 378-5 | 378-3 | 378-3 | 378-3 | 378-5
|  | Contingency Scenario | F384 | F384 | F384 | F384 | F384
F379 | 379-1 | Load (A) | 3.3579 | 5.4499 | 7.6265 | 9.8099 | 11.883
|  | Rating (A) | 200 | 200 | 200 | 200 | 200
|  | Utilisation (%) | 1.6789 | 2.725 | 3.8133 | 4.905 | 5.9415
|  | Hosting Capacity (A) | 196.6421 | 194.5501 | 192.3735 | 190.1901 | 188.117
|  | Power Factor | 0.93593 | 0.97685 | 0.98877 | 0.99364 | 0.99599
F380 | 380-1 | Load (A) | 7.4692 | 10.904 | 14.426 | 17.9566 | 21.3186
|  | Rating (A) | 200 | 200 | 200 | 200 | 200
|  | Utilisation (%) | 3.7346 | 5.452 | 7.213 | 8.9783 | 10.6593
|  | Hosting Capacity (A) | 192.5308 | 189.096 | 185.574 | 182.0434 | 178.6814
|  | Power Factor | 0.98273 | 0.9933 | 0.99711 | 0.99874 | 0.9995
|  | N-1 Load (A) | 25.1064 | 37.1883 | 49.3943 | 61.4961 | 72.8549
|  | N-1 Rating (A) | 200 | 200 | 200 | 200 | 200
|  | Contingency Utilisation (%) | 12.5532 | 18.5941 | 24.6972 | 30.748 | 36.4275
|  | N-1 Hosting Capacity (A) | 174.8936 | 162.8117 | 150.6057 | 138.5039 | 127.1451
|  | N-1 Power Factor | 0.98273 | 0.9933 | 0.99711 | 0.99981 | 0.99998
|  | N-1 Limiting section | 380-1(2) | 380-1(2) | 380-1(2) | 380-1 | 380-1
|  | Contingency Scenario | F3828 | F3828 | F3828 | F3828 | F3828
F380 | 380-3 | Load (A) | 6.6395 | 9.73 | 12.8689 | 15.9932 | 18.9486
|  | Rating (A) | 200 | 200 | 200 | 200 | 200
|  | Utilisation (%) | 3.3197 | 4.865 | 6.4344 | 7.9966 | 9.4743
|  | Hosting Capacity (A) | 193.3605 | 190.27 | 187.1311 | 184.0068 | 181.0514
|  | Power Factor | 0.99384 | 0.99632 | 0.99721 | 0.99761 | 0.99774
|  | N-1 Load (A) | 24.2983 | 36.026 | 47.8497 | 59.5526 | 70.5126
|  | N-1 Rating (A) | 200 | 200 | 200 | 200 | 200
|  | Contingency Utilisation (%) | 12.1491 | 18.013 | 23.9249 | 29.7763 | 35.2563
|  | N-1 Hosting Capacity (A) | 175.7017 | 163.974 | 152.1503 | 140.4474 | 129.4874
|  | N-1 Power Factor | 0.99384 | 0.99632 | 0.99721 | 0.99761 | 0.99774
|  | N-1 Limiting section | 380-3(1) | 380-3(1) | 380-3(1) | 380-3(1) | 380-3(1)
|  | Contingency Scenario | F3828 | F3828 | F3828 | F3828 | F3828
F3800 | 3800-1 | Load (A) | 17.8273 | 23.4346 | 25.9413 | 26.0211 | 24.4705
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 3.2237 | 4.2377 | 4.691 | 4.7054 | 4.425
|  | Hosting Capacity (A) | 535.1727 | 529.5654 | 527.0587 | 526.9789 | 528.5295
|  | Power Factor | 0.99966 | 0.9999 | 0.99995 | 0.99995 | 0.99993
|  | N-1 Load (A) | 37.9263 | 49.8527 | 55.1812 | 55.3508 | 52.0548
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 6.8583 | 9.015 | 9.9785 | 10.0092 | 9.4132
|  | N-1 Hosting Capacity (A) | 515.0737 | 503.1473 | 497.8188 | 497.6492 | 500.9452
|  | N-1 Power Factor | 0.99966 | 0.9999 | 0.99995 | 0.99995 | 0.99993
|  | N-1 Limiting section | 3800-1(1) | 3800-1(1) | 3800-1(1) | 3800-1(1) | 3800-1(1)
|  | Contingency Scenario | F3809 | F3809 | F3809 | F3809 | F3809
F3801 | 3801-1 | Load (A) | 53.0118 | 39.7899 | 28.1958 | 19.0638 | 13.5878
|  | Rating (A) | 720 | 720 | 720 | 720 | 720
|  | Utilisation (%) | 7.365 | 5.5264 | 3.9161 | 2.6535 | 1.8872
|  | Hosting Capacity (A) | 666.9882 | 680.2101 | 691.8042 | 700.9362 | 706.4122
|  | Power Factor | 0.96654 | 0.93986 | 0.88309 | 0.74289 | 0.39057
|  | N-1 Load (A) | 93.1281 | 68.6031 | 46.6401 | 37.5835 | 31.617
|  | N-1 Rating (A) | 765 | 765 | 765 | 765 | 765
|  | Contingency Utilisation (%) | 12.9345 | 9.5282 | 6.4778 | 5.2199 | 4.3913
|  | N-1 Hosting Capacity (A) | 671.8719 | 696.3969 | 718.3599 | 727.4165 | 733.383
|  | N-1 Power Factor | 0.96654 | 0.94035 | 0.88399 | 0.74289 | 0.39221
|  | N-1 Limiting section | 3801-1 | 3801-1 | 3801-1 | 3801-1 | 3801-1
|  | Contingency Scenario | F3808 | F3808 | F3808 | F3880 | F3880
F3802 | 3802-1 | Load (A) | 15.3825 | 33.9792 | 67.255 | 95.8751 | 117.8869
|  | Rating (A) | 592 | 592 | 592 | 592 | 592
|  | Utilisation (%) | 2.5984 | 5.7397 | 11.3606 | 16.1951 | 19.9133
|  | Hosting Capacity (A) | 576.6175 | 558.0208 | 524.745 | 496.1249 | 474.1131
|  | Power Factor | 0.37201 | 0.92285 | 0.98693 | 0.99619 | 0.9986
|  | N-1 Load (A) | 34.4547 | 80.0862 | 134.1806 | 187.0307 | 230.5952
|  | N-1 Rating (A) | 675 | 675 | 675 | 675 | 675
|  | Contingency Utilisation (%) | 5.82 | 13.5281 | 22.6656 | 31.593 | 38.9519
|  | N-1 Hosting Capacity (A) | 640.5453 | 594.9138 | 540.8194 | 487.9693 | 444.4048
|  | N-1 Power Factor | 0.37201 | 0.92285 | 0.98693 | 0.99619 | 0.9986
|  | N-1 Limiting section | 3802-1 | 3802-1 | 3802-1 | 3802-1 | 3802-1
|  | Contingency Scenario | F3881 | F3880 | F3880 | F3806 | F3806
F3802 | 3802-1_a | Load (A) | 18.1937 | 35.2396 | 67.8007 | 96.181 | 118.0817
|  | Rating (A) | 592 | 592 | 592 | 592 | 592
|  | Utilisation (%) | 3.0733 | 5.9526 | 11.4528 | 16.2468 | 19.9462
|  | Hosting Capacity (A) | 573.8063 | 556.7604 | 524.1993 | 495.819 | 473.9183
|  | Power Factor | 0.31461 | 0.88994 | 0.97908 | 0.9931 | 0.99701
|  | N-1 Load (A) | 35.5305 | 80.3095 | 133.3215 | 187.0314 | 230.3212
|  | N-1 Rating (A) | 592 | 592 | 592 | 592 | 592
|  | Contingency Utilisation (%) | 6.0018 | 13.5658 | 22.5205 | 31.5931 | 38.9056
|  | N-1 Hosting Capacity (A) | 556.4695 | 511.6905 | 458.6785 | 404.9686 | 361.6788
|  | N-1 Power Factor | 0.31461 | 0.88994 | 0.97908 | 0.99619 | 0.99701
|  | N-1 Limiting section | 3802-1_a | 3802-1_a | 3802-1_a | 3802-1 | 3802-1_a
|  | Contingency Scenario | F3881 | F3880 | F3880 | F3806 | F3806
F3802 | 3802-1_b | Load (A) | 15.6945 | 34.1099 | 67.3099 | 95.8751 | 117.9051
|  | Rating (A) | 592 | 592 | 592 | 592 | 592
|  | Utilisation (%) | 2.6511 | 5.7618 | 11.3699 | 16.2002 | 19.9164
|  | Hosting Capacity (A) | 576.3055 | 557.8901 | 524.6901 | 496.1249 | 474.0949
|  | Power Factor | 0.36462 | 0.91933 | 0.98614 | 0.99619 | 0.99845
|  | N-1 Load (A) | 34.5642 | 80.0734 | 133.3316 | 186.9541 | 230.3124
|  | N-1 Rating (A) | 592 | 592 | 592 | 592 | 592
|  | Contingency Utilisation (%) | 5.8385 | 13.5259 | 22.5222 | 31.5801 | 38.9041
|  | N-1 Hosting Capacity (A) | 557.4358 | 511.9266 | 458.6684 | 405.0459 | 361.6876
|  | N-1 Power Factor | 0.36462 | 0.92285 | 0.97908 | 0.99589 | 0.99845
|  | N-1 Limiting section | 3802-1_b | 3802-1 | 3802-1_a | 3802-1_b | 3802-1_b
|  | Contingency Scenario | F3881 | F3880 | F3880 | F3806 | F3806
F3803 | 3803-1 | Load (A) | 45.0055 | 23.8368 | 5.2286 | 12.2725 | 23.8272
|  | Rating (A) | 502 | 502 | 502 | 502 | 502
|  | Utilisation (%) | 8.9652 | 4.7484 | 1.0416 | 2.4447 | 4.7465
|  | Hosting Capacity (A) | 456.9945 | 478.1632 | 496.7714 | 489.7275 | 478.1728
|  | Power Factor | 0.98928 | 0.97379 | 0.69846 | 0.98482 | 0.99924
|  | N-1 Load (A) | 68.3219 | 60.7468 | 55.4725 | 78.0077 | 97.9864
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 13.6099 | 12.1009 | 11.0503 | 15.5394 | 19.5192
|  | N-1 Hosting Capacity (A) | 484.6781 | 492.2532 | 497.5275 | 474.9923 | 455.0136
|  | N-1 Power Factor | 0.98928 | 0.97379 | 0.69846 | 0.98482 | 0.99924
|  | N-1 Limiting section | 3803-1 | 3803-1 | 3803-1 | 3803-1 | 3803-1
|  | Contingency Scenario | F3805 | F3880 | F3880 | F3881 | F3881
F3805 | 3805-1 | Load (A) | 41.1485 | 21.7888 | 4.7555 | 11.2148 | 21.7852
|  | Rating (A) | 502 | 502 | 502 | 502 | 502
|  | Utilisation (%) | 8.1969 | 4.3404 | 0.9473 | 2.234 | 4.3397
|  | Hosting Capacity (A) | 460.8515 | 480.2112 | 497.2445 | 490.7852 | 480.2148
|  | Power Factor | 0.99127 | 0.9771 | 0.71188 | 0.983 | 0.99872
|  | N-1 Load (A) | 65.6483 | 55.5484 | 50.7255 | 71.3365 | 89.6057
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 13.0774 | 11.0654 | 10.1047 | 14.2105 | 17.8497
|  | N-1 Hosting Capacity (A) | 487.3517 | 497.4516 | 502.2745 | 481.6635 | 463.3943
|  | N-1 Power Factor | 0.99127 | 0.9771 | 0.71188 | 0.983 | 0.99872
|  | N-1 Limiting section | 3805-1(3) | 3805-1(3) | 3805-1(3) | 3805-1(3) | 3805-1(3)
|  | Contingency Scenario | F3803 | F3880 | F3880 | F3881 | F3881
F3806 | 3806-1 | Load (A) | 18.18 | 35.1266 | 67.5406 | 95.801 | 117.6108
|  | Rating (A) | 592 | 592 | 592 | 592 | 592
|  | Utilisation (%) | 3.0709 | 5.9336 | 11.4089 | 16.1826 | 19.8667
|  | Hosting Capacity (A) | 573.82 | 556.8734 | 524.4594 | 496.199 | 474.3892
|  | Power Factor | 0.31368 | 0.88915 | 0.97887 | 0.99301 | 0.99696
|  | N-1 Load (A) | 35.4119 | 79.9927 | 132.7824 | 187.0042 | 230.2852
|  | N-1 Rating (A) | 675 | 675 | 675 | 675 | 675
|  | Contingency Utilisation (%) | 5.9817 | 13.5123 | 22.4295 | 31.5885 | 38.8995
|  | N-1 Hosting Capacity (A) | 639.5881 | 595.0073 | 542.2176 | 487.9958 | 444.7148
|  | N-1 Power Factor | 0.31368 | 0.88915 | 0.97887 | 0.99301 | 0.99696
|  | N-1 Limiting section | 3806-1 | 3806-1 | 3806-1 | 3806-1 | 3806-1
|  | Contingency Scenario | F3881 | F3880 | F3880 | F3802 | F3802
F3806 | 3806-1_a | Load (A) | 15.6799 | 33.9929 | 67.0472 | 95.523 | 117.4326
|  | Rating (A) | 592 | 592 | 592 | 592 | 592
|  | Utilisation (%) | 2.6486 | 5.7421 | 11.3255 | 16.1356 | 19.8366
|  | Hosting Capacity (A) | 576.3201 | 558.0071 | 524.9528 | 496.477 | 474.5674
|  | Power Factor | 0.36361 | 0.91872 | 0.98599 | 0.99583 | 0.99842
|  | N-1 Load (A) | 34.4421 | 79.7544 | 132.7926 | 186.9262 | 230.2758
|  | N-1 Rating (A) | 592 | 592 | 592 | 592 | 592
|  | Contingency Utilisation (%) | 5.8179 | 13.472 | 22.4312 | 31.5754 | 38.8979
|  | N-1 Hosting Capacity (A) | 557.5579 | 512.2456 | 459.2074 | 405.0738 | 361.7242
|  | N-1 Power Factor | 0.36361 | 0.91872 | 0.97887 | 0.99583 | 0.99696
|  | N-1 Limiting section | 3806-1_a | 3806-1_a | 3806-1 | 3806-1_a | 3806-1
|  | Contingency Scenario | F3881 | F3880 | F3880 | F3802 | F3802
F3806 | 3806-1_b | Load (A) | 15.3603 | 33.8587 | 66.9907 | 95.4923 | 117.4138
|  | Rating (A) | 592 | 592 | 592 | 592 | 592
|  | Utilisation (%) | 2.5947 | 5.7194 | 11.316 | 16.1304 | 19.8334
|  | Hosting Capacity (A) | 576.6397 | 558.1413 | 525.0093 | 496.5077 | 474.5862
|  | Power Factor | 0.37116 | 0.92235 | 0.98681 | 0.99614 | 0.99857
|  | N-1 Load (A) | 34.3296 | 79.7663 | 133.6449 | 187.0016 | 230.5589
|  | N-1 Rating (A) | 592 | 592 | 592 | 592 | 592
|  | Contingency Utilisation (%) | 5.7989 | 13.474 | 22.5751 | 31.5881 | 38.9458
|  | N-1 Hosting Capacity (A) | 557.6704 | 512.2337 | 458.3551 | 404.9984 | 361.4411
|  | N-1 Power Factor | 0.37116 | 0.91872 | 0.98681 | 0.99301 | 0.99857
|  | N-1 Limiting section | 3806-1_b | 3806-1_a | 3806-1_b | 3806-1 | 3806-1_b
|  | Contingency Scenario | F3881 | F3880 | F3880 | F3802 | F3802
F3807 | 3807-1 | Load (A) | 57.1994 | 48.6161 | 40.3232 | 33.0643 | 26.9807
|  | Rating (A) | 748 | 748 | 748 | 748 | 748
|  | Utilisation (%) | 7.647 | 6.4995 | 5.3908 | 4.4204 | 3.607
|  | Hosting Capacity (A) | 690.8006 | 699.3839 | 707.6768 | 714.9357 | 721.0193
|  | Power Factor | 0.99955 | 0.99952 | 0.99945 | 0.99932 | 0.99911
F3808 | 3808-1 | Load (A) | 53.1242 | 39.8618 | 28.2458 | 19.1377 | 13.6093
|  | Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Utilisation (%) | 7.5892 | 5.6945 | 4.0351 | 2.734 | 1.9442
|  | Hosting Capacity (A) | 646.8758 | 660.1382 | 671.7542 | 680.8623 | 686.3907
|  | Power Factor | 0.96607 | 0.93962 | 0.88277 | 0.74085 | 0.38993
|  | N-1 Load (A) | 93.1618 | 68.6275 | 46.656 | 37.6514 | 31.6737
|  | N-1 Rating (A) | 748 | 748 | 748 | 748 | 748
|  | Contingency Utilisation (%) | 13.3088 | 9.8039 | 6.6651 | 5.3788 | 4.5248
|  | N-1 Hosting Capacity (A) | 654.8382 | 679.3725 | 701.344 | 710.3486 | 716.3263
|  | N-1 Power Factor | 0.96607 | 0.93962 | 0.88277 | 0.74085 | 0.38993
|  | N-1 Limiting section | 3808-1 | 3808-1 | 3808-1 | 3808-1 | 3808-1
|  | Contingency Scenario | F3801 | F3801 | F3801 | F3880 | F3880
F3809 | 3809-1 | Load (A) | 20.1488 | 26.4892 | 29.3236 | 29.4138 | 27.6604
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 3.644 | 4.7902 | 5.3027 | 5.319 | 5.002
|  | Hosting Capacity (A) | 532.8512 | 526.5108 | 523.6764 | 523.5862 | 525.3396
|  | Power Factor | 0.99991 | 0.99999 | 1 | 1 | 1
|  | N-1 Load (A) | 37.9343 | 49.8655 | 55.1966 | 55.3662 | 52.0686
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 6.8597 | 9.0173 | 9.9813 | 10.012 | 9.4157
|  | N-1 Hosting Capacity (A) | 515.0657 | 503.1345 | 497.8034 | 497.6338 | 500.9314
|  | N-1 Power Factor | 0.99991 | 0.99999 | 1 | 1 | 1
|  | N-1 Limiting section | 3809-1 | 3809-1 | 3809-1 | 3809-1 | 3809-1
|  | Contingency Scenario | F3800 | F3800 | F3800 | F3800 | F3800
F381 | 381-1 | Load (A) | 20.9627 | 11.9386 | 3.554 | 7.4923 | 16.014
|  | Rating (A) | 432 | 432 | 432 | 432 | 432
|  | Utilisation (%) | 4.8525 | 2.7636 | 0.82269 | 1.7343 | 3.7069
|  | Hosting Capacity (A) | 411.0373 | 420.0614 | 428.446 | 424.5077 | 415.986
|  | Power Factor | 0.99235 | 0.9734 | 0.64079 | 0.93946 | 0.99009
|  | N-1 Load (A) | 21.7868 | 12.2772 | 14.5734 | 31.7299 | 48.1981
|  | N-1 Rating (A) | 432 | 432 | 432 | 432 | 432
|  | Contingency Utilisation (%) | 5.0432 | 2.8419 | 3.3735 | 7.3449 | 11.157
|  | N-1 Hosting Capacity (A) | 410.2132 | 419.7228 | 417.4266 | 400.2701 | 383.8019
|  | N-1 Power Factor | 0.99235 | 0.9734 | 0.64079 | 0.93946 | 0.99009
|  | N-1 Limiting section | 381-1 | 381-1 | 381-1 | 381-1 | 381-1
|  | Contingency Scenario | F382 | F380 | F382 | F382 | F382
F381 | 381-3 | Load (A) | 20.9627 | 11.9386 | 3.5129 | 7.4923 | 16.014
|  | Rating (A) | 432 | 432 | 432 | 432 | 432
|  | Utilisation (%) | 4.851 | 2.7607 | 0.81318 | 1.7301 | 3.7052
|  | Hosting Capacity (A) | 411.0373 | 420.0614 | 428.4871 | 424.5077 | 415.986
|  | Power Factor | 0.99235 | 0.9734 | 0.64824 | 0.93946 | 0.99009
|  | N-1 Load (A) | 21.7752 | 12.2699 | 14.5592 | 31.7254 | 48.1969
|  | N-1 Rating (A) | 432 | 432 | 432 | 432 | 432
|  | Contingency Utilisation (%) | 5.0406 | 2.8403 | 3.3702 | 7.3438 | 11.1567
|  | N-1 Hosting Capacity (A) | 410.2248 | 419.7301 | 417.4408 | 400.2746 | 383.8031
|  | N-1 Power Factor | 0.99235 | 0.9734 | 0.64079 | 0.93946 | 0.99009
|  | N-1 Limiting section | 381-1 | 381-1 | 381-1 | 381-1 | 381-1
|  | Contingency Scenario | F382 | F380 | F382 | F382 | F382
F381 | 381-5 | Load (A) | 20.9073 | 11.8357 | 3.1941 | 7.339 | 15.9521
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 3.7805 | 2.14 | 0.57659 | 1.3267 | 2.8845
|  | Hosting Capacity (A) | 532.0927 | 541.1643 | 549.8059 | 545.661 | 537.0479
|  | Power Factor | 0.99461 | 0.98144 | 0.71253 | 0.95884 | 0.99366
|  | N-1 Load (A) | 21.6837 | 12.2185 | 14.4492 | 31.6909 | 48.1876
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 3.9211 | 2.2095 | 2.6129 | 5.7307 | 8.7139
|  | N-1 Hosting Capacity (A) | 531.3163 | 540.7815 | 538.5508 | 521.3091 | 504.8124
|  | N-1 Power Factor | 0.99461 | 0.98144 | 0.71253 | 0.95884 | 0.99366
|  | N-1 Limiting section | 381-3(6) | 381-3(6) | 381-3(6) | 381-3(6) | 381-3(6)
|  | Contingency Scenario | F382 | F380 | F382 | F382 | F382
F381 | 381-6 | Load (A) | 23.2226 | 20.7155 | 18.1728 | 15.6399 | 13.2437
|  | Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Utilisation (%) | 5.7624 | 5.1403 | 4.5094 | 3.8809 | 3.2863
|  | Hosting Capacity (A) | 379.7774 | 382.2845 | 384.8272 | 387.3601 | 389.7563
|  | Power Factor | 0.99965 | 0.99967 | 0.99969 | 0.99969 | 0.99968
|  | N-1 Load (A) | 23.2331 | 20.7261 | 18.1832 | 15.6519 | 13.2567
|  | N-1 Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Contingency Utilisation (%) | 5.765 | 5.1429 | 4.512 | 3.8839 | 3.2895
|  | N-1 Hosting Capacity (A) | 379.7669 | 382.2739 | 384.8168 | 387.3481 | 389.7433
|  | N-1 Power Factor | 0.99965 | 0.99967 | 0.99969 | 0.99969 | 0.99968
|  | N-1 Limiting section | 381-6 | 381-6 | 381-6 | 381-6 | 381-6
|  | Contingency Scenario | F380 | F380 | F380 | F3828 | F3828
F381 | 381-7 | Load (A) | 3.2619 | 9.3442 | 16.0173 | 22.7393 | 29.123
|  | Rating (A) | 582 | 582 | 582 | 582 | 582
|  | Utilisation (%) | 0.56046 | 1.6055 | 2.7521 | 3.9071 | 5.004
|  | Hosting Capacity (A) | 578.7381 | 572.6558 | 565.9827 | 559.2607 | 552.877
|  | Power Factor | 0.74462 | 0.97365 | 0.99222 | 0.99694 | 0.99872
|  | N-1 Load (A) | 4.7559 | 17.3794 | 32.2844 | 47.1874 | 61.3216
|  | N-1 Rating (A) | 582 | 582 | 582 | 582 | 582
|  | Contingency Utilisation (%) | 0.81717 | 2.9862 | 5.5472 | 8.1078 | 10.5364
|  | N-1 Hosting Capacity (A) | 577.2441 | 564.6206 | 549.7156 | 534.8126 | 520.6784
|  | N-1 Power Factor | 0.74462 | 0.97365 | 0.99222 | 0.99694 | 0.99872
|  | N-1 Limiting section | 381-7 | 381-7 | 381-7 | 381-7 | 381-7
|  | Contingency Scenario | F382 | F382 | F382 | F382 | F382
F381 | 381-8 | Load (A) | 23.2422 | 20.7352 | 18.1728 | 15.6615 | 13.2437
|  | Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Utilisation (%) | 5.7673 | 5.1452 | 4.5145 | 3.8862 | 3.2919
|  | Hosting Capacity (A) | 379.7578 | 382.2648 | 384.8272 | 387.3385 | 389.7563
|  | Power Factor | 0.99939 | 0.99937 | 0.99969 | 0.99925 | 0.99968
|  | N-1 Load (A) | 23.2527 | 20.7458 | 18.2039 | 15.6734 | 13.2792
|  | N-1 Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Contingency Utilisation (%) | 5.7699 | 5.1479 | 4.5171 | 3.8892 | 3.2951
|  | N-1 Hosting Capacity (A) | 379.7473 | 382.2542 | 384.7961 | 387.3266 | 389.7208
|  | N-1 Power Factor | 0.99965 | 0.99937 | 0.99933 | 0.99925 | 0.99911
|  | N-1 Limiting section | 381-6 | 381-8 | 381-8 | 381-8 | 381-8
|  | Contingency Scenario | F380 | F380 | F380 | F3828 | F3828
F381 | 381-9 | Load (A) | 25.8267 | 29.9543 | 34.1749 | 38.3914 | 42.3873
|  | Rating (A) | 200 | 200 | 200 | 200 | 200
|  | Utilisation (%) | 12.9133 | 14.9772 | 17.0875 | 19.1957 | 21.1936
|  | Hosting Capacity (A) | 174.1733 | 170.0457 | 165.8251 | 161.6086 | 157.6127
|  | Power Factor | 0.9934 | 0.9955 | 0.99702 | 0.9981 | 0.99887
|  | N-1 Load (A) | 0.1326 | 37.8898 | 50.375 | 62.7547 | 74.4869
|  | N-1 Rating (A) | 200 | 200 | 200 | 200 | 200
|  | Contingency Utilisation (%) | 0.017379 | 18.9449 | 25.1875 | 31.3773 | 37.2435
|  | N-1 Hosting Capacity (A) | 199.8674 | 162.1102 | 149.625 | 137.2453 | 125.5131
|  | N-1 Power Factor | 1 | 0.9955 | 0.99702 | 0.9981 | 0.99887
|  | N-1 Limiting section | 381-9(2) | 381-9 | 381-9 | 381-9 | 381-9
|  | Contingency Scenario | F382 | F382 | F382 | F382 | F382
F3818 | 3818-1 | Load (A) | 30.1937 | 27.8714 | 25.5869 | 23.5856 | 22.1404
|  | Rating (A) | 750 | 750 | 750 | 750 | 750
|  | Utilisation (%) | 4.0258 | 3.7162 | 3.4116 | 3.1447 | 2.9521
|  | Hosting Capacity (A) | 719.8063 | 722.1286 | 724.4131 | 726.4144 | 727.8596
|  | Power Factor | 0.95197 | 0.94245 | 0.93027 | 0.91637 | 0.90371
|  | N-1 Load (A) | 58.4698 | 53.5695 | 48.71 | 44.4107 | 41.2738
|  | N-1 Rating (A) | 750 | 750 | 750 | 750 | 750
|  | Contingency Utilisation (%) | 7.796 | 7.1426 | 6.4947 | 5.9214 | 5.5032
|  | N-1 Hosting Capacity (A) | 691.5302 | 696.4305 | 701.29 | 705.5893 | 708.7262
|  | N-1 Power Factor | 0.95197 | 0.94245 | 0.93027 | 0.91637 | 0.90371
|  | N-1 Limiting section | 3818-1 | 3818-1 | 3818-1 | 3818-1 | 3818-1
|  | Contingency Scenario | F679 | F679 | F679 | F679 | F679
F382 | 382-1 | Load (A) | 3.9429 | 8.7302 | 16.8127 | 25.1819 | 33.1778
|  | Rating (A) | 432 | 432 | 432 | 432 | 432
|  | Utilisation (%) | 0.9127 | 2.0209 | 3.8918 | 5.8292 | 7.68
|  | Hosting Capacity (A) | 428.0571 | 423.2698 | 415.1873 | 406.8181 | 398.8222
|  | Power Factor | 1 | 0.91113 | 0.98273 | 0.99518 | 0.99871
|  | N-1 Load (A) | 25.6282 | 37.72 | 50.1329 | 62.5462 | 74.3475
|  | N-1 Rating (A) | 432 | 432 | 432 | 432 | 432
|  | Contingency Utilisation (%) | 5.9324 | 8.7315 | 11.6048 | 14.4783 | 17.2101
|  | N-1 Hosting Capacity (A) | 406.3718 | 394.28 | 381.8671 | 369.4538 | 357.6525
|  | N-1 Power Factor | 1 | 0.91113 | 0.98273 | 0.99518 | 0.99871
|  | N-1 Limiting section | 382-1 | 382-1 | 382-1 | 382-1 | 382-1
|  | Contingency Scenario | F381 | F381 | F381 | F381 | F381
F382 | 382-3 | Load (A) | 3.9007 | 8.7302 | 16.8127 | 25.1819 | 33.1778
|  | Rating (A) | 432 | 432 | 432 | 432 | 432
|  | Utilisation (%) | 0.90293 | 2.0168 | 3.89 | 5.8282 | 7.6796
|  | Hosting Capacity (A) | 428.0993 | 423.2698 | 415.1873 | 406.8181 | 398.8222
|  | Power Factor | 1 | 0.91113 | 0.98273 | 0.99518 | 0.99871
|  | N-1 Load (A) | 25.6186 | 37.7143 | 50.1295 | 62.5444 | 74.3469
|  | N-1 Rating (A) | 432 | 432 | 432 | 432 | 432
|  | Contingency Utilisation (%) | 5.9302 | 8.7302 | 11.6041 | 14.4779 | 17.2099
|  | N-1 Hosting Capacity (A) | 406.3814 | 394.2857 | 381.8705 | 369.4556 | 357.6531
|  | N-1 Power Factor | 1 | 0.91113 | 0.98273 | 0.99518 | 0.99871
|  | N-1 Limiting section | 382-1 | 382-1 | 382-1 | 382-1 | 382-1
|  | Contingency Scenario | F381 | F381 | F381 | F381 | F381
F3828 | 3828-1 | Load (A) | 18.1241 | 27.0579 | 36.2063 | 45.3469 | 54.0014
|  | Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Utilisation (%) | 2.5892 | 3.8654 | 5.1723 | 6.4781 | 7.7145
|  | Hosting Capacity (A) | 681.8759 | 672.9421 | 663.7937 | 654.6531 | 645.9986
|  | Power Factor | 0.992 | 0.99712 | 0.9989 | 0.99962 | 0.99992
|  | N-1 Load (A) | 25.3821 | 37.7765 | 50.4507 | 63.0689 | 75.0367
|  | N-1 Rating (A) | 155 | 400 | 400 | 400 | 400
|  | Contingency Utilisation (%) | 3.626 | 5.3966 | 7.2072 | 9.0098 | 10.7195
|  | N-1 Hosting Capacity (A) | 129.6179 | 362.2235 | 349.5493 | 336.9311 | 324.9633
|  | N-1 Power Factor | 0.992 | 0.99712 | 0.9989 | 0.99962 | 0.99992
|  | N-1 Limiting section | 3828-1(4) | 3828-1(4) | 3828-1(4) | 3828-1(4) | 3828-1(4)
|  | Contingency Scenario | F3829 | F3829 | F3829 | F3829 | F3829
F3829 | 3829-1 | Load (A) | 7.3593 | 10.8496 | 14.4383 | 18.035 | 21.4509
|  | Rating (A) | 155 | 155 | 155 | 155 | 155
|  | Utilisation (%) | 4.7479 | 7.0032 | 9.3173 | 11.6355 | 13.8402
|  | Hosting Capacity (A) | 147.6407 | 144.1504 | 140.5617 | 136.965 | 133.5491
|  | Power Factor | 0.97863 | 0.99227 | 0.99667 | 0.99842 | 0.9994
|  | N-1 Load (A) | 24.9805 | 37.1279 | 49.4003 | 61.5578 | 72.9651
|  | N-1 Rating (A) | 155 | 155 | 155 | 155 | 155
|  | Contingency Utilisation (%) | 16.1164 | 23.9535 | 31.8711 | 39.7147 | 47.0742
|  | N-1 Hosting Capacity (A) | 130.0195 | 117.8721 | 105.5997 | 93.4422 | 82.0349
|  | N-1 Power Factor | 0.97863 | 0.99227 | 0.99667 | 0.99853 | 0.9994
|  | N-1 Limiting section | 3829-1(3) | 3829-1 | 3829-1 | 3829-1 | 3829-1
|  | Contingency Scenario | F3828 | F3828 | F3828 | F3828 | F3828
F3831 | 3831-1 | Load (A) | 31.7661 | 43.0337 | 54.6684 | 66.4195 | 77.6846
|  | Rating (A) | 355 | 355 | 355 | 355 | 355
|  | Utilisation (%) | 8.9482 | 12.1222 | 15.3995 | 18.7097 | 21.883
|  | Hosting Capacity (A) | 323.2339 | 311.9663 | 300.3316 | 288.5805 | 277.3154
|  | Power Factor | 0.99937 | 0.99944 | 0.99942 | 0.9992 | 0.99894
F384 | 384 | Load (A) | 4.994 | 7.6277 | 10.2792 | 12.8829 | 15.2763
|  | Rating (A) | 442 | 442 | 442 | 442 | 442
|  | Utilisation (%) | 1.1299 | 1.7257 | 2.3256 | 2.9147 | 3.4562
|  | Hosting Capacity (A) | 437.006 | 434.3723 | 431.7208 | 429.1171 | 426.7237
|  | Power Factor | 0.99995 | 0.99995 | 0.99994 | 0.99993 | 0.99991
F384 | 384-1 | Load (A) | 16.3317 | 27.004 | 37.9683 | 48.9654 | 59.4268
|  | Rating (A) | 451 | 451 | 451 | 451 | 451
|  | Utilisation (%) | 3.6212 | 5.9876 | 8.4187 | 10.8571 | 13.1767
|  | Hosting Capacity (A) | 434.6683 | 423.996 | 413.0317 | 402.0346 | 391.5732
|  | Power Factor | 0.99829 | 0.99997 | 0.9995 | 0.99883 | 0.99808
|  | N-1 Load (A) | 26.8334 | 45.0807 | 63.7516 | 82.4365 | 100.3041
|  | N-1 Rating (A) | 451 | 451 | 451 | 451 | 451
|  | Contingency Utilisation (%) | 5.9498 | 9.9957 | 14.1356 | 18.2786 | 22.2404
|  | N-1 Hosting Capacity (A) | 424.1666 | 405.9193 | 387.2484 | 368.5635 | 350.6959
|  | N-1 Power Factor | 0.99829 | 0.99997 | 0.9995 | 0.99883 | 0.99808
|  | N-1 Limiting section | 384-1 | 384-1 | 384-1 | 384-1 | 384-1
|  | Contingency Scenario | F378 | F378 | F378 | F378 | F378
F384 | 384-2 | Load (A) | 4.9966 | 7.6287 | 10.2793 | 12.8822 | 15.2753
|  | Rating (A) | 293 | 293 | 293 | 293 | 293
|  | Utilisation (%) | 1.7053 | 2.6037 | 3.5083 | 4.3966 | 5.2134
|  | Hosting Capacity (A) | 288.0034 | 285.3713 | 282.7207 | 280.1178 | 277.7247
|  | Power Factor | 0.99942 | 0.99982 | 0.99994 | 0.99999 | 0.99998
F384 | 384-3 | Load (A) | 11.3142 | 19.4113 | 27.7532 | 36.1728 | 44.2662
|  | Rating (A) | 495 | 495 | 495 | 495 | 495
|  | Utilisation (%) | 2.2857 | 3.9215 | 5.6067 | 7.3076 | 8.9427
|  | Hosting Capacity (A) | 483.6858 | 475.5887 | 467.2468 | 458.8272 | 450.7338
|  | Power Factor | 0.9995 | 0.99839 | 0.9975 | 0.99674 | 0.99604
|  | N-1 Load (A) | 21.8275 | 37.4723 | 53.5154 | 69.6231 | 85.1261
|  | N-1 Rating (A) | 495 | 495 | 495 | 495 | 495
|  | Contingency Utilisation (%) | 4.4096 | 7.5702 | 10.8112 | 14.0653 | 17.1972
|  | N-1 Hosting Capacity (A) | 473.1725 | 457.5277 | 441.4846 | 425.3769 | 409.8739
|  | N-1 Power Factor | 0.9995 | 0.99839 | 0.9975 | 0.99674 | 0.99604
|  | N-1 Limiting section | 384-3(10) | 384-3(10) | 384-3(10) | 384-3(10) | 384-3(10)
|  | Contingency Scenario | F378 | F378 | F378 | F378 | F378
F3840 | 3840-1 | Load (A) | 4.5937 | 6.6817 | 8.8006 | 10.9132 | 12.9288
|  | Rating (A) | 155 | 155 | 155 | 155 | 155
|  | Utilisation (%) | 2.9637 | 4.3108 | 5.6778 | 7.042 | 8.3412
|  | Hosting Capacity (A) | 150.4063 | 148.3183 | 146.1994 | 144.0868 | 142.0712
|  | Power Factor | 0.98951 | 0.99539 | 0.99767 | 0.99891 | 0.99905
|  | N-1 Load (A) | 13.2982 | 19.8912 | 26.5673 | 33.1609 | 39.314
|  | N-1 Rating (A) | 155 | 155 | 155 | 155 | 155
|  | Contingency Utilisation (%) | 8.5795 | 12.833 | 17.1402 | 21.3942 | 25.3639
|  | N-1 Hosting Capacity (A) | 141.7018 | 135.1088 | 128.4327 | 121.8391 | 115.686
|  | N-1 Power Factor | 0.9952 | 0.99781 | 0.99856 | 0.99891 | 0.99905
|  | N-1 Limiting section | 3840-1(2) | 3840-1(2) | 3840-1(2) | 3840-1(2) | 3840-1(2)
|  | Contingency Scenario | F3828 | F3828 | F3828 | F3828 | F3828
F3859 | 3859-1 | Load (A) | 2.8609 | 2.6647 | 3.6071 | 5.1313 | 6.7858
|  | Rating (A) | 764 | 764 | 764 | 764 | 764
|  | Utilisation (%) | 0.37447 | 0.34878 | 0.47214 | 0.67163 | 0.8882
|  | Hosting Capacity (A) | 761.1391 | 761.3353 | 760.3929 | 758.8687 | 757.2142
|  | Power Factor | 0.42405 | 0.2317 | 0.69735 | 0.86554 | 0.92688
|  | N-1 Load (A) | 3.4957 | 2.8063 | 5.6179 | 9.2146 | 12.8008
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 0.45755 | 0.36731 | 0.73532 | 1.2061 | 1.6755
|  | N-1 Hosting Capacity (A) | 796.5043 | 797.1937 | 794.3821 | 790.7854 | 787.1992
|  | N-1 Power Factor | 0.42405 | 0.2317 | 0.69735 | 0.86554 | 0.92688
|  | N-1 Limiting section | 3859-1(3) | 3859-1(3) | 3859-1(3) | 3859-1(3) | 3859-1(3)
|  | Contingency Scenario | F3860 | F3860 | F3860 | F3860 | F3860
F3860 | 3860-1 | Load (A) | 2.8431 | 2.646 | 3.5925 | 5.1196 | 6.7753
|  | Rating (A) | 764 | 764 | 764 | 764 | 764
|  | Utilisation (%) | 0.37214 | 0.34634 | 0.47023 | 0.6701 | 0.88682
|  | Hosting Capacity (A) | 761.1569 | 761.354 | 760.4075 | 758.8804 | 757.2247
|  | Power Factor | 0.42635 | 0.23328 | 0.69982 | 0.86703 | 0.92778
|  | N-1 Load (A) | 3.4987 | 2.81 | 5.6197 | 9.2157 | 12.8015
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 0.45794 | 0.3678 | 0.73556 | 1.2062 | 1.6756
|  | N-1 Hosting Capacity (A) | 796.5013 | 797.19 | 794.3803 | 790.7843 | 787.1985
|  | N-1 Power Factor | 0.42635 | 0.23328 | 0.69982 | 0.86703 | 0.92778
|  | N-1 Limiting section | 3860-1(3) | 3860-1(3) | 3860-1(3) | 3860-1(3) | 3860-1(3)
|  | Contingency Scenario | F3859 | F3859 | F3859 | F3859 | F3859
F387 | 387-1 | Load (A) | 12.3371 | 14.8087 | 21.1626 | 19.5795 | 14.4473
|  | Rating (A) | 290 | 290 | 290 | 290 | 290
|  | Utilisation (%) | 4.2542 | 5.1065 | 7.2974 | 6.7515 | 4.9818
|  | Hosting Capacity (A) | 277.6629 | 275.1913 | 268.8374 | 270.4205 | 275.5527
|  | Power Factor | 0.82395 | 0.84925 | 0.90091 | 0.88474 | 0.81255
|  | N-1 Load (A) | 32.7974 | 41.0701 | 49.7043 | 58.359 | 66.3934
|  | N-1 Rating (A) | 290 | 290 | 290 | 290 | 290
|  | Contingency Utilisation (%) | 11.3094 | 14.1621 | 17.1394 | 20.1238 | 22.8943
|  | N-1 Hosting Capacity (A) | 257.2026 | 248.9299 | 240.2957 | 231.641 | 223.6066
|  | N-1 Power Factor | 0.8453 | 0.86577 | 0.90997 | 0.89538 | 0.83057
|  | N-1 Limiting section | 387-1(10) | 387-1(10) | 387-1(10) | 387-1(10) | 387-1(10)
|  | Contingency Scenario | F436 | F436 | F436 | F436 | F436
F3870 | 3870-1 | Load (A) | 25.0642 | 12.8062 | 2.8563 | 13.4769 | 25.6338
|  | Rating (A) | 703 | 703 | 703 | 703 | 703
|  | Utilisation (%) | 3.5653 | 1.8217 | 0.4063 | 1.9171 | 3.6463
|  | Hosting Capacity (A) | 677.9358 | 690.1938 | 700.1437 | 689.5231 | 677.3662
|  | Power Factor | 0.99554 | 0.97731 | 1 | 0.97896 | 0.9954
|  | N-1 Load (A) |  |  | 4.4742
|  | N-1 Rating (A) | 703 | 703 | 703 | 703 | 703
F3871 | 3871-1 | Load (A) | 22.1243 | 12.8952 | 3.4875 | 5.9834 | 14.8957
|  | Rating (A) | 432 | 432 | 432 | 432 | 432
|  | Utilisation (%) | 5.1214 | 2.985 | 0.8073 | 1.3851 | 3.4481
|  | Hosting Capacity (A) | 409.8757 | 419.1048 | 428.5125 | 426.0166 | 417.1043
|  | Power Factor | 0.99959 | 0.99923 | 0.99149 | 0.99698 | 0.99936
|  | N-1 Load (A) | 22.1314 | 12.9038 | 3.5133 | 5.9992 | 14.9039
|  | N-1 Rating (A) | 432 | 432 | 432 | 432 | 432
|  | Contingency Utilisation (%) | 5.123 | 2.987 | 0.81326 | 1.3887 | 3.45
|  | N-1 Hosting Capacity (A) | 409.8686 | 419.0962 | 428.4867 | 426.0008 | 417.0961
|  | N-1 Power Factor | 0.99959 | 0.99923 | 0.99149 | 0.99698 | 0.99936
|  | N-1 Limiting section | 3871-1(1) | 3871-1(1) | 3871-1(1) | 3871-1(1) | 3871-1(1)
|  | Contingency Scenario | F383 | F383 | F383 | F383 | F383
F3880 | 3880-1 | Load (A) | 60.3914 | 98.8658 | 135.0467 | 162.8553 | 181.3766
|  | Rating (A) | 742 | 742 | 742 | 742 | 742
|  | Utilisation (%) | 8.139 | 13.3242 | 18.2004 | 21.9481 | 24.4443
|  | Hosting Capacity (A) | 681.6086 | 643.1342 | 606.9533 | 579.1447 | 560.6234
|  | Power Factor | 0.93602 | 0.98422 | 0.99572 | 0.99652 | 0.9957
|  | N-1 Load (A) | 111.1721 | 195.9156 | 275.0042 | 335.0164 | 375.0165
|  | N-1 Rating (A) | 742 | 742 | 742 | 742 | 742
|  | Contingency Utilisation (%) | 14.9828 | 26.4037 | 37.0626 | 45.1505 | 50.5413
|  | N-1 Hosting Capacity (A) | 630.8279 | 546.0844 | 466.9958 | 406.9836 | 366.9835
|  | N-1 Power Factor | 0.93602 | 0.98422 | 0.99572 | 0.99652 | 0.9957
|  | N-1 Limiting section | 3880-1 | 3880-1 | 3880-1 | 3880-1 | 3880-1
|  | Contingency Scenario | F3881 | F3881 | F3881 | F3881 | F3881
F3881 | 3881-1 | Load (A) | 54.0136 | 98.4005 | 139.2643 | 169.8881 | 190.0634
|  | Rating (A) | 742 | 742 | 742 | 742 | 742
|  | Utilisation (%) | 7.2795 | 13.2615 | 18.7688 | 22.896 | 25.615
|  | Hosting Capacity (A) | 687.9864 | 643.5995 | 602.7357 | 572.1119 | 551.9366
|  | Power Factor | 0.99321 | 0.99935 | 0.99838 | 0.99738 | 0.99661
|  | N-1 Load (A) | 110.0949 | 196.0152 | 275.1712 | 335.1596 | 375.0867
|  | N-1 Rating (A) | 742 | 742 | 742 | 742 | 742
|  | Contingency Utilisation (%) | 14.8376 | 26.4171 | 37.0851 | 45.1698 | 50.5508
|  | N-1 Hosting Capacity (A) | 631.9051 | 545.9848 | 466.8288 | 406.8404 | 366.9133
|  | N-1 Power Factor | 0.99321 | 0.99935 | 0.99838 | 0.99738 | 0.99661
|  | N-1 Limiting section | 3881-1 | 3881-1 | 3881-1 | 3881-1 | 3881-1
|  | Contingency Scenario | F3880 | F3880 | F3880 | F3880 | F3880
F389 | 389-1 | Load (A) | 12.5036 | 32.4065 | 54.6117 | 77.9544 | 101.2424
|  | Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Utilisation (%) | 1.603 | 4.1547 | 7.0015 | 9.9942 | 12.9798
|  | Hosting Capacity (A) | 767.4964 | 747.5935 | 725.3883 | 702.0456 | 678.7576
|  | Power Factor | 0.82903 | 0.97834 | 0.99397 | 0.99803 | 0.99943
|  | N-1 Load (A) | 47.7313 | 63.4672 | 80.1967 | 112.8168 | 160.2467
|  | N-1 Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Contingency Utilisation (%) | 6.1194 | 8.1368 | 10.2816 | 14.4637 | 20.5444
|  | N-1 Hosting Capacity (A) | 732.2687 | 716.5328 | 699.8033 | 667.1832 | 619.7533
|  | N-1 Power Factor | 0.82903 | 0.97834 | 0.99397 | 0.99803 | 0.99943
|  | N-1 Limiting section | 389-1(1) | 389-1(1) | 389-1(1) | 389-1(1) | 389-1(1)
|  | Contingency Scenario | F3670 | F3670 | F3670 | F474A | F474A
F389 | 389-2 | Load (A) | 65.1394 | 55.7378 | 45.3244 | 34.0391 | 22.4232
|  | Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Utilisation (%) | 8.3512 | 7.1459 | 5.8108 | 4.364 | 2.8748
|  | Hosting Capacity (A) | 714.8606 | 724.2622 | 734.6756 | 745.9609 | 757.5768
|  | Power Factor | 0.99829 | 0.99866 | 0.99908 | 0.99955 | 0.99997
|  | N-1 Load (A) | 94.9561 | 76.477 | 56.4317 | 45.1776 | 41.2927
|  | N-1 Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Contingency Utilisation (%) | 12.1739 | 9.8047 | 7.2348 | 5.792 | 5.2939
|  | N-1 Hosting Capacity (A) | 685.0439 | 703.523 | 723.5683 | 734.8224 | 738.7073
|  | N-1 Power Factor | 0.99829 | 0.99866 | 0.99908 | 0.99955 | 0.99997
|  | N-1 Limiting section | 389-2 | 389-2 | 389-2 | 389-2 | 389-2
|  | Contingency Scenario | F458 | F458 | F458 | F474A | F474A
F389 | 389-3 | Load (A) | 76.1369 | 87.8688 | 99.8613 | 111.9683 | 123.6585
|  | Rating (A) | 631 | 631 | 631 | 631 | 631
|  | Utilisation (%) | 12.0661 | 13.9253 | 15.8259 | 17.7446 | 19.5972
|  | Hosting Capacity (A) | 554.8631 | 543.1312 | 531.1387 | 519.0317 | 507.3415
|  | Power Factor | 0.99015 | 0.99418 | 0.9969 | 0.99864 | 0.99955
|  | N-1 Load (A) | 103.7201 | 111.4362 | 119.1695 | 157.9771 | 201.6318
|  | N-1 Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Contingency Utilisation (%) | 16.4374 | 17.6602 | 18.8858 | 25.036 | 31.9543
|  | N-1 Hosting Capacity (A) | 613.2799 | 605.5638 | 597.8305 | 559.0229 | 515.3682
|  | N-1 Power Factor | 0.99015 | 0.99418 | 0.9969 | 0.99864 | 0.99955
|  | N-1 Limiting section | 389-3(1) | 389-3(1) | 389-3(1) | 389-3(1) | 389-3(1)
|  | Contingency Scenario | F3670 | F3670 | F3670 | F474A | F474A
F390 | 390-1 | Load (A) | 22.4048 | 11.4747 | 7.5259 | 17.8582 | 27.577
|  | Rating (A) | 637 | 637 | 704 | 637 | 637
|  | Utilisation (%) | 3.5172 | 1.8014 | 1.069 | 2.8035 | 4.3292
|  | Hosting Capacity (A) | 614.5952 | 625.5253 | 696.4741 | 619.1418 | 609.423
|  | Power Factor | 0.97476 | 0.90212 | 0.5069 | 0.97381 | 0.99211
|  | N-1 Load (A) | 49.371 | 23.8829 | 10.5892 | 38.5352 | 60.4261
|  | N-1 Rating (A) | 637 | 637 | 637 | 637 | 637
|  | Contingency Utilisation (%) | 7.7506 | 3.7493 | 1.5041 | 6.0495 | 9.486
|  | N-1 Hosting Capacity (A) | 587.629 | 613.1171 | 626.4108 | 598.4648 | 576.5739
|  | N-1 Power Factor | 0.97476 | 0.90212 | 0.5069 | 0.97381 | 0.99211
|  | N-1 Limiting section | 390-1(2) | 390-1(2) | 390-1 | 390-1(2) | 390-1(2)
|  | Contingency Scenario | F391 | F391 | F391 | F391 | F391
F390 | 390-2 | Load (A) | 21.945 | 10.5674 | 4.2194 | 17.4323 | 27.3631
|  | Rating (A) | 578 | 578 | 578 | 578 | 578
|  | Utilisation (%) | 3.7967 | 1.8283 | 0.73 | 3.016 | 4.7341
|  | Hosting Capacity (A) | 556.055 | 567.4326 | 573.7806 | 560.5677 | 550.6369
|  | Power Factor | 0.99468 | 0.97907 | 0.90376 | 0.9973 | 0.99963
|  | N-1 Load (A) | 49.2696 | 23.5201 | 8.4573 | 38.3554 | 60.381
|  | N-1 Rating (A) | 653 | 653 | 653 | 653 | 653
|  | Contingency Utilisation (%) | 8.5242 | 4.0692 | 1.4632 | 6.6359 | 10.4465
|  | N-1 Hosting Capacity (A) | 603.7304 | 629.4799 | 644.5427 | 614.6446 | 592.619
|  | N-1 Power Factor | 0.99468 | 0.97907 | 0.90376 | 0.9973 | 0.99963
|  | N-1 Limiting section | 390-2(6) | 390-2(6) | 390-2(6) | 390-2(6) | 390-2(6)
|  | Contingency Scenario | F391 | F391 | F391 | F391 | F391
F3901 | 3901-1 | Load (A) | 98.1623 | 125.7081 | 169.0841 | 182.0332 | 179.3913
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 17.7509 | 22.732 | 30.5758 | 32.9174 | 32.4397
|  | Hosting Capacity (A) | 454.8377 | 427.2919 | 383.9159 | 370.9668 | 373.6087
|  | Power Factor | 0.99999 | 0.99992 | 0.99967 | 0.99959 | 0.99962
|  | N-1 Load (A) | 188.0151 | 241.0996 | 325.0316 | 350.1684 | 345.0292
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 33.9991 | 43.5985 | 58.7761 | 63.3216 | 62.3923
|  | N-1 Hosting Capacity (A) | 364.9849 | 311.9004 | 227.9684 | 202.8316 | 207.9708
|  | N-1 Power Factor | 0.99999 | 0.99992 | 0.99967 | 0.99959 | 0.99962
|  | N-1 Limiting section | 3901-1(2) | 3901-1(2) | 3901-1(2) | 3901-1(2) | 3901-1(2)
|  | Contingency Scenario | F475 | F475 | F475 | F475 | F475
F391 | 391-1 | Load (A) | 27.3522 | 13.4781 | 5.8107 | 21.4386 | 33.5594
|  | Rating (A) | 623 | 623 | 623 | 623 | 623
|  | Utilisation (%) | 4.3904 | 2.1634 | 0.93269 | 3.4412 | 5.3867
|  | Hosting Capacity (A) | 595.6478 | 609.5219 | 617.1893 | 601.5614 | 589.4406
|  | Power Factor | 0.99546 | 0.96973 | 0.75832 | 0.98339 | 0.99378
|  | N-1 Load (A) | 49.1879 | 23.563 | 8.6585 | 38.4777 | 60.6814
|  | N-1 Rating (A) | 623 | 623 | 623 | 623 | 623
|  | Contingency Utilisation (%) | 7.8953 | 3.7822 | 1.3898 | 6.1762 | 9.7402
|  | N-1 Hosting Capacity (A) | 573.8121 | 599.437 | 614.3415 | 584.5223 | 562.3186
|  | N-1 Power Factor | 0.99948 | 0.96973 | 0.75832 | 0.98339 | 0.99996
|  | N-1 Limiting section | 391-1(1) | 391-1 | 391-1 | 391-1 | 391-1(1)
|  | Contingency Scenario | F390 | F390 | F390 | F390 | F390
F392 | 392-1 | Load (A) | 40.4821 | 76.3492 | 111.0898 | 142.1326 | 168.7173
|  | Rating (A) | 708 | 708 | 708 | 708 | 708
|  | Utilisation (%) | 5.7178 | 10.7838 | 15.6906 | 20.0752 | 23.8301
|  | Hosting Capacity (A) | 667.5179 | 631.6508 | 596.9102 | 565.8674 | 539.2827
|  | Power Factor | 0.99989 | 0.99968 | 0.99874 | 0.99754 | 0.99626
|  | N-1 Load (A) | 80.976 | 152.673 | 222.0331 | 283.9469 | 336.9482
|  | N-1 Rating (A) | 708 | 708 | 708 | 708 | 708
|  | Contingency Utilisation (%) | 11.4373 | 21.564 | 31.3606 | 40.1055 | 47.5916
|  | N-1 Hosting Capacity (A) | 627.024 | 555.327 | 485.9669 | 424.0531 | 371.0518
|  | N-1 Power Factor | 0.99989 | 0.99968 | 0.99874 | 0.99754 | 0.99626
|  | N-1 Limiting section | 392-1(1) | 392-1(1) | 392-1(1) | 392-1(1) | 392-1(1)
|  | Contingency Scenario | F473 | F473 | F473 | F473 | F473
F393 | 393-1 | Load (A) | 131.8379 | 126.5116 | 120.1731 | 112.8414 | 104.8914
|  | Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Utilisation (%) | 32.7141 | 31.3925 | 29.8196 | 28.0004 | 26.0276
|  | Hosting Capacity (A) | 271.1621 | 276.4884 | 282.8269 | 290.1586 | 298.1086
|  | Power Factor | 0.99849 | 0.9986 | 0.99872 | 0.99885 | 0.99896
|  | N-1 Load (A) | 132.243 | 126.8686 | 120.4831 | 113.1075 | 105.094
|  | N-1 Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Contingency Utilisation (%) | 32.8146 | 31.481 | 29.8965 | 28.0664 | 26.0779
|  | N-1 Hosting Capacity (A) | 270.757 | 276.1314 | 282.5169 | 289.8925 | 297.906
|  | N-1 Power Factor | 0.99849 | 0.9986 | 0.99872 | 0.99885 | 0.99896
|  | N-1 Limiting section | 393-1(1) | 393-1(1) | 393-1(1) | 393-1(1) | 393-1(1)
|  | Contingency Scenario | F3751 | F3751 | F3751 | F3751 | F3751
F394 | 394-1 | Load (A) | 38.3644 | 62.2127 | 86.5159 | 113.1822 | 137.9943
|  | Rating (A) | 734 | 734 | 716 | 716 | 716
|  | Utilisation (%) | 5.2268 | 8.4759 | 12.0832 | 15.8076 | 19.273
|  | Hosting Capacity (A) | 695.6356 | 671.7873 | 629.4841 | 602.8178 | 578.0057
|  | Power Factor | 0.83959 | 0.95127 | 0.99776 | 0.99832 | 0.99745
|  | N-1 Load (A) | 66.6414 | 116.8537 | 170.39 | 223.1829 | 272.0751
|  | N-1 Rating (A) | 716 | 716 | 716 | 716 | 716
|  | Contingency Utilisation (%) | 9.0792 | 16.3203 | 23.7975 | 31.1708 | 37.9993
|  | N-1 Hosting Capacity (A) | 649.3586 | 599.1463 | 545.61 | 492.8171 | 443.9249
|  | N-1 Power Factor | 0.83959 | 0.99064 | 0.99909 | 0.99832 | 0.99745
|  | N-1 Limiting section | 394-1 | 394-1(6) | 394-1(9) | 394-1(9) | 394-1(9)
|  | Contingency Scenario | F3640 | F3640 | F3640 | F3640 | F3640
F3940 | 3940-1 | Load (A) | 135.5565 | 172.8103 | 229.7857 | 249.0911 | 248.8573
|  | Rating (A) | 437 | 437 | 437 | 437 | 437
|  | Utilisation (%) | 31.0198 | 39.5447 | 52.5825 | 57.0003 | 56.9467
|  | Hosting Capacity (A) | 301.4435 | 264.1897 | 207.2143 | 187.9089 | 188.1427
|  | Power Factor | 0.99977 | 0.99987 | 0.99994 | 0.99995 | 0.99995
|  | N-1 Load (A) | 246.9776 | 314.9431 | 418.9454 | 454.2027 | 453.7748
|  | N-1 Rating (A) | 437 | 437 | 437 | 437 | 437
|  | Contingency Utilisation (%) | 56.5166 | 72.0694 | 95.8685 | 103.9365 | 103.8386
|  | N-1 Hosting Capacity (A) | 190.0224 | 122.0569 | 18.0546 | -17.2027 | -16.7748
|  | N-1 Power Factor | 0.99977 | 0.99987 | 0.99994 | 0.99995 | 0.99995
|  | N-1 Limiting section | 3940-1 | 3940-1 | 3940-1 | 3940-1 | 3940-1
|  | Contingency Scenario | F3941 | F3941 | F3941 | F3941 | F3941
F3941 | 3941-1 | Load (A) | 111.2072 | 141.7623 | 188.4946 | 204.3297 | 204.1379
|  | Rating (A) | 437 | 437 | 437 | 437 | 437
|  | Utilisation (%) | 25.4479 | 32.4399 | 43.1338 | 46.7574 | 46.7135
|  | Hosting Capacity (A) | 325.7928 | 295.2377 | 248.5054 | 232.6703 | 232.8621
|  | Power Factor | 0.99965 | 0.9998 | 0.9999 | 0.99992 | 0.99992
|  | N-1 Load (A) | 247.0452 | 315.058 | 419.1653 | 454.4674 | 454.0386
|  | N-1 Rating (A) | 437 | 437 | 437 | 437 | 437
|  | Contingency Utilisation (%) | 56.5321 | 72.0956 | 95.9188 | 103.9971 | 103.899
|  | N-1 Hosting Capacity (A) | 189.9548 | 121.942 | 17.8347 | -17.4674 | -17.0386
|  | N-1 Power Factor | 0.99965 | 0.9998 | 0.9999 | 0.99992 | 0.99992
|  | N-1 Limiting section | 3941-1 | 3941-1 | 3941-1 | 3941-1 | 3941-1
|  | Contingency Scenario | F3940 | F3940 | F3940 | F3940 | F3940
F395 | 395-1 | Load (A) | 50.4769 | 19.8763 | 12.3806 | 45.3141 | 77.5005
|  | Rating (A) | 654 | 654 | 654 | 654 | 654
|  | Utilisation (%) | 7.7182 | 3.0449 | 1.8931 | 6.9321 | 11.8533
|  | Hosting Capacity (A) | 603.5231 | 634.1237 | 641.6194 | 608.6859 | 576.4995
|  | Power Factor | 0.99926 | 0.99869 | 0.99242 | 0.99947 | 0.99944
F396 | 396-1 | Load (A) | 76.1969 | 67.5236 | 58.4212 | 48.9969 | 39.6847
|  | Rating (A) | 806 | 806 | 806 | 806 | 806
|  | Utilisation (%) | 9.4537 | 8.3776 | 7.2483 | 6.079 | 4.9237
|  | Hosting Capacity (A) | 729.8031 | 738.4764 | 747.5788 | 757.0031 | 766.3153
|  | Power Factor | 0.99954 | 0.99926 | 0.99911 | 0.99897 | 0.99889
|  | N-1 Load (A) | 125.224 | 112.6701 | 99.4839 | 85.8116 | 85.7636
|  | N-1 Rating (A) | 806 | 806 | 806 | 806 | 806
|  | Contingency Utilisation (%) | 15.5365 | 13.9789 | 12.3429 | 10.6466 | 10.6406
|  | N-1 Hosting Capacity (A) | 680.776 | 693.3299 | 706.5161 | 720.1884 | 720.2364
|  | N-1 Power Factor | 0.99954 | 0.99926 | 0.99911 | 0.99897 | 0.99889
|  | N-1 Limiting section | 396-1(7) | 396-1(7) | 396-1(7) | 396-1(7) | 396-1(7)
|  | Contingency Scenario | F3751 | F3751 | F3751 | F3751 | F3756
F3960 | 3960-1 | Load (A) | 28.3296 | 44.1082 | 60.6642 | 76.8044 | 91.2774
|  | Rating (A) | 711 | 711 | 711 | 711 | 711
|  | Utilisation (%) | 3.9845 | 6.2037 | 8.5322 | 10.8023 | 12.8379
|  | Hosting Capacity (A) | 682.6704 | 666.8918 | 650.3358 | 634.1956 | 619.7226
|  | Power Factor | 0.79293 | 0.91012 | 0.94926 | 0.96663 | 0.97551
|  | N-1 Load (A) | 32.1734 | 51.5813 | 71.8334 | 91.6172 | 109.6536
|  | N-1 Rating (A) | 711 | 711 | 711 | 711 | 711
|  | Contingency Utilisation (%) | 4.5251 | 7.2548 | 10.1032 | 12.8857 | 15.4224
|  | N-1 Hosting Capacity (A) | 678.8266 | 659.4187 | 639.1666 | 619.3828 | 601.3464
|  | N-1 Power Factor | 0.79293 | 0.91012 | 0.94926 | 0.96663 | 0.97551
|  | N-1 Limiting section | 3960-1(1) | 3960-1(1) | 3960-1(1) | 3960-1(1) | 3960-1(1)
|  | Contingency Scenario | F362 | F362 | F362 | F363 | F363
F397 | 397-1 | Load (A) | 2.5602 | 2.5602 | 2.5602 | 2.5602 | 2.5602
|  | Rating (A) | 602 | 602 | 602 | 602 | 602
|  | Utilisation (%) | 0.42528 | 0.42528 | 0.42528 | 0.42528 | 0.42528
|  | Hosting Capacity (A) | 599.4398 | 599.4398 | 599.4398 | 599.4398 | 599.4398
|  | Power Factor | 1 | 1 | 1 | 1 | 1
F3972 | 3972-1 | Load (A) | 11.1556 | 16.5497 | 23.2207 | 28.4657 | 35.6534
|  | Rating (A) | 893 | 893 | 893 | 818 | 818
|  | Utilisation (%) | 1.2492 | 1.8533 | 2.6003 | 3.4799 | 4.3586
|  | Hosting Capacity (A) | 881.8444 | 876.4503 | 869.7793 | 789.5343 | 782.3466
|  | Power Factor | 0.41139 | 0.72259 | 0.83979 | 0.94912 | 0.96051
|  | N-1 Load (A) | 18.3074 | 28.092 | 37.5053 | 46.0902 | 53.9729
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 2.2381 | 3.4342 | 4.585 | 5.6345 | 6.5982
|  | N-1 Hosting Capacity (A) | 781.6926 | 771.908 | 762.4947 | 753.9098 | 746.0271
|  | N-1 Power Factor | 0.65281 | 0.87454 | 0.92947 | 0.94912 | 0.96051
|  | N-1 Limiting section | 3972-1 | 3972-1 | 3972-1(6) | 3972-1 | 3972-1
|  | Contingency Scenario | F3960 | F3960 | F3960 | F3960 | F363
F3972 | 3972-1_a | Load (A) | 7.9185 | 14.2363 | 21.431 | 28.8407 | 35.9823
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 0.96803 | 1.7404 | 2.6199 | 3.5258 | 4.3988
|  | Hosting Capacity (A) | 810.0815 | 803.7637 | 796.569 | 789.1593 | 782.0177
|  | Power Factor | 0.57953 | 0.83993 | 0.90982 | 0.93893 | 0.95417
|  | N-1 Load (A) | 18.2719 | 28.0705 | 37.4909 | 46.08 | 54.1829
|  | N-1 Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Contingency Utilisation (%) | 2.2337 | 3.4316 | 4.5832 | 5.6333 | 6.6238
|  | N-1 Hosting Capacity (A) | 799.7281 | 789.9295 | 780.5091 | 771.92 | 763.8171
|  | N-1 Power Factor | 0.57953 | 0.87454 | 0.92747 | 0.94912 | 0.95417
|  | N-1 Limiting section | 3972-1_a | 3972-1 | 3972-1 | 3972-1 | 3972-1_a
|  | Contingency Scenario | F3960 | F3960 | F3960 | F3960 | F363
F3980 | 3980-1 | Load (A) | 3.6832 | 6.1455 | 9.7415 | 13.5724 | 17.277
|  | Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Utilisation (%) | 0.51658 | 0.86192 | 1.3663 | 1.9036 | 2.4231
|  | Hosting Capacity (A) | 709.3168 | 706.8545 | 703.2585 | 699.4276 | 695.723
|  | Power Factor | 0.27414 | 0.81877 | 0.93408 | 0.96824 | 0.98184
|  | N-1 Load (A) | 5.4531 | 11.066 | 18.4968 | 26.1863 | 33.5465
|  | N-1 Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Contingency Utilisation (%) | 0.76481 | 1.552 | 2.5942 | 3.6727 | 4.705
|  | N-1 Hosting Capacity (A) | 707.5469 | 701.934 | 694.5032 | 686.8137 | 679.4535
|  | N-1 Power Factor | 0.27414 | 0.81877 | 0.93408 | 0.96824 | 0.98184
|  | N-1 Limiting section | 3980-1 | 3980-1 | 3980-1 | 3980-1 | 3980-1
|  | Contingency Scenario | F401 | F401 | F401 | F401 | F401
F401 | 401-1 | Load (A) | 3.3651 | 5.788 | 9.2872 | 12.9959 | 16.5758
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 0.60852 | 1.0467 | 1.6794 | 2.3501 | 2.9974
|  | Hosting Capacity (A) | 549.6349 | 547.212 | 543.7128 | 540.0041 | 536.4242
|  | Power Factor | 0.27858 | 0.83133 | 0.94006 | 0.97145 | 0.98381
|  | N-1 Load (A) | 3.3801 | 9.949 | 17.8925 | 25.8091 | 33.3002
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 0.61123 | 1.7991 | 3.2355 | 4.6671 | 6.0217
|  | N-1 Hosting Capacity (A) | 549.6199 | 543.051 | 535.1075 | 527.1909 | 519.6998
|  | N-1 Power Factor | 0.27858 | 0.83133 | 0.94006 | 0.97145 | 0.98381
|  | N-1 Limiting section | 401-1 | 401-1 | 401-1 | 401-1 | 401-1
|  | Contingency Scenario | F363 | F3980 | F3980 | F3980 | F3980
F402 | 402-1 | Load (A) | 45.0795 | 69.1714 | 93.4275 | 117.2801 | 139.5591
|  | Rating (A) | 579 | 579 | 579 | 579 | 579
|  | Utilisation (%) | 7.7858 | 11.9467 | 16.136 | 20.2556 | 24.1035
|  | Hosting Capacity (A) | 533.9205 | 509.8286 | 485.5725 | 461.7199 | 439.4409
|  | Power Factor | 0.99995 | 0.99988 | 0.99935 | 0.99856 | 0.99757
|  | N-1 Load (A) | 67.5997 | 106.8186 | 146.2464 | 185.1063 | 221.5785
|  | N-1 Rating (A) | 579 | 579 | 579 | 579 | 579
|  | Contingency Utilisation (%) | 11.6753 | 18.4488 | 25.2584 | 31.97 | 38.2692
|  | N-1 Hosting Capacity (A) | 511.4003 | 472.1814 | 432.7536 | 393.8937 | 357.4215
|  | N-1 Power Factor | 0.99995 | 0.99988 | 0.99935 | 0.99856 | 0.99757
|  | N-1 Limiting section | 402-1(5) | 402-1(5) | 402-1(5) | 402-1(5) | 402-1(5)
|  | Contingency Scenario | F469 | F469 | F469 | F469 | F469
F402 | 402-2 | Load (A) | 23.9305 | 32.2022 | 40.3082 | 48.0643 | 55.1054
|  | Rating (A) | 439 | 439 | 439 | 439 | 439
|  | Utilisation (%) | 5.4511 | 7.3354 | 9.1818 | 10.9486 | 12.5525
|  | Hosting Capacity (A) | 415.0695 | 406.7978 | 398.6918 | 390.9357 | 383.8946
|  | Power Factor | 0.99982 | 0.99969 | 0.99954 | 0.99934 | 0.99914
|  | N-1 Load (A) |  |  |  | 48.0643 | 55.1055
|  | N-1 Rating (A) | 439 | 439 | 439 | 439 | 439
|  | Contingency Utilisation (%) |  |  |  | 10.9486 | 12.5525
|  | N-1 Hosting Capacity (A) |  |  |  | 390.9357 | 383.8945
|  | N-1 Power Factor |  |  |  | 0.99934 | 0.99914
|  | N-1 Limiting section |  |  |  | 402-2 | 402-2
|  | Contingency Scenario |  |  |  | F3590 | F3590
F402 | 402-3 | Load (A) | 21.1534 | 36.9855 | 53.1468 | 69.2541 | 84.505
|  | Rating (A) | 812 | 812 | 812 | 812 | 812
|  | Utilisation (%) | 2.6051 | 4.5549 | 6.5452 | 8.5288 | 10.407
|  | Hosting Capacity (A) | 790.8466 | 775.0145 | 758.8532 | 742.7459 | 727.495
|  | Power Factor | 0.99975 | 0.9998 | 0.99961 | 0.9993 | 0.9987
|  | N-1 Load (A) | 43.7794 | 74.8434 | 106.3011 | 137.5433 | 167.103
|  | N-1 Rating (A) | 812 | 812 | 812 | 812 | 812
|  | Contingency Utilisation (%) | 5.3915 | 9.2172 | 13.0913 | 16.9388 | 20.5792
|  | N-1 Hosting Capacity (A) | 768.2206 | 737.1566 | 705.6989 | 674.4567 | 644.897
|  | N-1 Power Factor | 0.99975 | 0.9998 | 0.99961 | 0.9993 | 0.9987
|  | N-1 Limiting section | 402-3 | 402-3 | 402-3 | 402-3 | 402-3
|  | Contingency Scenario | F469 | F469 | F469 | F469 | F469
F404 | 404-1 | Load (A) | 4.6284 | 8.7808 | 13.1829 | 17.6488 | 21.9434
|  | Rating (A) | 155 | 155 | 155 | 155 | 155
|  | Utilisation (%) | 2.986 | 5.6744 | 8.5051 | 11.39 | 14.1594
|  | Hosting Capacity (A) | 150.3716 | 146.2192 | 141.8171 | 137.3512 | 133.0566
|  | Power Factor | 0.95396 | 0.99024 | 0.99582 | 0.99857 | 0.99943
|  | N-1 Load (A) | 4.629 | 8.7959
|  | N-1 Rating (A) | 155 | 155 | 155 | 155 | 155
|  | Contingency Utilisation (%) | 2.9865 | 5.6748
|  | N-1 Hosting Capacity (A) | 150.371 | 146.2041
|  | N-1 Power Factor | 0.95396 | 0.99024
|  | N-1 Limiting section | 404-1(6) | 404-1
|  | Contingency Scenario | F469 | F469
F405 | 405-1 | Load (A) | 13.655 | 30.7876 | 47.8658 | 64.553 | 80.1314
|  | Rating (A) | 820 | 807 | 807 | 807 | 807
|  | Utilisation (%) | 1.6731 | 3.8153 | 5.9313 | 7.9992 | 9.9297
|  | Hosting Capacity (A) | 806.345 | 776.2124 | 759.1342 | 742.447 | 726.8686
|  | Power Factor | 0.98587 | 0.99982 | 0.99999 | 0.99986 | 0.99961
|  | N-1 Load (A) | 47.0478 | 65.6326 | 91.621 | 128.991 | 163.7025
|  | N-1 Rating (A) | 807 | 807 | 807 | 807 | 807
|  | Contingency Utilisation (%) | 5.83 | 8.1329 | 11.3533 | 15.984 | 20.2853
|  | N-1 Hosting Capacity (A) | 759.9522 | 741.3674 | 715.379 | 678.009 | 643.2975
|  | N-1 Power Factor | 0.99753 | 0.99982 | 0.99999 | 0.99986 | 0.99961
|  | N-1 Limiting section | 405-1(1) | 405-1(1) | 405-1(1) | 405-1(1) | 405-1(1)
|  | Contingency Scenario | F3591 | F3591 | F3590 | F3590 | F3590
F405 | 405-3 | Load (A) | 13.4634 | 30.7861 | 47.8791 | 64.5763 | 80.1634
|  | Rating (A) | 774 | 774 | 774 | 774 | 774
|  | Utilisation (%) | 1.7395 | 3.9775 | 6.1859 | 8.3432 | 10.357
|  | Hosting Capacity (A) | 760.5366 | 743.2139 | 726.1209 | 709.4237 | 693.8366
|  | Power Factor | 0.99978 | 0.99983 | 0.99973 | 0.99958 | 0.99938
|  | N-1 Load (A) | 47.062 | 65.6599 | 91.6444 | 129.0234 | 163.7428
|  | N-1 Rating (A) | 774 | 774 | 774 | 774 | 774
|  | Contingency Utilisation (%) | 6.0804 | 8.4832 | 11.8404 | 16.6697 | 21.1554
|  | N-1 Hosting Capacity (A) | 726.938 | 708.3401 | 682.3556 | 644.9766 | 610.2572
|  | N-1 Power Factor | 0.99978 | 0.99983 | 0.99973 | 0.99958 | 0.99938
|  | N-1 Limiting section | 405-3(1) | 405-3(1) | 405-3(1) | 405-3(1) | 405-3(1)
|  | Contingency Scenario | F3591 | F3591 | F3590 | F3590 | F3590
F406A&B | 406B-1 | Load (A) | 1.7068 | 1.7072 | 1.7075 | 1.7079 | 1.7082
|  | Rating (A) | 796 | 796 | 796 | 796 | 796
|  | Utilisation (%) | 0.21442 | 0.21447 | 0.21452 | 0.21456 | 0.21459
|  | Hosting Capacity (A) | 794.2932 | 794.2928 | 794.2925 | 794.2921 | 794.2918
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 52.7439 | 117.3595 | 188.8337 | 260.7532 | 328.1852
|  | N-1 Rating (A) | 0 | 0 | 0 | 0 | 0
|  | Contingency Utilisation (%) | 6.762 | 15.0461 | 24.2095 | 33.4299 | 42.075
|  | N-1 Hosting Capacity (A) | -52.7439 | -117.3595 | -188.8337 | -260.7532 | -328.1852
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 406B-1 | 406B-1 | 406B-1 | 406B-1 | 406B-1
|  | Contingency Scenario | F496 | F453 | F453 | F453 | F453
F407 | 407-1 | Load (A) | 52.1771 | 31.9087 | 9.8494 | 14.0665 | 37.7398
|  | Rating (A) | 777 | 777 | 777 | 777 | 777
|  | Utilisation (%) | 6.7152 | 4.1067 | 1.2676 | 1.8104 | 4.8598
|  | Hosting Capacity (A) | 724.8229 | 745.0913 | 767.1506 | 762.9335 | 739.2602
|  | Power Factor | 0.99987 | 0.99931 | 0.98546 | 0.99234 | 0.99994
|  | N-1 Load (A) | 98.9203 | 60.4134 | 18.4419 | 26.471 | 71.3828
|  | N-1 Rating (A) | 777 | 777 | 777 | 777 | 777
|  | Contingency Utilisation (%) | 12.7311 | 7.7752 | 2.3735 | 3.4068 | 9.187
|  | N-1 Hosting Capacity (A) | 678.0797 | 716.5866 | 758.5581 | 750.529 | 705.6172
|  | N-1 Power Factor | 0.99987 | 0.99931 | 0.99695 | 0.99234 | 0.99994
|  | N-1 Limiting section | 407-1(6) | 407-1(6)_a | 407-1(6) | 407-1(6)_a | 407-1(6)
|  | Contingency Scenario | F409 | F409 | F409 | F409 | F409
F408 | 408-1 | Load (A) | 8.976 | 33.4789 | 59.481 | 86.4357 | 112.836
|  | Rating (A) | 529 | 529 | 529 | 529 | 529
|  | Utilisation (%) | 1.6968 | 6.3287 | 11.244 | 16.3394 | 21.3301
|  | Hosting Capacity (A) | 520.024 | 495.5211 | 469.519 | 442.5643 | 416.164
|  | Power Factor | 0.99123 | 0.99965 | 1 | 0.99982 | 0.9994
|  | N-1 Load (A) | 16.2444 | 60.6244 | 107.6864 | 156.4464 | 204.1828
|  | N-1 Rating (A) | 529 | 529 | 529 | 529 | 529
|  | Contingency Utilisation (%) | 3.0708 | 11.4602 | 20.3566 | 29.574 | 38.5979
|  | N-1 Hosting Capacity (A) | 512.7556 | 468.3756 | 421.3136 | 372.5536 | 324.8172
|  | N-1 Power Factor | 0.99123 | 0.99965 | 1 | 0.99982 | 0.9994
|  | N-1 Limiting section | 408-1(10) | 408-1(10) | 408-1(10) | 408-1(10) | 408-1(10)
|  | Contingency Scenario | F452 | F452 | F452 | F452 | F452
F409 | 409-1 | Load (A) | 46.5956 | 28.4729 | 8.6723 | 12.482 | 33.7119
|  | Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Utilisation (%) | 5.9738 | 3.6506 | 1.1131 | 1.6009 | 4.3221
|  | Hosting Capacity (A) | 733.4044 | 751.5271 | 771.3277 | 767.518 | 746.2881
|  | Power Factor | 0.99998 | 0.99996 | 0.99838 | 0.99962 | 0.99996
|  | N-1 Load (A) | 98.9711 | 60.4284 | 18.3763 | 26.4255 | 71.364
|  | N-1 Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Contingency Utilisation (%) | 12.6886 | 7.7472 | 2.3559 | 3.3879 | 9.1492
|  | N-1 Hosting Capacity (A) | 681.0289 | 719.5716 | 761.6237 | 753.5745 | 708.636
|  | N-1 Power Factor | 0.99998 | 0.99996 | 0.99838 | 0.99962 | 0.99996
|  | N-1 Limiting section | 409-1 | 409-1 | 409-1 | 409-1 | 409-1
|  | Contingency Scenario | F407 | F407 | F407 | F407 | F407
F410 | 410-1 | Load (A) | 50.1023 | 38.4028 | 26.8353 | 21.8903 | 26.5767
|  | Rating (A) | 400 | 400 | 400 | 400 | 400
|  | Utilisation (%) | 12.5256 | 9.6007 | 6.7088 | 5.4726 | 6.6442
|  | Hosting Capacity (A) | 349.8977 | 361.5972 | 373.1647 | 378.1097 | 373.4233
|  | Power Factor | 0.90746 | 0.82805 | 0.58128 | 1 | 0.57912
|  | N-1 Load (A) | 79.7733 | 59.1961 | 52.7659 | 47.1887 | 52.4649
|  | N-1 Rating (A) | 451 | 451 | 451 | 451 | 451
|  | Contingency Utilisation (%) | 19.9433 | 14.799 | 13.1915 | 11.7972 | 13.1162
|  | N-1 Hosting Capacity (A) | 371.2267 | 391.8039 | 398.2341 | 403.8113 | 398.5351
|  | N-1 Power Factor | 0.90746 | 0.82805 | 0.58128 | 1 | 0.57912
|  | N-1 Limiting section | 410-1 | 410-1 | 410-1 | 410-1 | 410-1
|  | Contingency Scenario | F703 | F703 | F571 | F571 | F539
F411 | 411-1 | Load (A) | 24.5508 | 9.4697 | 7.37 | 25.8676 | 44.5845
|  | Rating (A) | 558 | 558 | 558 | 558 | 558
|  | Utilisation (%) | 4.3998 | 1.6971 | 1.3214 | 4.6364 | 7.9908
|  | Hosting Capacity (A) | 533.4492 | 548.5303 | 550.63 | 532.1324 | 513.4155
|  | Power Factor | 0.99984 | 0.99971 | 0.99972 | 0.9995 | 0.99928
|  | N-1 Load (A) | 54.2962 | 33.7051 | 25.9239 | 50.5209 | 87.0476
|  | N-1 Rating (A) | 631 | 631 | 631 | 631 | 631
|  | Contingency Utilisation (%) | 9.7305 | 6.0403 | 4.6459 | 9.0539 | 15.5999
|  | N-1 Hosting Capacity (A) | 576.7038 | 597.2949 | 605.0761 | 580.4791 | 543.9524
|  | N-1 Power Factor | 0.99984 | 0.99971 | 0.99972 | 0.9995 | 0.99928
|  | N-1 Limiting section | 411-1 | 411-1 | 411-1 | 411-1 | 411-1
|  | Contingency Scenario | F354 | F354 | F355 | F361 | F361
F412 | 412-1 | Load (A) | 76.6645 | 113.4322 | 150.9139 | 188.1814 | 223.2612
|  | Rating (A) | 823 | 823 | 823 | 823 | 823
|  | Utilisation (%) | 9.3168 | 13.7828 | 18.3383 | 22.868 | 27.1316
|  | Hosting Capacity (A) | 746.3355 | 709.5678 | 672.0861 | 634.8186 | 599.7388
|  | Power Factor | 0.99971 | 0.99992 | 0.99918 | 0.99785 | 0.99616
|  | N-1 Load (A) | 167.3202 | 246.1551 | 326.4082 | 406.5054 | 482.3597
|  | N-1 Rating (A) | 823 | 823 | 823 | 823 | 823
|  | Contingency Utilisation (%) | 20.3305 | 29.9095 | 39.6608 | 49.3931 | 58.6099
|  | N-1 Hosting Capacity (A) | 655.6798 | 576.8449 | 496.5918 | 416.4946 | 340.6403
|  | N-1 Power Factor | 0.99971 | 0.99992 | 0.99918 | 0.99785 | 0.99749
|  | N-1 Limiting section | 412-1(2) | 412-1(2) | 412-1(2) | 412-1(2) | 412-1(3)
|  | Contingency Scenario | F350 | F350 | F350 | F350 | F350
F413 | 413-1 | Load (A) | 9.9823 | 39.34 | 70.9165 | 103.1101 | 134.0748
|  | Rating (A) | 611 | 611 | 611 | 611 | 611
|  | Utilisation (%) | 1.6338 | 6.4386 | 11.6066 | 16.8756 | 21.9435
|  | Hosting Capacity (A) | 601.0177 | 571.66 | 540.0835 | 507.8899 | 476.9252
|  | Power Factor | 0.83339 | 0.99376 | 0.99902 | 0.99856 | 0.99803
|  | N-1 Load (A) | 20.8637 | 74.9767 | 135.8621 | 197.5222 | 256.8214
|  | N-1 Rating (A) | 611 | 611 | 611 | 611 | 611
|  | Contingency Utilisation (%) | 3.4147 | 12.2711 | 22.236 | 32.3277 | 42.033
|  | N-1 Hosting Capacity (A) | 590.1363 | 536.0233 | 475.1379 | 413.4778 | 354.1786
|  | N-1 Power Factor | 0.83339 | 0.99376 | 0.99902 | 0.99856 | 0.99803
|  | N-1 Limiting section | 413-1 | 413-1 | 413-1 | 413-1 | 413-1
|  | Contingency Scenario | F371 | F372 | F372 | F372 | F372
F414 | 414-1 | Load (A) | 7.8774 | 20.993 | 34.8464 | 48.8572 | 62.3567
|  | Rating (A) | 500 | 495 | 495 | 495 | 495
|  | Utilisation (%) | 1.5755 | 4.241 | 7.0397 | 9.8701 | 12.5973
|  | Hosting Capacity (A) | 492.1226 | 474.007 | 460.1536 | 446.1428 | 432.6433
|  | Power Factor | 0.95117 | 0.99997 | 0.9999 | 0.99964 | 0.99929
|  | N-1 Load (A) | 19.8417 | 51.6 | 84.3527 | 117.5326 | 149.5368
|  | N-1 Rating (A) | 495 | 495 | 495 | 495 | 495
|  | Contingency Utilisation (%) | 4.0084 | 10.4242 | 17.0409 | 23.744 | 30.2095
|  | N-1 Hosting Capacity (A) | 475.1583 | 443.4 | 410.6473 | 377.4674 | 345.4632
|  | N-1 Power Factor | 0.99783 | 0.99997 | 0.9999 | 0.99964 | 0.99929
|  | N-1 Limiting section | 414-1(4) | 414-1(4) | 414-1(4) | 414-1(4) | 414-1(4)
|  | Contingency Scenario | F558 | F558 | F558 | F558 | F558
F415 | 415-1 | Load (A) | 47.3983 | 47.4005 | 47.4025 | 47.4046 | 47.4073
|  | Rating (A) | 628 | 628 | 628 | 628 | 628
|  | Utilisation (%) | 7.5521 | 7.5524 | 7.5528 | 7.5531 | 7.5535
|  | Hosting Capacity (A) | 580.6017 | 580.5995 | 580.5975 | 580.5954 | 580.5927
|  | Power Factor | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973
F416 | 416-1 | Load (A) | 51.8745 | 43.4607 | 34.6653 | 26.594 | 20.2299
|  | Rating (A) | 355 | 355 | 355 | 355 | 355
|  | Utilisation (%) | 14.6125 | 12.2424 | 9.7649 | 7.4913 | 5.6986
|  | Hosting Capacity (A) | 303.1255 | 311.5393 | 320.3347 | 328.406 | 334.7701
|  | Power Factor | 0.99728 | 0.9954 | 0.99176 | 0.98471 | 0.97217
|  | N-1 Load (A) | 100.9301 | 84.3541 | 67.0182 | 51.0814 | 38.4624
|  | N-1 Rating (A) | 470 | 470 | 470 | 470 | 470
|  | Contingency Utilisation (%) | 28.431 | 23.7617 | 18.8784 | 14.3891 | 10.8345
|  | N-1 Hosting Capacity (A) | 369.0699 | 385.6459 | 402.9818 | 418.9186 | 431.5376
|  | N-1 Power Factor | 0.99728 | 0.9954 | 0.99176 | 0.98471 | 0.97217
|  | N-1 Limiting section | 416-1 | 416-1 | 416-1 | 416-1 | 416-1
|  | Contingency Scenario | F575 | F575 | F575 | F575 | F575
F417 | 417-1 | Load (A) | 51.3971 | 77.3734 | 103.857 | 130.1329 | 154.7493
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 6.2833 | 9.4589 | 12.6965 | 15.9087 | 18.918
|  | Hosting Capacity (A) | 766.6029 | 740.6266 | 714.143 | 687.8671 | 663.2507
|  | Power Factor | 0.99994 | 0.99922 | 0.99806 | 0.99668 | 0.9952
|  | N-1 Load (A) | 126.7279 | 188.2175 | 250.6928 | 312.6883 | 370.9591
|  | N-1 Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Contingency Utilisation (%) | 15.4924 | 23.0095 | 30.647 | 38.226 | 45.3495
|  | N-1 Hosting Capacity (A) | 691.2721 | 629.7825 | 567.3072 | 505.3117 | 447.0409
|  | N-1 Power Factor | 0.99994 | 0.99922 | 0.99806 | 0.99668 | 0.9952
|  | N-1 Limiting section | 417-1 | 417-1 | 417-1 | 417-1 | 417-1
|  | Contingency Scenario | F412 | F412 | F412 | F412 | F412
F418 | 418-1 | Load (A) | 20.3639 | 42.6649 | 65.2122 | 87.6261 | 108.8983
|  | Rating (A) | 631 | 631 | 631 | 631 | 631
|  | Utilisation (%) | 3.2272 | 6.7615 | 10.3347 | 13.8869 | 17.2581
|  | Hosting Capacity (A) | 610.6361 | 588.3351 | 565.7878 | 543.3739 | 522.1017
|  | Power Factor | 0.99986 | 0.99997 | 0.99989 | 0.99979 | 0.99966
F420 | 420-1 | Load (A) | 108.7785 | 113.9632 | 120.9949 | 125.0302 | 131.4709
|  | Rating (A) | 349 | 349 | 349 | 349 | 349
|  | Utilisation (%) | 31.1686 | 32.6542 | 34.669 | 35.8253 | 37.6707
|  | Hosting Capacity (A) | 240.2215 | 235.0368 | 228.0051 | 223.9698 | 217.5291
|  | Power Factor | 0.9998 | 0.99986 | 0.99992 | 0.99999 | 1
|  | N-1 Load (A) | 177.4012 | 173.9038 | 173.9059 | 169.1135 | 169.0261
|  | N-1 Rating (A) | 349 | 349 | 349 | 349 | 349
|  | Contingency Utilisation (%) | 50.8313 | 49.8292 | 49.8298 | 48.4566 | 48.4315
|  | N-1 Hosting Capacity (A) | 171.5988 | 175.0962 | 175.0941 | 179.8865 | 179.9739
|  | N-1 Power Factor | 0.9998 | 0.99986 | 0.99992 | 0.99999 | 1
|  | N-1 Limiting section | 420-1(2) | 420-1(2) | 420-1(2) | 420-1(2) | 420-1(2)
|  | Contingency Scenario | F368 | F368 | F368 | F368 | F368
F421 | 421-1 | Load (A) | 38.8594 | 18.5596 | 24 | 48.3524 | 74.6065
|  | Rating (A) | 673 | 673 | 673 | 673 | 673
|  | Utilisation (%) | 5.7741 | 2.7577 | 3.5661 | 7.1846 | 11.0857
|  | Hosting Capacity (A) | 634.1406 | 654.4404 | 649 | 624.6476 | 598.3935
|  | Power Factor | 0.91256 | 0.49577 | 0.75139 | 0.95054 | 0.98304
|  | N-1 Load (A) | 66.7521 | 38.4235 | 69.5329 | 102.6336 | 135.3581
|  | N-1 Rating (A) | 721 | 721 | 721 | 721 | 721
|  | Contingency Utilisation (%) | 9.9186 | 5.7093 | 10.3318 | 15.2502 | 20.1126
|  | N-1 Hosting Capacity (A) | 654.2479 | 682.5765 | 651.4671 | 618.3664 | 585.6419
|  | N-1 Power Factor | 0.91256 | 0.49577 | 0.75139 | 0.95054 | 0.98304
|  | N-1 Limiting section | 421-1(1) | 421-1(1) | 421-1(1) | 421-1(1) | 421-1(1)
|  | Contingency Scenario | F486 | F389 | F389 | F389 | F389
F425 | 425-1 | Load (A) | 27.8463 | 44.1452 | 60.7063 | 77.1391 | 92.6676
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 5.0362 | 7.9844 | 10.9776 | 13.9532 | 16.762
|  | Hosting Capacity (A) | 525.1537 | 508.8548 | 492.2937 | 475.8609 | 460.3324
|  | Power Factor | 0.9997 | 0.99986 | 0.99907 | 0.99855 | 0.99774
|  | N-1 Load (A) | 76.9854 | 122.1683 | 167.9202 | 213.3124 | 256.1373
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 13.9214 | 22.0919 | 30.3653 | 38.5737 | 46.3178
|  | N-1 Hosting Capacity (A) | 476.0146 | 430.8317 | 385.0798 | 339.6876 | 296.8627
|  | N-1 Power Factor | 0.9997 | 0.99986 | 0.99907 | 0.99855 | 0.99774
|  | N-1 Limiting section | 425-1(1) | 425-1(1) | 425-1(12) | 425-1(1) | 425-1(1)
|  | Contingency Scenario | F3550 | F3550 | F3550 | F3550 | F3550
F426 | 426-1 | Load (A) | 8.0158 | 4.4087 | 2.5027 | 3.5972 | 5.2237
|  | Rating (A) | 740 | 740 | 740 | 740 | 740
|  | Utilisation (%) | 1.0832 | 0.59577 | 0.33821 | 0.48611 | 0.70591
|  | Hosting Capacity (A) | 731.9842 | 735.5913 | 737.4973 | 736.4028 | 734.7763
|  | Power Factor | 0.95008 | 0.82244 | 1 | 0.72482 | 0.88235
|  | N-1 Load (A) | 14.9555 | 8.1584 | 4.0128 | 6.4601 | 9.8351
|  | N-1 Rating (A) | 740 | 740 | 740 | 740 | 740
|  | Contingency Utilisation (%) | 2.0975 | 1.1025 | 0.54227 | 0.87298 | 1.3291
|  | N-1 Hosting Capacity (A) | 725.0445 | 731.8416 | 735.9872 | 733.5399 | 730.1649
|  | N-1 Power Factor | 0.99381 | 0.82244 | 1 | 0.72482 | 0.88235
|  | N-1 Limiting section | 426-1(7) | 426-1(2) | 426-1(2) | 426-1(2) | 426-1(2)
|  | Contingency Scenario | F427 | F427 | F427 | F427 | F427
F427 | 427-1 | Load (A) | 7.6579 | 4.1889 | 2.3416 | 3.4101 | 4.9807
|  | Rating (A) | 740 | 740 | 740 | 740 | 740
|  | Utilisation (%) | 1.0348 | 0.56606 | 0.31644 | 0.46082 | 0.67307
|  | Hosting Capacity (A) | 732.3421 | 735.8111 | 737.6584 | 736.5899 | 735.0193
|  | Power Factor | 0.95545 | 0.83441 | 1 | 0.72591 | 0.882
|  | N-1 Load (A) | 14.9744 | 7.3809 | 2.4485 | 5.7689 | 9.4612
|  | N-1 Rating (A) | 740 | 740 | 740 | 740 | 740
|  | Contingency Utilisation (%) | 2.0236 | 0.99742 | 0.33087 | 0.77957 | 1.2785
|  | N-1 Hosting Capacity (A) | 725.0256 | 732.6191 | 737.5515 | 734.2311 | 730.5388
|  | N-1 Power Factor | 0.95545 | 0.83441 | 1 | 0.72591 | 0.882
|  | N-1 Limiting section | 427-1(2) | 427-1(2) | 427-1(2) | 427-1(2) | 427-1(2)
|  | Contingency Scenario | F426 | F426 | F426 | F426 | F426
F428 | 428-1 | Load (A) | 14.9043 | 5.6891 | 9.4827 | 20.0291 | 30.4249
|  | Rating (A) | 351 | 351 | 351 | 351 | 351
|  | Utilisation (%) | 4.2462 | 1.6208 | 2.7016 | 5.7122 | 8.6681
|  | Hosting Capacity (A) | 336.0957 | 345.3109 | 341.5173 | 330.9709 | 320.5751
|  | Power Factor | 0.9727 | 0.54884 | 0.87532 | 0.97832 | 0.9928
F429 | 429-1 | Load (A) | 117.3813 | 104.1476 | 90.8354 | 78.6279 | 65.9917
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 21.2263 | 18.8332 | 16.4259 | 14.2184 | 11.9334
|  | Hosting Capacity (A) | 435.6187 | 448.8524 | 462.1646 | 474.3721 | 487.0083
|  | Power Factor | 0.97958 | 0.97871 | 0.97632 | 0.97245 | 0.96629
|  | N-1 Load (A) | 247.6903 | 240.1083 | 232.8043 | 226.8908 | 219.5097
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 44.7903 | 43.4192 | 42.0984 | 41.0291 | 39.6943
|  | N-1 Hosting Capacity (A) | 305.3097 | 312.8917 | 320.1957 | 326.1092 | 333.4903
|  | N-1 Power Factor | 0.97958 | 0.97871 | 0.97632 | 0.97245 | 0.96629
|  | N-1 Limiting section | 429-1(1) | 429-1(1) | 429-1(1) | 429-1(1) | 429-1(1)
|  | Contingency Scenario | F341 | F341 | F341 | F341 | F341
F429 | 429-2 | Load (A) | 13.1041 | 16.5551 | 20.0517 | 23.5329 | 26.8373
|  | Rating (A) | 461 | 461 | 461 | 461 | 461
|  | Utilisation (%) | 2.8425 | 3.5911 | 4.3496 | 5.1047 | 5.8215
|  | Hosting Capacity (A) | 447.8959 | 444.4449 | 440.9483 | 437.4671 | 434.1627
|  | Power Factor | 0.9999 | 0.99988 | 0.99986 | 0.99982 | 0.99978
|  | N-1 Load (A) | 13.3265 | 16.848 | 20.4265 | 23.9808 | 27.3626
|  | N-1 Rating (A) | 461 | 461 | 461 | 461 | 461
|  | Contingency Utilisation (%) | 2.8908 | 3.6547 | 4.4309 | 5.2019 | 5.9355
|  | N-1 Hosting Capacity (A) | 447.6735 | 444.152 | 440.5735 | 437.0192 | 433.6374
|  | N-1 Power Factor | 0.9999 | 0.99988 | 0.99986 | 0.99982 | 0.99978
|  | N-1 Limiting section | 429-2 | 429-2 | 429-2 | 429-2 | 429-2
|  | Contingency Scenario | F341 | F341 | F341 | F341 | F341
F429 | 429-3 | Load (A) | 130.4505 | 120.5935 | 110.6784 | 101.8183 | 92.3094
|  | Rating (A) | 410 | 410 | 410 | 410 | 410
|  | Utilisation (%) | 31.8172 | 29.4131 | 26.9947 | 24.8337 | 22.5145
|  | Hosting Capacity (A) | 279.5495 | 289.4065 | 299.3216 | 308.1817 | 317.6906
|  | Power Factor | 0.98916 | 0.98883 | 0.98788 | 0.98667 | 0.98511
|  | N-1 Load (A) | 261.0014 | 256.9081 | 253.1391 | 250.7501 | 246.7146
|  | N-1 Rating (A) | 463 | 463 | 463 | 463 | 463
|  | Contingency Utilisation (%) | 63.6589 | 62.6605 | 61.7412 | 61.1586 | 60.1743
|  | N-1 Hosting Capacity (A) | 201.9986 | 206.0919 | 209.8609 | 212.2499 | 216.2854
|  | N-1 Power Factor | 0.98916 | 0.98883 | 0.98788 | 0.98667 | 0.98511
|  | N-1 Limiting section | 429-3 | 429-3 | 429-3 | 429-3 | 429-3
|  | Contingency Scenario | F341 | F341 | F341 | F341 | F341
F431 | 431-1 | Load (A) | 51.4851 | 73.7864 | 96.4277 | 118.9464 | 140.2365
|  | Rating (A) | 396 | 396 | 396 | 396 | 396
|  | Utilisation (%) | 13.0013 | 18.6329 | 24.3504 | 30.037 | 35.4133
|  | Hosting Capacity (A) | 344.5149 | 322.2136 | 299.5723 | 277.0536 | 255.7635
|  | Power Factor | 1 | 0.99982 | 0.99946 | 0.99896 | 0.99837
|  | N-1 Load (A) | 102.7044 | 147.1838 | 192.3339 | 237.2412 | 279.6961
|  | N-1 Rating (A) | 443 | 443 | 443 | 443 | 443
|  | Contingency Utilisation (%) | 25.9355 | 37.1676 | 48.5692 | 59.9094 | 70.6303
|  | N-1 Hosting Capacity (A) | 340.2956 | 295.8162 | 250.6661 | 205.7588 | 163.3039
|  | N-1 Power Factor | 1 | 0.99982 | 0.99946 | 0.99896 | 0.99837
|  | N-1 Limiting section | 431-1(2) | 431-1(2) | 431-1(2) | 431-1(2) | 431-1(2)
|  | Contingency Scenario | F457 | F457 | F457 | F457 | F457
F432 | 432-1 | Load (A) | 13.6173 | 13.6173 | 13.6173 | 13.6173 | 13.6173
|  | Rating (A) | 476 | 476 | 476 | 476 | 476
|  | Utilisation (%) | 2.8608 | 2.8608 | 2.8608 | 2.8608 | 2.8608
|  | Hosting Capacity (A) | 462.3827 | 462.3827 | 462.3827 | 462.3827 | 462.3827
|  | Power Factor | 1 | 1 | 1 | 1 | 1
F433 | 433-1 | Load (A) | 2.354 | 2.354 | 2.354 | 2.354 | 2.354
|  | Rating (A) | 406 | 406 | 406 | 406 | 406
|  | Utilisation (%) | 0.5798 | 0.5798 | 0.5798 | 0.5798 | 0.5798
|  | Hosting Capacity (A) | 403.646 | 403.646 | 403.646 | 403.646 | 403.646
|  | Power Factor | 1 | 1 | 1 | 1 | 1
F434 | 434-1 | Load (A) | 1.6856 | 1.6859 | 1.6862 | 1.6865 | 1.6867
|  | Rating (A) | 406 | 406 | 406 | 406 | 406
|  | Utilisation (%) | 0.41517 | 0.41525 | 0.41532 | 0.41539 | 0.41545
|  | Hosting Capacity (A) | 404.3144 | 404.3141 | 404.3138 | 404.3135 | 404.3133
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 1.6865 | 1.6871 | 1.6878 | 1.6884 | 1.689
|  | N-1 Rating (A) | 406 | 406 | 406 | 406 | 406
|  | Contingency Utilisation (%) | 0.41538 | 0.41555 | 0.41571 | 0.41586 | 0.41601
|  | N-1 Hosting Capacity (A) | 404.3135 | 404.3129 | 404.3122 | 404.3116 | 404.311
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 434-1(1) | 434-1(1) | 434-1(1) | 434-1(1) | 434-1(1)
|  | Contingency Scenario | F690 | F690 | F690 | F690 | F690
F436 | 436-1 | Load (A) | 43.6834 | 54.6693 | 70.2108 | 77.438 | 80.112
|  | Rating (A) | 351 | 351 | 351 | 351 | 351
|  | Utilisation (%) | 12.4454 | 15.5753 | 20.0031 | 22.0621 | 22.8239
|  | Hosting Capacity (A) | 307.3166 | 296.3307 | 280.7892 | 273.562 | 270.888
|  | Power Factor | 0.98997 | 0.99021 | 0.98941 | 0.99022 | 0.99149
|  | N-1 Load (A) | 59.0455 | 73.4545 | 95.2079 | 103.3948 | 104.3482
|  | N-1 Rating (A) | 351 | 351 | 351 | 351 | 351
|  | Contingency Utilisation (%) | 16.8221 | 20.9272 | 27.1248 | 29.4572 | 29.7288
|  | N-1 Hosting Capacity (A) | 291.9545 | 277.5455 | 255.7921 | 247.6052 | 246.6518
|  | N-1 Power Factor | 0.98997 | 0.99021 | 0.98941 | 0.99022 | 0.99149
|  | N-1 Limiting section | 436-1(1) | 436-1(1) | 436-1(1) | 436-1(1) | 436-1(1)
|  | Contingency Scenario | F366 | F366 | F366 | F366 | F366
F436 | 436-4 | Load (A) | 43.7914 | 54.7736 | 70.3153 | 77.537 | 80.2038
|  | Rating (A) | 208 | 208 | 208 | 208 | 208
|  | Utilisation (%) | 21.0536 | 26.3335 | 33.8054 | 37.2774 | 38.5595
|  | Hosting Capacity (A) | 164.2086 | 153.2264 | 137.6847 | 130.463 | 127.7962
|  | Power Factor | 0.98879 | 0.98982 | 0.98977 | 0.99084 | 0.99215
|  | N-1 Load (A) | 59.167 | 73.57 | 95.3201 | 103.5015 | 104.4487
|  | N-1 Rating (A) | 208 | 208 | 208 | 208 | 208
|  | Contingency Utilisation (%) | 28.4457 | 35.3702 | 45.827 | 49.7603 | 50.2157
|  | N-1 Hosting Capacity (A) | 148.833 | 134.43 | 112.6799 | 104.4985 | 103.5513
|  | N-1 Power Factor | 0.98879 | 0.98982 | 0.98977 | 0.99084 | 0.99215
|  | N-1 Limiting section | 436-4 | 436-4 | 436-4 | 436-4 | 436-4
|  | Contingency Scenario | F366 | F366 | F366 | F366 | F366
F438 | 438-1 | Load (A) | 2.4387 | 2.4419 | 2.4449 | 2.448 | 2.4518
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 0.44099 | 0.44157 | 0.44212 | 0.44267 | 0.44337
|  | Hosting Capacity (A) | 550.5613 | 550.5581 | 550.5551 | 550.552 | 550.5482
|  | Power Factor | 0.99459 | 0.9946 | 0.99462 | 0.99463 | 0.99465
F443 | 443-1 | Load (A) | 17.0956 | 3.3777 | 12.3221 | 28.8258 | 45.714
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 3.0914 | 0.6108 | 2.2282 | 5.2126 | 8.2665
|  | Hosting Capacity (A) | 535.9044 | 549.6223 | 540.6779 | 524.1742 | 507.286
|  | Power Factor | 0.9967 | 0.91485 | 0.99634 | 0.99991 | 0.99988
|  | N-1 Load (A) | 41.1458 | 7.4683 | 29.6388 | 69.5688 | 110.3106
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 7.4405 | 1.3505 | 5.3596 | 12.5802 | 19.9477
|  | N-1 Hosting Capacity (A) | 511.8542 | 545.5317 | 523.3612 | 483.4312 | 442.6894
|  | N-1 Power Factor | 0.9967 | 0.91485 | 0.99634 | 0.99991 | 0.99988
|  | N-1 Limiting section | 443-1(1) | 443-1(1) | 443-1(1) | 443-1(1) | 443-1(1)
|  | Contingency Scenario | F3426 | F3426 | F3426 | F3426 | F3426
F445 | 445-1 | Load (A) | 47.6803 | 68.5113 | 89.2634 | 109.3327 | 127.721
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 8.6221 | 12.389 | 16.1417 | 19.7708 | 23.096
|  | Hosting Capacity (A) | 505.3197 | 484.4887 | 463.7366 | 443.6673 | 425.279
|  | Power Factor | 0.99757 | 0.9994 | 0.99992 | 0.99997 | 0.99977
|  | N-1 Load (A) | 82.4875 | 118.5742 | 154.434 | 189.0594 | 220.751
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 14.9164 | 21.442 | 27.9266 | 34.188 | 39.9188
|  | N-1 Hosting Capacity (A) | 470.5125 | 434.4258 | 398.566 | 363.9406 | 332.249
|  | N-1 Power Factor | 0.99757 | 0.9994 | 0.99992 | 0.99997 | 0.99977
|  | N-1 Limiting section | 445-1(5) | 445-1(5) | 445-1(5) | 445-1(5) | 445-1(5)
|  | Contingency Scenario | F357 | F357 | F357 | F357 | F357
F446 | 446-12 | Load (A) | 98.9282 | 101.3556 | 103.9916 | 106.7957 | 109.6195
|  | Rating (A) | 731 | 731 | 731 | 731 | 731
|  | Utilisation (%) | 13.5342 | 13.8662 | 14.2268 | 14.6103 | 14.9965
|  | Hosting Capacity (A) | 632.0718 | 629.6444 | 627.0084 | 624.2043 | 621.3805
|  | Power Factor | 0.99843 | 0.99856 | 0.99871 | 0.99888 | 0.99904
|  | N-1 Load (A) | 178.4561 | 178.4348 | 178.3986 | 178.3619 | 178.3269
|  | N-1 Rating (A) | 731 | 731 | 731 | 731 | 731
|  | Contingency Utilisation (%) | 24.4126 | 24.4097 | 24.4047 | 24.3997 | 24.3949
|  | N-1 Hosting Capacity (A) | 552.5439 | 552.5652 | 552.6014 | 552.6381 | 552.6731
|  | N-1 Power Factor | 0.99843 | 0.99856 | 0.99871 | 0.99888 | 0.99904
|  | N-1 Limiting section | 446-12(11) | 446-12(11) | 446-12(11) | 446-12(11) | 446-12(11)
|  | Contingency Scenario | F446C | F446C | F446C | F446C | F446C
F446C | 446-11 | Load (A) | 79.0114 | 76.5551 | 73.888 | 71.052 | 68.1985
|  | Rating (A) | 468 | 468 | 468 | 468 | 468
|  | Utilisation (%) | 16.8835 | 16.3581 | 15.788 | 15.182 | 14.5723
|  | Hosting Capacity (A) | 388.9886 | 391.4449 | 394.112 | 396.948 | 399.8015
|  | Power Factor | 0.99988 | 0.99986 | 0.99981 | 0.99974 | 0.99963
|  | N-1 Load (A) | 178.9773 | 178.9773 | 178.9773 | 178.9773 | 178.9773
|  | N-1 Rating (A) | 468 | 468 | 468 | 468 | 468
|  | Contingency Utilisation (%) | 38.243 | 38.243 | 38.243 | 38.243 | 38.243
|  | N-1 Hosting Capacity (A) | 289.0227 | 289.0227 | 289.0227 | 289.0227 | 289.0227
|  | N-1 Power Factor | 0.99988 | 0.99986 | 0.99981 | 0.99974 | 0.99963
|  | N-1 Limiting section | 446-11(19) | 446-11(19) | 446-11(19) | 446-11(19) | 446-11(19)
|  | Contingency Scenario | F446 | F446 | F446 | F446 | F446
F446E | 446E-1 | Load (A) | 178.0059 | 177.9766 | 177.9638 | 177.942 | 177.9213
|  | Rating (A) | 787 | 787 | 787 | 787 | 787
|  | Utilisation (%) | 22.6172 | 22.6146 | 22.6118 | 22.6091 | 22.6064
|  | Hosting Capacity (A) | 608.9941 | 609.0234 | 609.0362 | 609.058 | 609.0787
|  | Power Factor | 0.9989 | 0.9989 | 0.9989 | 0.9989 | 0.9989
|  | Power Factor | 0.9989 | 0.99894 | 0.9989 | 0.9989 | 0.9989
|  | N-1 Load (A) | 179.0751 | 179.0751 | 179.0751 | 179.0751 | 179.0751
|  | N-1 Rating (A) | 787 | 787 | 787 | 787 | 787
|  | Contingency Utilisation (%) | 22.7541 | 22.7541 | 22.7541 | 22.7541 | 22.7541
|  | N-1 Hosting Capacity (A) | 607.9249 | 607.9249 | 607.9249 | 607.9249 | 607.9249
|  | N-1 Power Factor | 0.99894 | 0.99894 | 0.99894 | 0.99894 | 0.99894
|  | N-1 Limiting section | 446E-1(1) | 446E-1(1) | 446E-1(1) | 446E-1(1) | 446E-1(1)
|  | Contingency Scenario | F446 | F446 | F446 | F446 | F446
F448 | 448-1 | Load (A) | 110.3015 | 162.3708 | 215.7991 | 266.3887 | 310.4
|  | Rating (A) | 776 | 776 | 776 | 776 | 776
|  | Utilisation (%) | 14.2141 | 20.9241 | 27.8092 | 34.3284 | 40
|  | Hosting Capacity (A) | 665.6985 | 613.6292 | 560.2009 | 509.6113 | 465.6
|  | Power Factor | 0.99982 | 0.99936 | 0.99864 | 0.99765 | 0.99666
|  | N-1 Load (A) | 128.1509 | 192.3637 | 258.1499 | 320.8062 | 375.8771
|  | N-1 Rating (A) | 776 | 776 | 776 | 776 | 776
|  | Contingency Utilisation (%) | 16.5143 | 24.7891 | 33.2667 | 41.341 | 48.4378
|  | N-1 Hosting Capacity (A) | 647.8491 | 583.6363 | 517.8501 | 455.1938 | 400.1229
|  | N-1 Power Factor | 0.99982 | 0.99936 | 0.99864 | 0.99765 | 0.99666
|  | N-1 Limiting section | 448-1(1) | 448-1(1) | 448-1(1) | 448-1(1) | 448-1(1)
|  | Contingency Scenario | F322 | F322 | F322 | F322 | F322
F448 | 448-2 | Load (A) | 91.2161 | 140.3837 | 191.2371 | 238.8842 | 279.4194
|  | Rating (A) | 698 | 698 | 698 | 698 | 698
|  | Utilisation (%) | 13.0682 | 20.1123 | 27.3979 | 34.2241 | 40.0314
|  | Hosting Capacity (A) | 606.7839 | 557.6163 | 506.7629 | 459.1158 | 418.5806
|  | Power Factor | 0.99982 | 0.99948 | 0.99898 | 0.99829 | 0.99764
|  | N-1 Load (A) | 91.2213 | 140.3948 | 191.2561 | 238.9122 | 279.4565
|  | N-1 Rating (A) | 698 | 698 | 698 | 698 | 698
|  | Contingency Utilisation (%) | 13.0689 | 20.1139 | 27.4006 | 34.2281 | 40.0367
|  | N-1 Hosting Capacity (A) | 606.7787 | 557.6052 | 506.7439 | 459.0878 | 418.5435
|  | N-1 Power Factor | 0.99982 | 0.99948 | 0.99898 | 0.99829 | 0.99764
|  | N-1 Limiting section | 448-2(1) | 448-2(1) | 448-2(1) | 448-2(1) | 448-2(1)
|  | Contingency Scenario | F323 | F323 | F323 | F323 | F323
F448 | 448-3 | Load (A) | 19.1108 | 22.0268 | 24.6286 | 27.6152 | 31.1343
|  | Rating (A) | 485 | 485 | 485 | 485 | 485
|  | Utilisation (%) | 3.9404 | 4.5416 | 5.0781 | 5.6939 | 6.4194
|  | Hosting Capacity (A) | 465.8892 | 462.9732 | 460.3714 | 457.3848 | 453.8657
|  | Power Factor | 0.99919 | 0.99946 | 0.99968 | 0.99983 | 0.99984
|  | N-1 Load (A) | 36.9696 | 52.0659 | 67.0599 | 82.1618 | 96.7734
|  | N-1 Rating (A) | 485 | 485 | 485 | 485 | 485
|  | Contingency Utilisation (%) | 7.6226 | 10.7352 | 13.8268 | 16.9406 | 19.9533
|  | N-1 Hosting Capacity (A) | 448.0304 | 432.9341 | 417.9401 | 402.8382 | 388.2266
|  | N-1 Power Factor | 0.99919 | 0.99946 | 0.99968 | 0.99983 | 0.99984
|  | N-1 Limiting section | 448-3(2) | 448-3(2) | 448-3(2) | 448-3(2) | 448-3(2)
|  | Contingency Scenario | F322 | F322 | F322 | F322 | F322
F449 | 449-1 | Load (A) | 150.9694 | 150.9694 | 150.9694 | 150.9694 | 150.9694
|  | Rating (A) | 440 | 440 | 440 | 440 | 440
|  | Utilisation (%) | 34.3126 | 34.3126 | 34.3126 | 34.3126 | 34.3126
|  | Hosting Capacity (A) | 289.0306 | 289.0306 | 289.0306 | 289.0306 | 289.0306
|  | Power Factor | 0.99728 | 0.99728 | 0.99728 | 0.99728 | 0.99728
F451 | 451-1 | Load (A) | 23.9058 | 24.1338 | 25.0408 | 26.0397 | 26.9344
|  | Rating (A) | 422 | 422 | 422 | 422 | 422
|  | Utilisation (%) | 5.6649 | 5.7189 | 5.9338 | 6.1705 | 6.3826
|  | Hosting Capacity (A) | 398.0942 | 397.8662 | 396.9592 | 395.9603 | 395.0656
|  | Power Factor | 0.9998 | 0.99984 | 0.99989 | 0.99993 | 0.99995
|  | N-1 Load (A) | 80.4285 | 111.5715 | 141.7378 | 170.4879 | 196.6934
|  | N-1 Rating (A) | 422 | 422 | 422 | 422 | 422
|  | Contingency Utilisation (%) | 19.0589 | 26.4387 | 33.5872 | 40.4 | 46.6098
|  | N-1 Hosting Capacity (A) | 341.5715 | 310.4285 | 280.2622 | 251.5121 | 225.3066
|  | N-1 Power Factor | 0.9998 | 0.99984 | 0.99989 | 0.99993 | 0.99995
|  | N-1 Limiting section | 451-1(5) | 451-1(5) | 451-1(5) | 451-1(5) | 451-1(5)
|  | Contingency Scenario | F3250 | F3250 | F3250 | F3250 | F3250
F452 | 452-1 | Load (A) | 7.2727 | 27.1767 | 48.2916 | 70.1789 | 91.6158
|  | Rating (A) | 510 | 510 | 510 | 510 | 510
|  | Utilisation (%) | 1.4292 | 5.329 | 9.4689 | 13.7606 | 17.9639
|  | Hosting Capacity (A) | 502.7273 | 482.8233 | 461.7084 | 439.8211 | 418.3842
|  | Power Factor | 0.99462 | 0.99998 | 0.99984 | 0.99937 | 0.99876
|  | N-1 Load (A) | 16.1289 | 60.6109 | 107.6811 | 156.4229 | 204.1244
|  | N-1 Rating (A) | 510 | 510 | 510 | 510 | 510
|  | Contingency Utilisation (%) | 3.1625 | 11.8845 | 21.1139 | 30.6712 | 40.0244
|  | N-1 Hosting Capacity (A) | 493.8711 | 449.3891 | 402.3189 | 353.5771 | 305.8756
|  | N-1 Power Factor | 0.99462 | 0.99998 | 0.99984 | 0.99937 | 0.99876
|  | N-1 Limiting section | 452-1 | 452-1 | 452-1 | 452-1 | 452-1
|  | Contingency Scenario | F408 | F408 | F408 | F408 | F408
F453 | 453-1 | Load (A) | 48.6554 | 116.5616 | 188.1497 | 260.5547 | 328.6834
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 5.9481 | 14.2496 | 23.0012 | 31.8527 | 40.1814
|  | Hosting Capacity (A) | 769.3446 | 701.4384 | 629.8503 | 557.4453 | 489.3166
|  | Power Factor | 0.99877 | 0.99999 | 0.99975 | 0.99918 | 0.99844
F454 | 454-1 | Load (A) | 20.058 | 14.0985 | 8.1659 | 2.7296 | 3.7366
|  | Rating (A) | 430 | 430 | 430 | 430 | 430
|  | Utilisation (%) | 4.6646 | 3.2787 | 1.899 | 0.6348 | 0.86897
|  | Hosting Capacity (A) | 409.942 | 415.9015 | 421.8341 | 427.2704 | 426.2634
|  | Power Factor | 0.9971 | 0.9932 | 0.97766 | 0.76748 | 0.88404
|  | N-1 Load (A) | 40.1722 | 28.1456 | 16.1048 | 4.5366 | 6.8411
|  | N-1 Rating (A) | 460 | 460 | 460 | 460 | 460
|  | Contingency Utilisation (%) | 9.3424 | 6.5455 | 3.7453 | 1.055 | 1.5909
|  | N-1 Hosting Capacity (A) | 419.8278 | 431.8544 | 443.8952 | 455.4634 | 453.1589
|  | N-1 Power Factor | 0.99972 | 0.9932 | 0.97766 | 0.76748 | 0.88404
|  | N-1 Limiting section | 454-1(2) | 454-1(4) | 454-1(4) | 454-1(4) | 454-1(4)
|  | Contingency Scenario | F455 | F455 | F455 | F455 | F455
F455 | 455-1 | Load (A) | 20.1885 | 14.1919 | 8.2236 | 2.7633 | 3.7721
|  | Rating (A) | 430 | 430 | 430 | 430 | 430
|  | Utilisation (%) | 4.695 | 3.3004 | 1.9125 | 0.64263 | 0.87723
|  | Hosting Capacity (A) | 409.8115 | 415.8081 | 421.7764 | 427.2367 | 426.2279
|  | Power Factor | 0.99699 | 0.99297 | 0.977 | 0.76292 | 0.88137
|  | N-1 Load (A) | 40.1729 | 28.1473 | 16.1083 | 4.5497 | 6.8497
|  | N-1 Rating (A) | 460 | 460 | 460 | 460 | 460
|  | Contingency Utilisation (%) | 9.3425 | 6.5459 | 3.7461 | 1.0581 | 1.593
|  | N-1 Hosting Capacity (A) | 419.8271 | 431.8527 | 443.8917 | 455.4503 | 453.1503
|  | N-1 Power Factor | 0.99972 | 0.99297 | 0.977 | 0.76292 | 0.88137
|  | N-1 Limiting section | 455-1(2) | 455-1(4) | 455-1(4) | 455-1(4) | 455-1(4)
|  | Contingency Scenario | F454 | F454 | F454 | F454 | F454
F456 | 456-1 | Load (A) | 17.9341 | 5.7681 | 5.9467 | 14.7869 | 21.1216
|  | Rating (A) | 899 | 899 | 899 | 899 | 899
|  | Utilisation (%) | 1.9949 | 0.64162 | 0.66148 | 1.6448 | 2.3495
|  | Hosting Capacity (A) | 881.0659 | 893.2319 | 893.0533 | 884.2131 | 877.8784
|  | Power Factor | 0.98767 | 0.94196 | 0.99307 | 0.99949 | 0.998
|  | N-1 Load (A) | 36.339 | 31.3512 | 42.8987 | 60.2912 | 72.3138
|  | N-1 Rating (A) | 899 | 899 | 899 | 899 | 899
|  | Contingency Utilisation (%) | 4.0422 | 3.4873 | 4.7718 | 6.7065 | 8.0438
|  | N-1 Hosting Capacity (A) | 862.661 | 867.6488 | 856.1013 | 838.7088 | 826.6862
|  | N-1 Power Factor | 0.98767 | 0.94196 | 0.99307 | 0.99949 | 0.998
|  | N-1 Limiting section | 456-1 | 456-1 | 456-1 | 456-1 | 456-1
|  | Contingency Scenario | F3803 | F3880 | F3881 | F3881 | F3881
F456 | 456-2 | Load (A) | 18.0629 | 6.0532 | 6.0764 | 14.7852 | 21.1182
|  | Rating (A) | 441 | 441 | 441 | 441 | 441
|  | Utilisation (%) | 4.0959 | 1.3726 | 1.3779 | 3.3527 | 4.7887
|  | Hosting Capacity (A) | 422.9371 | 434.9468 | 434.9236 | 426.2148 | 419.8818
|  | Power Factor | 0.98067 | 0.89763 | 0.97188 | 0.99959 | 0.99814
|  | N-1 Load (A) | 36.4648 | 31.3469 | 42.8886 | 60.2792 | 72.3006
|  | N-1 Rating (A) | 441 | 441 | 441 | 441 | 441
|  | Contingency Utilisation (%) | 8.2687 | 7.1081 | 9.7253 | 13.6687 | 16.3947
|  | N-1 Hosting Capacity (A) | 404.5352 | 409.6531 | 398.1114 | 380.7208 | 368.6994
|  | N-1 Power Factor | 0.98067 | 0.89763 | 0.97188 | 0.99959 | 0.99814
|  | N-1 Limiting section | 456-2(3) | 456-2(3) | 456-2(3) | 456-2(3) | 456-2(3)
|  | Contingency Scenario | F3803 | F3880 | F3881 | F3881 | F3881
F456 | 456-3 | Load (A) | 17.876 | 5.6467 | 5.9175 | 14.8602 | 21.2168
|  | Rating (A) | 441 | 441 | 441 | 441 | 441
|  | Utilisation (%) | 4.0535 | 1.2804 | 1.3418 | 3.3697 | 4.8111
|  | Hosting Capacity (A) | 423.124 | 435.3533 | 435.0825 | 426.1398 | 419.7832
|  | Power Factor | 0.99085 | 0.9622 | 0.99796 | 0.99457 | 0.99354
|  | N-1 Load (A) | 36.2763 | 31.4539 | 43.1115 | 60.5384 | 72.5815
|  | N-1 Rating (A) | 441 | 441 | 441 | 441 | 441
|  | Contingency Utilisation (%) | 8.2259 | 7.1324 | 9.7759 | 13.7275 | 16.4584
|  | N-1 Hosting Capacity (A) | 404.7237 | 409.5461 | 397.8885 | 380.4616 | 368.4185
|  | N-1 Power Factor | 0.99085 | 0.9622 | 0.99796 | 0.99457 | 0.99354
|  | N-1 Limiting section | 456-3(4) | 456-3(4) | 456-3(4) | 456-3(4) | 456-3(4)
|  | Contingency Scenario | F3803 | F3880 | F3881 | F3881 | F3881
F457 | 457-1 | Load (A) | 51.2035 | 73.3863 | 95.9068 | 118.3053 | 139.4817
|  | Rating (A) | 402 | 402 | 402 | 402 | 402
|  | Utilisation (%) | 12.7372 | 18.2553 | 23.8574 | 29.4292 | 34.6969
|  | Hosting Capacity (A) | 350.7965 | 328.6137 | 306.0932 | 283.6947 | 262.5183
|  | Power Factor | 0.99979 | 0.99935 | 0.99879 | 0.99811 | 0.99735
|  | N-1 Load (A) | 102.7636 | 147.2751 | 192.4547 | 237.39 | 279.8704
|  | N-1 Rating (A) | 512 | 512 | 512 | 512 | 512
|  | Contingency Utilisation (%) | 25.5631 | 36.6356 | 47.8743 | 59.0522 | 69.6195
|  | N-1 Hosting Capacity (A) | 409.2364 | 364.7249 | 319.5453 | 274.61 | 232.1296
|  | N-1 Power Factor | 0.99979 | 0.99935 | 0.99879 | 0.99811 | 0.99735
|  | N-1 Limiting section | 457-1 | 457-1 | 457-1 | 457-1 | 457-1
|  | Contingency Scenario | F431 | F431 | F431 | F431 | F431
F458 | 458-1 | Load (A) | 30.0595 | 21.0448 | 11.5453 | 2.9741 | 9.2052
|  | Rating (A) | 780 | 780 | 780 | 800 | 780
|  | Utilisation (%) | 3.8538 | 2.6981 | 1.4802 | 0.37176 | 1.1802
|  | Hosting Capacity (A) | 749.9405 | 758.9552 | 768.4547 | 797.0259 | 770.7948
|  | Power Factor | 0.99382 | 0.9879 | 0.96524 | 0.35692 | 0.97686
|  | N-1 Load (A) | 95.4572 | 76.8224 | 56.64 | 35.2051 | 27.8813
|  | N-1 Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Contingency Utilisation (%) | 12.2381 | 9.849 | 7.2615 | 4.5135 | 3.5745
|  | N-1 Hosting Capacity (A) | 684.5428 | 703.1776 | 723.36 | 744.7949 | 752.1187
|  | N-1 Power Factor | 0.99382 | 0.9879 | 0.96524 | 0.38005 | 0.97686
|  | N-1 Limiting section | 458-1(1) | 458-1(1) | 458-1(1) | 458-1(1) | 458-1(1)
|  | Contingency Scenario | F389 | F389 | F389 | F389 | F474A
F459A | 459A | Load (A) | 20.8247 | 19.1059 | 17.3465 | 15.5855 | 13.9287
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 3.7658 | 3.4549 | 3.1368 | 2.8184 | 2.5188
|  | Hosting Capacity (A) | 532.1753 | 533.8941 | 535.6535 | 537.4145 | 539.0713
|  | Power Factor | 0.96183 | 0.96002 | 0.95765 | 0.95452 | 0.95058
|  | N-1 Load (A) | 117.791 | 107.7633 | 97.4979 | 87.2178 | 77.5371
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 21.3004 | 19.487 | 17.6307 | 15.7718 | 14.0212
|  | N-1 Hosting Capacity (A) | 435.209 | 445.2367 | 455.5021 | 465.7822 | 475.4629
|  | N-1 Power Factor | 0.97195 | 0.96002 | 0.9704 | 0.96917 | 0.96756
|  | N-1 Limiting section | 459A(1) | 459A(6) | 459A(1) | 459A(1) | 459A(1)
|  | Contingency Scenario | F3440 | F3440 | F3440 | F3440 | F3440
F459B | 459B | Load (A) | 20.855 | 19.3528 | 17.8517 | 16.3963 | 15.0824
|  | Rating (A) | 801 | 801 | 801 | 801 | 801
|  | Utilisation (%) | 2.6036 | 2.4161 | 2.2287 | 2.047 | 1.8829
|  | Hosting Capacity (A) | 780.145 | 781.6472 | 783.1483 | 784.6037 | 785.9176
|  | Power Factor | 0.96012 | 0.9475 | 0.93031 | 0.90712 | 0.8777
|  | N-1 Load (A) | 117.8879 | 107.9314 | 97.7476 | 87.5612 | 77.9839
|  | N-1 Rating (A) | 801 | 801 | 801 | 801 | 801
|  | Contingency Utilisation (%) | 14.7176 | 13.4746 | 12.2032 | 10.9315 | 9.7358
|  | N-1 Hosting Capacity (A) | 683.1121 | 693.0686 | 703.2524 | 713.4388 | 723.0161
|  | N-1 Power Factor | 0.96012 | 0.9475 | 0.93031 | 0.90712 | 0.8777
|  | N-1 Limiting section | 459B | 459B | 459B | 459B | 459B
|  | Contingency Scenario | F3440 | F3440 | F3440 | F3440 | F3440
F460 | 460 | Load (A) | 24.8091 | 19.6456 | 40.8176 | 68.0358 | 94.4821
|  | Rating (A) | 762 | 762 | 762 | 762 | 762
|  | Utilisation (%) | 3.2558 | 2.5782 | 5.3566 | 8.9286 | 12.3992
|  | Hosting Capacity (A) | 737.1909 | 742.3544 | 721.1824 | 693.9642 | 667.5179
|  | Power Factor | 0.70101 | 0.44274 | 0.90874 | 0.97249 | 0.98876
|  | N-1 Load (A) | 34.2353 | 26.6523 | 57.5714 | 96.6163 | 134.4056
|  | N-1 Rating (A) | 762 | 762 | 762 | 762 | 762
|  | Contingency Utilisation (%) | 4.4928 | 3.4977 | 7.5553 | 12.6793 | 17.6385
|  | N-1 Hosting Capacity (A) | 727.7647 | 735.3477 | 704.4286 | 665.3837 | 627.5944
|  | N-1 Power Factor | 0.70101 | 0.44274 | 0.90874 | 0.97249 | 0.98876
|  | N-1 Limiting section | 460 | 460 | 460 | 460 | 460
|  | Contingency Scenario | F554 | F554 | F554 | F554 | F554
F460 | 460-1 | Load (A) | 27.8437 | 23.3479 | 42.6675 | 69.0909 | 95.1704
|  | Rating (A) | 762 | 762 | 762 | 762 | 762
|  | Utilisation (%) | 3.654 | 3.064 | 5.5994 | 9.0671 | 12.4895
|  | Hosting Capacity (A) | 734.1563 | 738.6521 | 719.3325 | 692.9091 | 666.8296
|  | Power Factor | 0.62479 | 0.37258 | 0.86952 | 0.95783 | 0.98179
|  | N-1 Load (A) | 37.1243 | 30.3123 | 59.3259 | 97.6179 | 135.0638
|  | N-1 Rating (A) | 763 | 763 | 763 | 763 | 763
|  | Contingency Utilisation (%) | 4.872 | 3.978 | 7.7856 | 12.8108 | 17.7249
|  | N-1 Hosting Capacity (A) | 725.8757 | 732.6877 | 703.6741 | 665.3821 | 627.9362
|  | N-1 Power Factor | 0.62479 | 0.37258 | 0.86952 | 0.95783 | 0.98179
|  | N-1 Limiting section | 460-1 | 460-1 | 460-1 | 460-1 | 460-1
|  | Contingency Scenario | F554 | F554 | F554 | F554 | F554
F461 | 461-1 | Load (A) | 25.1446 | 70.747 | 118.9554 | 165.9434 | 207.8446
|  | Rating (A) | 676 | 676 | 676 | 676 | 676
|  | Utilisation (%) | 3.7196 | 10.4655 | 17.5969 | 24.5479 | 30.7462
|  | Hosting Capacity (A) | 650.8554 | 605.253 | 557.0446 | 510.0566 | 468.1554
|  | Power Factor | 0.93711 | 0.9948 | 0.9989 | 0.99835 | 0.99775
|  | N-1 Load (A) | 43.2733 | 127.1698 | 214.6981 | 299.4283 | 374.9671
|  | N-1 Rating (A) | 758 | 758 | 758 | 758 | 758
|  | Contingency Utilisation (%) | 6.4014 | 18.8121 | 31.7601 | 44.2941 | 55.4685
|  | N-1 Hosting Capacity (A) | 714.7267 | 630.8302 | 543.3019 | 458.5717 | 383.0329
|  | N-1 Power Factor | 0.93711 | 0.9948 | 0.9989 | 0.99835 | 0.99775
|  | N-1 Limiting section | 461-1 | 461-1 | 461-1 | 461-1 | 461-1
|  | Contingency Scenario | F499 | F499 | F499 | F499 | F499
F464 | 464-1 | Load (A) | 47.9957 | 64.3828 | 80.6662 | 96.5127 | 111.2139
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 8.6791 | 11.6425 | 14.587 | 17.4526 | 20.111
|  | Hosting Capacity (A) | 505.0043 | 488.6172 | 472.3338 | 456.4873 | 441.7861
|  | Power Factor | 0.99998 | 0.99984 | 0.99942 | 0.99883 | 0.99813
|  | N-1 Load (A) | 85.7507 | 112.3215 | 138.5872 | 163.931 | 187.2016
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 15.5065 | 20.3113 | 25.061 | 29.6439 | 33.852
|  | N-1 Hosting Capacity (A) | 467.2493 | 440.6785 | 414.4128 | 389.069 | 365.7984
|  | N-1 Power Factor | 0.99998 | 0.99984 | 0.99942 | 0.99883 | 0.99813
|  | N-1 Limiting section | 464-1(2) | 464-1(2) | 464-1(2) | 464-1(2) | 464-1(2)
|  | Contingency Scenario | F309 | F309 | F309 | F309 | F309
F465 | 465-1 | Load (A) | 66.1845 | 90.4118 | 114.5906 | 138.2985 | 160.4333
|  | Rating (A) | 508 | 508 | 508 | 508 | 508
|  | Utilisation (%) | 13.0284 | 17.7976 | 22.5572 | 27.2241 | 31.5814
|  | Hosting Capacity (A) | 441.8155 | 417.5882 | 393.4094 | 369.7015 | 347.5667
|  | Power Factor | 0.99979 | 0.9997 | 0.99957 | 0.99939 | 0.99918
|  | N-1 Load (A) | 89.9737 | 126.5821 | 163.7711 | 200.2934 | 234.4194
|  | N-1 Rating (A) | 508 | 508 | 508 | 508 | 508
|  | Contingency Utilisation (%) | 17.7114 | 24.9177 | 32.2384 | 39.4278 | 46.1455
|  | N-1 Hosting Capacity (A) | 418.0263 | 381.4179 | 344.2289 | 307.7066 | 273.5806
|  | N-1 Power Factor | 0.99979 | 0.9997 | 0.99957 | 0.99939 | 0.99918
|  | N-1 Limiting section | 465-1 | 465-1 | 465-1 | 465-1 | 465-1
|  | Contingency Scenario | F3580 | F375 | F375 | F375 | F375
F466 | 466-1 | Load (A) | 24.6465 | 20.643 | 16.448 | 12.182 | 8.1312
|  | Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Utilisation (%) | 6.1158 | 5.1223 | 4.0814 | 3.0228 | 2.0177
|  | Hosting Capacity (A) | 378.3535 | 382.357 | 386.552 | 390.818 | 394.8688
|  | Power Factor | 0.99818 | 0.99831 | 0.99845 | 0.99861 | 0.99881
|  | N-1 Load (A) | 41.1776 | 34.482 | 27.4683 | 20.3377 | 13.5686
|  | N-1 Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Contingency Utilisation (%) | 10.2178 | 8.5563 | 6.816 | 5.0466 | 3.3669
|  | N-1 Hosting Capacity (A) | 361.8224 | 368.518 | 375.5317 | 382.6623 | 389.4314
|  | N-1 Power Factor | 0.99818 | 0.99831 | 0.99845 | 0.99861 | 0.99881
|  | N-1 Limiting section | 466-1(2) | 466-1(2) | 466-1(2) | 466-1(2) | 466-1(2)
|  | Contingency Scenario | F467 | F467 | F467 | F467 | F467
F467 | 467-1 | Load (A) | 16.624 | 13.9309 | 11.11 | 8.243 | 5.5252
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 3.0061 | 2.5192 | 2.009 | 1.4906 | 0.99912
|  | Hosting Capacity (A) | 536.376 | 539.0691 | 541.89 | 544.757 | 547.4748
|  | Power Factor | 0.99528 | 0.99442 | 0.99307 | 0.99062 | 0.98532
|  | N-1 Load (A) | 41.263 | 34.5417 | 27.5077 | 20.363 | 13.5878
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 7.4617 | 6.2462 | 4.9743 | 3.6823 | 2.4571
|  | N-1 Hosting Capacity (A) | 511.737 | 518.4583 | 525.4923 | 532.637 | 539.4122
|  | N-1 Power Factor | 0.99528 | 0.99442 | 0.99307 | 0.99062 | 0.98532
|  | N-1 Limiting section | 467-1(1) | 467-1(1) | 467-1(1) | 467-1(1) | 467-1(1)
|  | Contingency Scenario | F466 | F466 | F466 | F466 | F466
F468 | 468-1 | Load (A) | 18.4048 | 38.9026 | 60.4482 | 82.5454 | 103.9087
|  | Rating (A) | 579 | 579 | 579 | 579 | 579
|  | Utilisation (%) | 3.1787 | 6.7189 | 10.4401 | 14.2566 | 17.9462
|  | Hosting Capacity (A) | 560.5952 | 540.0974 | 518.5518 | 496.4546 | 475.0913
|  | Power Factor | 0.99086 | 0.99734 | 0.99902 | 0.99971 | 0.99997
|  | N-1 Load (A) | 28.6721 | 56.7978 | 86.008 | 115.6755 | 144.1286
|  | N-1 Rating (A) | 579 | 579 | 579 | 579 | 579
|  | Contingency Utilisation (%) | 4.952 | 9.8096 | 14.8546 | 19.9785 | 24.8927
|  | N-1 Hosting Capacity (A) | 550.3279 | 522.2022 | 492.992 | 463.3245 | 434.8714
|  | N-1 Power Factor | 0.99086 | 0.99734 | 0.99902 | 0.99971 | 0.99997
|  | N-1 Limiting section | 468-1(2) | 468-1(2) | 468-1(2) | 468-1(2) | 468-1(2)
|  | Contingency Scenario | F402 | F402 | F402 | F402 | F402
F469 | 469-1 | Load (A) | 19.1416 | 40.2772 | 62.4851 | 85.2526 | 107.2582
|  | Rating (A) | 537 | 537 | 537 | 537 | 537
|  | Utilisation (%) | 3.5645 | 7.5004 | 11.6359 | 15.8757 | 19.9736
|  | Hosting Capacity (A) | 517.8584 | 496.7228 | 474.5149 | 451.7474 | 429.7418
|  | Power Factor | 0.99947 | 0.99946 | 0.99813 | 0.99657 | 0.99496
|  | N-1 Load (A) | 37.4593 | 78.9497 | 122.496 | 167.0925 | 210.1524
|  | N-1 Rating (A) | 537 | 537 | 537 | 537 | 537
|  | Contingency Utilisation (%) | 6.9757 | 14.702 | 22.8112 | 31.1159 | 39.1345
|  | N-1 Hosting Capacity (A) | 499.5407 | 458.0503 | 414.504 | 369.9075 | 326.8476
|  | N-1 Power Factor | 0.99947 | 0.99946 | 0.99813 | 0.99657 | 0.99496
|  | N-1 Limiting section | 469-1 | 469-1 | 469-1 | 469-1 | 469-1
|  | Contingency Scenario | F468 | F468 | F468 | F468 | F468
F469 | 469-2 | Load (A) | 4.103 | 1.9167 | 7.5964 | 14.2219 | 20.9609
|  | Rating (A) | 579 | 579 | 579 | 579 | 579
|  | Utilisation (%) | 0.70864 | 0.33104 | 1.312 | 2.4563 | 3.6202
|  | Hosting Capacity (A) | 574.897 | 577.0833 | 571.4036 | 564.7781 | 558.0391
|  | Power Factor | 0.98812 | 0.61893 | 0.94539 | 0.96866 | 0.97484
|  | N-1 Load (A) | 14.3922 | 39.9403 | 67.4183 | 96.0321 | 123.9654
|  | N-1 Rating (A) | 579 | 579 | 579 | 579 | 579
|  | Contingency Utilisation (%) | 2.4857 | 6.8981 | 11.6439 | 16.5859 | 21.4103
|  | N-1 Hosting Capacity (A) | 564.6078 | 539.0597 | 511.5817 | 482.9679 | 455.0346
|  | N-1 Power Factor | 0.98812 | 0.61893 | 0.94539 | 0.96866 | 0.97484
|  | N-1 Limiting section | 469-2(1) | 469-2(1) | 469-2(1) | 469-2(1) | 469-2(1)
|  | Contingency Scenario | F402 | F468 | F468 | F468 | F468
F469 | 469-3 | Load (A) | 23.1993 | 39.0689 | 55.2131 | 71.2933 | 86.5316
|  | Rating (A) | 512 | 512 | 512 | 512 | 512
|  | Utilisation (%) | 4.5311 | 7.6306 | 10.7838 | 13.9245 | 16.9007
|  | Hosting Capacity (A) | 488.8007 | 472.9311 | 456.7869 | 440.7067 | 425.4684
|  | Power Factor | 0.9993 | 1 | 0.9997 | 0.999 | 0.9981
|  | N-1 Load (A) | 44.3289 | 75.854 | 107.7733 | 139.4649 | 169.3594
|  | N-1 Rating (A) | 512 | 512 | 512 | 512 | 512
|  | Contingency Utilisation (%) | 8.658 | 14.8152 | 21.0495 | 27.2392 | 33.078
|  | N-1 Hosting Capacity (A) | 467.6711 | 436.146 | 404.2267 | 372.5351 | 342.6406
|  | N-1 Power Factor | 0.9993 | 1 | 0.9997 | 0.999 | 0.9981
|  | N-1 Limiting section | 469-3(1) | 469-3(1) | 469-3(1) | 469-3(1) | 469-3(1)
|  | Contingency Scenario | F402 | F402 | F402 | F402 | F402
F470 | 470-1 | Load (A) | 70.5895 | 106.9145 | 145.5656 | 184.096 | 218.6008
|  | Rating (A) | 512 | 512 | 512 | 512 | 512
|  | Utilisation (%) | 13.7878 | 20.883 | 28.4325 | 35.9585 | 42.6955
|  | Hosting Capacity (A) | 441.4105 | 405.0855 | 366.4344 | 327.904 | 293.3992
|  | Power Factor | 0.99938 | 0.99845 | 0.99705 | 0.99522 | 0.9941
F471 | 471-1 | Load (A) | 183.6912 | 183.6912 | 183.6912 | 183.6912 | 183.6912
|  | Rating (A) | 654 | 654 | 654 | 654 | 654
|  | Utilisation (%) | 28.0874 | 28.0874 | 28.0874 | 28.0874 | 28.0874
|  | Hosting Capacity (A) | 470.3088 | 470.3088 | 470.3088 | 470.3088 | 470.3088
|  | Power Factor | 0.99134 | 0.99134 | 0.99134 | 0.99134 | 0.99134
|  | N-1 Load (A) | 359.0863 | 359.0863 | 359.0863 | 359.0863 | 359.0863
|  | N-1 Rating (A) | 654 | 654 | 654 | 654 | 654
|  | Contingency Utilisation (%) | 54.9062 | 54.9062 | 54.9062 | 54.9062 | 54.9062
|  | N-1 Hosting Capacity (A) | 294.9137 | 294.9137 | 294.9137 | 294.9137 | 294.9137
|  | N-1 Power Factor | 0.99134 | 0.99134 | 0.99134 | 0.99134 | 0.99134
|  | N-1 Limiting section | 471-1(3) | 471-1(3) | 471-1(3) | 471-1(3) | 471-1(3)
|  | Contingency Scenario | F472 | F472 | F472 | F472 | F472
F472 | 472-1 | Load (A) | 175.0524 | 175.0524 | 175.0524 | 175.0524 | 175.0524
|  | Rating (A) | 654 | 654 | 654 | 654 | 654
|  | Utilisation (%) | 26.7664 | 26.7664 | 26.7664 | 26.7664 | 26.7664
|  | Hosting Capacity (A) | 478.9476 | 478.9476 | 478.9476 | 478.9476 | 478.9476
|  | Power Factor | 0.9916 | 0.9916 | 0.9916 | 0.9916 | 0.9916
|  | N-1 Load (A) | 359.1362 | 359.1362 | 359.1362 | 359.1362 | 359.1362
|  | N-1 Rating (A) | 654 | 654 | 654 | 654 | 654
|  | Contingency Utilisation (%) | 54.9138 | 54.9138 | 54.9138 | 54.9138 | 54.9138
|  | N-1 Hosting Capacity (A) | 294.8638 | 294.8638 | 294.8638 | 294.8638 | 294.8638
|  | N-1 Power Factor | 0.9916 | 0.9916 | 0.9916 | 0.9916 | 0.9916
|  | N-1 Limiting section | 472-1(3) | 472-1(3) | 472-1(3) | 472-1(3) | 472-1(3)
|  | Contingency Scenario | F471 | F471 | F471 | F471 | F471
F473 | 473-1 | Load (A) | 40.5721 | 76.5584 | 111.4028 | 142.5369 | 169.1993
|  | Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Utilisation (%) | 5.659 | 10.6776 | 15.5373 | 19.8796 | 23.5982
|  | Hosting Capacity (A) | 676.4279 | 640.4416 | 605.5972 | 574.4631 | 547.8007
|  | Power Factor | 0.99994 | 0.99933 | 0.99849 | 0.99748 | 0.99641
|  | N-1 Load (A) | 80.9918 | 152.7167 | 222.1015 | 284.0369 | 337.0566
|  | N-1 Rating (A) | 717 | 717 | 717 | 717 | 717
|  | Contingency Utilisation (%) | 11.2959 | 21.2994 | 30.9765 | 39.6146 | 47.0093
|  | N-1 Hosting Capacity (A) | 636.0082 | 564.2833 | 494.8985 | 432.9631 | 379.9434
|  | N-1 Power Factor | 0.99985 | 0.99933 | 0.99849 | 0.99748 | 0.99641
|  | N-1 Limiting section | 473-1(2) | 473-1(2) | 473-1(2) | 473-1(2) | 473-1(2)
|  | Contingency Scenario | F392 | F392 | F392 | F392 | F392
F474A | 474A-1 | Load (A) | 47.6298 | 21.2087 | 18.8345 | 47.6649 | 78.896
|  | Rating (A) | 631 | 631 | 631 | 631 | 631
|  | Utilisation (%) | 7.5483 | 3.3611 | 2.9849 | 7.5539 | 12.5033
|  | Hosting Capacity (A) | 583.3702 | 609.7913 | 612.1655 | 583.3351 | 552.104
|  | Power Factor | 0.96371 | 0.79229 | 0.74745 | 0.971 | 0.99258
|  | N-1 Load (A) | 74.5481 | 72.009 | 114.1564 | 158.0981 | 201.6397
|  | N-1 Rating (A) | 631 | 631 | 631 | 631 | 631
|  | Contingency Utilisation (%) | 11.8143 | 11.4119 | 18.0914 | 25.0552 | 31.9556
|  | N-1 Hosting Capacity (A) | 556.4519 | 558.991 | 516.8436 | 472.9019 | 429.3603
|  | N-1 Power Factor | 0.96371 | 0.79229 | 0.74745 | 0.971 | 0.99258
|  | N-1 Limiting section | 474A-1(1) | 474A-1(1) | 474A-1(1) | 474A-1(1) | 474A-1(1)
|  | Contingency Scenario | F3670 | F389 | F389 | F389 | F389
F474B | 474B-1 | Load (A) | 3.7586 | 3.7609 | 3.7632 | 3.7655 | 3.8864
|  | Rating (A) | 786 | 786 | 786 | 786 | 818
|  | Utilisation (%) | 0.4782 | 0.47849 | 0.47878 | 0.47907 | 0.47933
|  | Hosting Capacity (A) | 782.2414 | 782.2391 | 782.2368 | 782.2345 | 814.1136
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 3.764 | 3.9202 | 3.923 | 3.9257 | 3.9282
|  | N-1 Rating (A) | 786 | 786 | 786 | 786 | 786
|  | Contingency Utilisation (%) | 0.47888 | 0.47924 | 0.47959 | 0.47992 | 0.48022
|  | N-1 Hosting Capacity (A) | 782.236 | 782.0798 | 782.077 | 782.0743 | 782.0718
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 474B-1(1) | 474B-1 | 474B-1 | 474B-1 | 474B-1
|  | Contingency Scenario | F389 | F389 | F389 | F389 | F474A
F475 | 475-1 | Load (A) | 96.7116 | 123.8507 | 166.586 | 179.3439 | 176.741
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 17.4887 | 22.3961 | 30.1241 | 32.4311 | 31.9604
|  | Hosting Capacity (A) | 456.2884 | 429.1493 | 386.414 | 373.6561 | 376.259
|  | Power Factor | 0.99998 | 0.99999 | 0.9999 | 0.99987 | 0.99988
|  | N-1 Load (A) | 187.8118 | 240.8555 | 324.7342 | 349.8585 | 344.7217
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 33.9624 | 43.5543 | 58.7223 | 63.2655 | 62.3367
|  | N-1 Hosting Capacity (A) | 365.1882 | 312.1445 | 228.2658 | 203.1415 | 208.2783
|  | N-1 Power Factor | 0.99998 | 0.99999 | 0.9999 | 0.99987 | 0.99988
|  | N-1 Limiting section | 475-1(3) | 475-1(3) | 475-1(3) | 475-1(3) | 475-1(3)
|  | Contingency Scenario | F3901 | F3901 | F3901 | F3901 | F3901
F477 | 477-1 | Load (A) | 1.6044 | 1.6075 | 1.6104 | 1.6131 | 1.6153
|  | Rating (A) | 155 | 155 | 155 | 155 | 155
|  | Utilisation (%) | 1.0351 | 1.0371 | 1.039 | 1.0407 | 1.0421
|  | Hosting Capacity (A) | 153.3956 | 153.3925 | 153.3896 | 153.3869 | 153.3847
|  | Power Factor | 1 | 1 | 1 | 1 | 1
F477 | 477-2 | Load (A) | 26.3628 | 11.3429 | 3.6026 | 17.8836 | 30.9668
|  | Rating (A) | 330 | 330 | 330 | 330 | 330
|  | Utilisation (%) | 7.9887 | 3.4372 | 1.0917 | 5.4193 | 9.3839
|  | Hosting Capacity (A) | 303.6372 | 318.6571 | 326.3974 | 312.1164 | 299.0332
|  | Power Factor | 0.99996 | 0.99859 | 0.98196 | 0.99964 | 0.99996
F477 | 477-3 | Load (A) | 26.5293 | 11.8238 | 4.9623 | 18.1728 | 31.0899
|  | Rating (A) | 711 | 711 | 711 | 711 | 711
|  | Utilisation (%) | 3.7313 | 1.663 | 0.69794 | 2.556 | 4.3727
|  | Hosting Capacity (A) | 684.4707 | 699.1762 | 706.0377 | 692.8272 | 679.9101
|  | Power Factor | 0.9944 | 0.95888 | 0.7132 | 0.98442 | 0.99656
F478 | 478-1 | Load (A) | 2.1805 | 2.1805 | 2.1805 | 2.1805 | 2.1805
|  | Rating (A) | 813 | 813 | 813 | 813 | 813
|  | Utilisation (%) | 0.26821 | 0.26821 | 0.26821 | 0.26821 | 0.26821
|  | Hosting Capacity (A) | 810.8195 | 810.8195 | 810.8195 | 810.8195 | 810.8195
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 202.2942 | 252.4794 | 300.6124 | 345.1367 | 383.6437
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 24.8824 | 31.0553 | 36.9757 | 42.4522 | 47.1886
|  | N-1 Hosting Capacity (A) | 597.7058 | 547.5206 | 499.3876 | 454.8633 | 416.3563
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 478-1(2) | 478-1(4) | 478-1(4) | 478-1(2) | 478-1(4)
|  | Contingency Scenario | F479 | F479 | F479 | F479 | F479
F479 | 479-1 | Load (A) | 204.5311 | 255.2569 | 304.032 | 349.0785 | 387.9145
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 25.0038 | 31.205 | 37.1677 | 42.6746 | 47.4223
|  | Hosting Capacity (A) | 613.4689 | 562.7431 | 513.968 | 468.9215 | 430.0855
|  | Power Factor | 0.99849 | 0.99763 | 0.99648 | 0.99536 | 0.99427
F480 | 480-1 | Load (A) | 49.5834 | 49.2579 | 48.9642 | 48.672 | 48.3682
|  | Rating (A) | 610 | 610 | 610 | 610 | 610
|  | Utilisation (%) | 8.1284 | 8.0751 | 8.0269 | 7.979 | 7.9292
|  | Hosting Capacity (A) | 560.4166 | 560.7421 | 561.0358 | 561.328 | 561.6318
|  | Power Factor | 0.99694 | 0.99707 | 0.99721 | 0.99735 | 0.99745
|  | N-1 Load (A) | 95.018 | 93.4167 | 91.7755 | 90.106 | 88.4847
|  | N-1 Rating (A) | 610 | 610 | 610 | 610 | 610
|  | Contingency Utilisation (%) | 15.5767 | 15.3142 | 15.0452 | 14.7715 | 14.5057
|  | N-1 Hosting Capacity (A) | 514.982 | 516.5833 | 518.2245 | 519.894 | 521.5153
|  | N-1 Power Factor | 0.99694 | 0.99707 | 0.99721 | 0.99735 | 0.99745
|  | N-1 Limiting section | 480-1 | 480-1 | 480-1 | 480-1 | 480-1
|  | Contingency Scenario | F3393 | F3393 | F3393 | F3393 | F3393
F481 | 481-1 | Load (A) | 11.9797 | 30.8162 | 54.6503 | 78.4218 | 100.3253
|  | Rating (A) | 705 | 705 | 705 | 705 | 705
|  | Utilisation (%) | 1.6993 | 4.3711 | 7.7518 | 11.1237 | 14.2305
|  | Hosting Capacity (A) | 693.0203 | 674.1838 | 650.3497 | 626.5782 | 604.6747
|  | Power Factor | 0.38361 | 0.93868 | 0.98467 | 0.99499 | 0.99835
|  | N-1 Load (A) | 32.6128 | 87.9003 | 147.922 | 207.9781 | 263.7246
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 4.6259 | 12.4681 | 20.9818 | 29.5004 | 37.4078
|  | N-1 Hosting Capacity (A) | 767.3872 | 712.0997 | 652.078 | 592.0219 | 536.2754
|  | N-1 Power Factor | 0.38361 | 0.93868 | 0.99992 | 0.99957 | 0.9991
|  | N-1 Limiting section | 481-1(1) | 481-1(1) | 481-1 | 481-1 | 481-1
|  | Contingency Scenario | F496 | F453 | F453 | F453 | F453
F482 | 482-1 | Load (A) | 11.9962 | 30.9785 | 54.9576 | 78.8677 | 100.8109
|  | Rating (A) | 705 | 705 | 705 | 705 | 704
|  | Utilisation (%) | 1.7016 | 4.3941 | 7.7954 | 11.1869 | 14.3197
|  | Hosting Capacity (A) | 693.0038 | 674.0215 | 650.0424 | 626.1323 | 603.1891
|  | Power Factor | 0.38518 | 0.93902 | 0.9847 | 0.99497 | 0.99917
|  | N-1 Load (A) | 32.7868 | 88.3995 | 148.7536 | 209.1469 | 265.2065
|  | N-1 Rating (A) | 704 | 704 | 704 | 704 | 704
|  | Contingency Utilisation (%) | 4.6506 | 12.5389 | 21.1298 | 29.7084 | 37.6714
|  | N-1 Hosting Capacity (A) | 671.2132 | 615.6005 | 555.2464 | 494.8531 | 438.7935
|  | N-1 Power Factor | 0.38518 | 0.93902 | 0.99995 | 0.99963 | 0.99917
|  | N-1 Limiting section | 482-1(1) | 482-1(1) | 482-1(5) | 482-1(5) | 482-1(5)
|  | Contingency Scenario | F496 | F453 | F453 | F453 | F453
F484 | 484-1 | Load (A) | 70.414 | 81.6661 | 92.7999 | 103.8005 | 114.4018
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 12.7331 | 14.7678 | 16.7812 | 18.7704 | 20.6875
|  | Hosting Capacity (A) | 482.586 | 471.3339 | 460.2001 | 449.1995 | 438.5982
|  | Power Factor | 0.99973 | 0.99901 | 0.99784 | 0.99625 | 0.99435
|  | N-1 Load (A) | 117.1268 | 163.8582 | 211.3149 | 258.8066 | 304.4051
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 21.1803 | 29.6308 | 38.2125 | 46.8005 | 55.0461
|  | N-1 Hosting Capacity (A) | 435.8732 | 389.1418 | 341.6851 | 294.1934 | 248.5949
|  | N-1 Power Factor | 0.99973 | 0.99901 | 0.99784 | 0.99625 | 0.99435
|  | N-1 Limiting section | 484-1(2) | 484-1(2) | 484-1(2) | 484-1(2) | 484-1(2)
|  | Contingency Scenario | F371 | F371 | F371 | F371 | F371
F486 | 486-1 | Load (A) | 38.8922 | 18.5845 | 24.0269 | 48.3921 | 74.6632
|  | Rating (A) | 673 | 673 | 673 | 673 | 673
|  | Utilisation (%) | 5.7789 | 2.7614 | 3.5701 | 7.1905 | 11.0941
|  | Hosting Capacity (A) | 634.1078 | 654.4155 | 648.9731 | 624.6079 | 598.3368
|  | Power Factor | 0.9125 | 0.49556 | 0.75101 | 0.95041 | 0.98298
|  | N-1 Load (A) | 66.7706 | 38.4578 | 69.5866 | 102.7098 | 135.4571
|  | N-1 Rating (A) | 721 | 721 | 721 | 721 | 721
|  | Contingency Utilisation (%) | 9.9213 | 5.7144 | 10.3398 | 15.2615 | 20.1273
|  | N-1 Hosting Capacity (A) | 654.2294 | 682.5422 | 651.4134 | 618.2902 | 585.5429
|  | N-1 Power Factor | 0.9125 | 0.49556 | 0.75101 | 0.95041 | 0.98298
|  | N-1 Limiting section | 486-1(2) | 486-1(2) | 486-1(2) | 486-1(2) | 486-1(2)
|  | Contingency Scenario | F421 | F389 | F389 | F389 | F389
F487 | 487-1 | Load (A) | 14.0388 | 4.825 | 13.2784 | 25.775 | 37.9001
|  | Rating (A) | 821 | 821 | 821 | 821 | 821
|  | Utilisation (%) | 1.71 | 0.58769 | 1.6173 | 3.1395 | 4.6163
|  | Hosting Capacity (A) | 806.9612 | 816.175 | 807.7216 | 795.225 | 783.0999
|  | Power Factor | 0.93812 | 1 | 0.9388 | 0.98674 | 0.99532
|  | N-1 Load (A) | 17.913 | 11.7538 | 37.3801 | 64.1141 | 89.5319
|  | N-1 Rating (A) | 821 | 821 | 821 | 821 | 821
|  | Contingency Utilisation (%) | 2.1819 | 1.4316 | 4.553 | 7.8093 | 10.9052
|  | N-1 Hosting Capacity (A) | 803.087 | 809.2462 | 783.6199 | 756.8859 | 731.4681
|  | N-1 Power Factor | 0.93812 | 1 | 0.9388 | 0.98674 | 0.99532
|  | N-1 Limiting section | 487-1 | 487-1 | 487-1 | 487-1 | 487-1
|  | Contingency Scenario | F377 | F377 | F377 | F377 | F377
F487 | 487-3 | Load (A) | 13.9156 | 4.4588 | 13.1561 | 25.775 | 37.8662
|  | Rating (A) | 818 | 818 | 818 | 821 | 818
|  | Utilisation (%) | 1.7012 | 0.54508 | 1.6083 | 3.144 | 4.6291
|  | Hosting Capacity (A) | 804.0844 | 813.5412 | 804.8439 | 795.225 | 780.1338
|  | Power Factor | 0.94642 | 1 | 0.94753 | 0.98674 | 0.9962
|  | N-1 Load (A) | 17.7822 | 11.5574 | 37.3248 | 64.0881 | 89.5193
|  | N-1 Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Contingency Utilisation (%) | 2.1739 | 1.4129 | 4.5629 | 7.8347 | 10.9437
|  | N-1 Hosting Capacity (A) | 800.2178 | 806.4426 | 780.6752 | 753.9119 | 728.4807
|  | N-1 Power Factor | 0.94642 | 1 | 0.94753 | 0.98893 | 0.9962
|  | N-1 Limiting section | 487-3 | 487-3 | 487-3 | 487-3 | 487-3
|  | Contingency Scenario | F377 | F377 | F377 | F377 | F377
F487 | 487-4 | Load (A) | 22.9436 | 20.8813 | 18.7397 | 16.5633 | 14.4622
|  | Rating (A) | 251 | 251 | 251 | 251 | 251
|  | Utilisation (%) | 9.1409 | 8.3193 | 7.466 | 6.5989 | 5.7618
|  | Hosting Capacity (A) | 228.0564 | 230.1187 | 232.2603 | 234.4367 | 236.5378
|  | Power Factor | 0.99983 | 0.99985 | 0.99988 | 0.9999 | 0.99992
|  | N-1 Load (A) | 22.9491 | 20.8889 | 18.7487 | 16.5729 | 14.4719
|  | N-1 Rating (A) | 251 | 251 | 251 | 251 | 251
|  | Contingency Utilisation (%) | 9.1431 | 8.3223 | 7.4696 | 6.6028 | 5.7657
|  | N-1 Hosting Capacity (A) | 228.0509 | 230.1111 | 232.2513 | 234.4271 | 236.5281
|  | N-1 Power Factor | 0.99983 | 0.99985 | 0.99988 | 0.9999 | 0.99992
|  | N-1 Limiting section | 487-4 | 487-4 | 487-4 | 487-4 | 487-4
|  | Contingency Scenario | F531 | F531 | F531 | F531 | F531
F487 | 487-5 | Load (A) | 22.9458 | 20.8834 | 18.7416 | 16.5651 | 14.4639
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 2.8051 | 2.553 | 2.2912 | 2.0251 | 1.7682
|  | Hosting Capacity (A) | 795.0542 | 797.1166 | 799.2584 | 801.4349 | 803.5361
|  | Power Factor | 0.99974 | 0.99976 | 0.99978 | 0.9998 | 0.99981
|  | N-1 Load (A) | 22.9515 | 20.8912 | 18.7508 | 16.5749 | 14.4737
|  | N-1 Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Contingency Utilisation (%) | 2.8058 | 2.5539 | 2.2923 | 2.0263 | 1.7694
|  | N-1 Hosting Capacity (A) | 795.0485 | 797.1088 | 799.2492 | 801.4251 | 803.5263
|  | N-1 Power Factor | 0.99974 | 0.99976 | 0.99978 | 0.9998 | 0.99981
|  | N-1 Limiting section | 487-5 | 487-5 | 487-5 | 487-5 | 487-5
|  | Contingency Scenario | F531 | F531 | F531 | F531 | F531
F487 | 487-7 | Load (A) | 22.9458 | 20.8834 | 18.7416 | 16.5651 | 14.4639
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 2.8051 | 2.553 | 2.2912 | 2.0251 | 1.7682
|  | Hosting Capacity (A) | 795.0542 | 797.1166 | 799.2584 | 801.4349 | 803.5361
|  | Power Factor | 0.99974 | 0.99976 | 0.99978 | 0.9998 | 0.99981
|  | N-1 Load (A) | 22.9515 | 20.8912 | 18.7508 | 16.5749 | 14.4738
|  | N-1 Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Contingency Utilisation (%) | 2.8058 | 2.5539 | 2.2923 | 2.0263 | 1.7694
|  | N-1 Hosting Capacity (A) | 795.0485 | 797.1088 | 799.2492 | 801.4251 | 803.5262
|  | N-1 Power Factor | 0.99974 | 0.99976 | 0.99978 | 0.9998 | 0.99981
|  | N-1 Limiting section | 487-5 | 487-5 | 487-5 | 487-5 | 487-5
|  | Contingency Scenario | F531 | F531 | F531 | F531 | F531
F487 | 487-9 | Load (A) | 9.8079 | 20.3944 | 31.202 | 41.9897 | 52.183
|  | Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Utilisation (%) | 1.3756 | 2.8604 | 4.3762 | 5.8892 | 7.3188
|  | Hosting Capacity (A) | 703.1921 | 692.6056 | 681.798 | 671.0103 | 660.817
|  | Power Factor | 0.99646 | 0.99948 | 0.99993 | 0.99999 | 0.99992
|  | N-1 Load (A) |  | 30.8048 | 55.6566 | 80.4602 | 103.8889
|  | N-1 Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Contingency Utilisation (%) |  | 4.3204 | 7.806 | 11.2847 | 14.5707
|  | N-1 Hosting Capacity (A) |  | 682.1952 | 657.3434 | 632.5398 | 609.1111
|  | N-1 Power Factor | 1 | 0.99948 | 0.99993 | 0.99999 | 0.99992
|  | N-1 Limiting section | 487-2 | 487-9(1) | 487-9(1) | 487-9(1) | 487-9(1)
|  | Contingency Scenario |  | F377 | F377 | F377 | F377
F488 | 488-1 | Load (A) | 30.8457 | 46.6186 | 62.3173 | 77.6243 | 91.5137
|  | Rating (A) | 582 | 582 | 582 | 582 | 582
|  | Utilisation (%) | 5.2999 | 8.0101 | 10.7074 | 13.3375 | 15.724
|  | Hosting Capacity (A) | 551.1543 | 535.3814 | 519.6827 | 504.3757 | 490.4863
|  | Power Factor | 0.99998 | 0.99976 | 0.99999 | 0.99995 | 0.99979
F488 | 488-3 | Load (A) | 30.8452 | 46.6167 | 62.3169 | 77.6254 | 91.516
|  | Rating (A) | 293 | 293 | 293 | 293 | 293
|  | Utilisation (%) | 10.5275 | 15.9107 | 21.2687 | 26.4933 | 31.2341
|  | Hosting Capacity (A) | 262.1548 | 246.3833 | 230.6831 | 215.3746 | 201.484
|  | Power Factor | 0.99999 | 0.99978 | 0.99999 | 0.99996 | 0.99981
F488 | 488-4 | Load (A) | 15.1239 | 23.7326 | 32.3233 | 40.6244 | 47.9459
|  | Rating (A) | 293 | 293 | 293 | 293 | 293
|  | Utilisation (%) | 5.1617 | 8.0999 | 11.0319 | 13.865 | 16.3638
|  | Hosting Capacity (A) | 277.8761 | 269.2674 | 260.6767 | 252.3756 | 245.0541
|  | Power Factor | 0.99492 | 0.99987 | 0.99974 | 0.99956 | 0.99939
F488 | 488-5 | Load (A) | 15.8552 | 22.9029 | 30.0139 | 37.0236 | 43.5935
|  | Rating (A) | 403 | 403 | 403 | 403 | 403
|  | Utilisation (%) | 3.9343 | 5.6831 | 7.4476 | 9.187 | 10.8177
|  | Hosting Capacity (A) | 387.1448 | 380.0971 | 372.9861 | 365.9764 | 359.4065
|  | Power Factor | 0.99656 | 0.99888 | 0.99967 | 0.99994 | 1
F488 | 488-6 | Load (A) | 15.8005 | 22.8792 | 30.0105 | 37.0357 | 43.6194
|  | Rating (A) | 438 | 438 | 438 | 438 | 438
|  | Utilisation (%) | 3.6074 | 5.2236 | 6.8517 | 8.4557 | 9.9588
|  | Hosting Capacity (A) | 422.1995 | 415.1208 | 407.9895 | 400.9643 | 394.3806
|  | Power Factor | 0.99989 | 0.99981 | 0.99971 | 0.99959 | 0.99943
F489 | 489-1 | Load (A) | 75.406 | 88.1552 | 100.7599 | 112.6519 | 123.0534
|  | Rating (A) | 293 | 293 | 293 | 293 | 293
|  | Utilisation (%) | 25.7358 | 30.0871 | 34.389 | 38.4477 | 41.9978
|  | Hosting Capacity (A) | 217.594 | 204.8448 | 192.2401 | 180.3481 | 169.9466
|  | Power Factor | 0.97116 | 0.96972 | 0.96762 | 0.96517 | 0.96271
|  | N-1 Load (A) | 92.0959 | 123.6781 | 156.4161 | 189.3216 | 220.4606
|  | N-1 Rating (A) | 293 | 293 | 293 | 293 | 293
|  | Contingency Utilisation (%) | 31.432 | 42.2109 | 53.3843 | 64.6149 | 75.2425
|  | N-1 Hosting Capacity (A) | 200.9041 | 169.3219 | 136.5839 | 103.6784 | 72.5394
|  | N-1 Power Factor | 0.97116 | 0.96972 | 0.96762 | 0.96517 | 0.96271
|  | N-1 Limiting section | 489-1(3) | 489-1(3) | 489-1(3) | 489-1(3) | 489-1(3)
|  | Contingency Scenario | F3100 | F3100 | F3100 | F3100 | F3100
F490 | 490-1 | Load (A) | 60.4241 | 60.4241 | 60.4241 | 60.4241 | 60.4241
|  | Rating (A) | 628 | 628 | 628 | 628 | 628
|  | Utilisation (%) | 9.6217 | 9.6217 | 9.6217 | 9.6217 | 9.6217
|  | Hosting Capacity (A) | 567.5759 | 567.5759 | 567.5759 | 567.5759 | 567.5759
|  | Power Factor | 0.99695 | 0.99695 | 0.99695 | 0.99695 | 0.99695
|  | N-1 Load (A) | 118.0303 | 118.0303 | 118.0303 | 118.0303 | 118.0303
|  | N-1 Rating (A) | 628 | 628 | 628 | 628 | 628
|  | Contingency Utilisation (%) | 18.7946 | 18.7946 | 18.7946 | 18.7946 | 18.7946
|  | N-1 Hosting Capacity (A) | 509.9697 | 509.9697 | 509.9697 | 509.9697 | 509.9697
|  | N-1 Power Factor | 0.99695 | 0.99695 | 0.99695 | 0.99695 | 0.99695
|  | N-1 Limiting section | 490-1 | 490-1 | 490-1 | 490-1 | 490-1
|  | Contingency Scenario | F492 | F492 | F492 | F492 | F492
F491 | 491-1 | Load (A) | 144.2989 | 144.315 | 144.3303 | 144.346 | 144.365
|  | Rating (A) | 450 | 450 | 450 | 450 | 450
|  | Utilisation (%) | 32.0664 | 32.07 | 32.0734 | 32.0769 | 32.0811
|  | Hosting Capacity (A) | 305.7011 | 305.685 | 305.6697 | 305.654 | 305.635
|  | Power Factor | 0.99644 | 0.99644 | 0.99644 | 0.99644 | 0.99644
|  | N-1 Load (A) | 288.0806 | 288.113 | 288.1437 | 288.1753 | 288.2135
|  | N-1 Rating (A) | 450 | 450 | 450 | 450 | 450
|  | Contingency Utilisation (%) | 64.0179 | 64.0251 | 64.0319 | 64.039 | 64.0475
|  | N-1 Hosting Capacity (A) | 161.9194 | 161.887 | 161.8563 | 161.8247 | 161.7865
|  | N-1 Power Factor | 0.99644 | 0.99644 | 0.99644 | 0.99644 | 0.99644
|  | N-1 Limiting section | 491-1(1) | 491-1(1) | 491-1(1) | 491-1(1) | 491-1(1)
|  | Contingency Scenario | F493 | F493 | F493 | F493 | F493
F492 | 492-1 | Load (A) | 58.4004 | 58.4004 | 58.4004 | 58.4004 | 58.4004
|  | Rating (A) | 463 | 463 | 463 | 463 | 463
|  | Utilisation (%) | 12.6135 | 12.6135 | 12.6135 | 12.6135 | 12.6135
|  | Hosting Capacity (A) | 404.5996 | 404.5996 | 404.5996 | 404.5996 | 404.5996
|  | Power Factor | 0.98819 | 0.98819 | 0.98819 | 0.98819 | 0.98819
|  | N-1 Load (A) | 118.0822 | 118.0822 | 118.0822 | 118.0822 | 118.0822
|  | N-1 Rating (A) | 463 | 463 | 463 | 463 | 463
|  | Contingency Utilisation (%) | 25.5037 | 25.5037 | 25.5037 | 25.5037 | 25.5037
|  | N-1 Hosting Capacity (A) | 344.9178 | 344.9178 | 344.9178 | 344.9178 | 344.9178
|  | N-1 Power Factor | 0.98819 | 0.98819 | 0.98819 | 0.98819 | 0.98819
|  | N-1 Limiting section | 492-1(1) | 492-1(1) | 492-1(1) | 492-1(1) | 492-1(1)
|  | Contingency Scenario | F490 | F490 | F490 | F490 | F490
F493 | 493-1 | Load (A) | 144.6763 | 144.6925 | 144.7079 | 144.7237 | 144.7428
|  | Rating (A) | 536 | 536 | 536 | 536 | 536
|  | Utilisation (%) | 26.9918 | 26.9949 | 26.9977 | 27.0007 | 27.0043
|  | Hosting Capacity (A) | 391.3237 | 391.3075 | 391.2921 | 391.2763 | 391.2572
|  | Power Factor | 0.99213 | 0.99212 | 0.99212 | 0.99212 | 0.99212
|  | N-1 Load (A) | 287.8634 | 287.8958 | 287.9264 | 287.9579 | 287.9961
|  | N-1 Rating (A) | 536 | 536 | 536 | 536 | 536
|  | Contingency Utilisation (%) | 53.7059 | 53.7119 | 53.7176 | 53.7235 | 53.7306
|  | N-1 Hosting Capacity (A) | 248.1366 | 248.1042 | 248.0736 | 248.0421 | 248.0039
|  | N-1 Power Factor | 0.99213 | 0.99212 | 0.99212 | 0.99212 | 0.99212
|  | N-1 Limiting section | 493-1 | 493-1 | 493-1 | 493-1 | 493-1
|  | Contingency Scenario | F491 | F491 | F491 | F491 | F491
F494 | 494-1 | Load (A) | 33.0499 | 32.4458 | 32.2259 | 32.174 | 32.2072
|  | Rating (A) | 488 | 488 | 488 | 488 | 488
|  | Utilisation (%) | 6.7725 | 6.6487 | 6.6037 | 6.593 | 6.5998
|  | Hosting Capacity (A) | 454.9501 | 455.5542 | 455.7741 | 455.826 | 455.7928
|  | Power Factor | 0.9931 | 0.99301 | 0.99297 | 0.99296 | 0.99297
|  | N-1 Load (A) | 66.46 | 65.2438 | 64.801 | 64.6966 | 64.7633
|  | N-1 Rating (A) | 488 | 488 | 488 | 488 | 488
|  | Contingency Utilisation (%) | 13.6189 | 13.3696 | 13.2789 | 13.2575 | 13.2712
|  | N-1 Hosting Capacity (A) | 421.54 | 422.7562 | 423.199 | 423.3034 | 423.2367
|  | N-1 Power Factor | 0.9931 | 0.99301 | 0.99297 | 0.99296 | 0.99297
|  | N-1 Limiting section | 494-1(1) | 494-1(1) | 494-1(1) | 494-1(1) | 494-1(1)
|  | Contingency Scenario | F495 | F495 | F495 | F495 | F495
F495 | 495-1 | Load (A) | 33.6342 | 33.0191 | 32.7952 | 32.7424 | 32.7762
|  | Rating (A) | 600 | 600 | 600 | 600 | 600
|  | Utilisation (%) | 5.6057 | 5.5032 | 5.4659 | 5.4571 | 5.4627
|  | Hosting Capacity (A) | 566.3658 | 566.9809 | 567.2048 | 567.2576 | 567.2238
|  | Power Factor | 0.99881 | 0.99889 | 0.99892 | 0.99893 | 0.99892
|  | N-1 Load (A) | 66.4588 | 65.2458 | 64.8043 | 64.7001 | 64.7667
|  | N-1 Rating (A) | 600 | 600 | 600 | 600 | 600
|  | Contingency Utilisation (%) | 11.0765 | 10.8743 | 10.8007 | 10.7834 | 10.7945
|  | N-1 Hosting Capacity (A) | 533.5412 | 534.7542 | 535.1957 | 535.2999 | 535.2333
|  | N-1 Power Factor | 0.99881 | 0.99889 | 0.99892 | 0.99893 | 0.99892
|  | N-1 Limiting section | 495-1 | 495-1 | 495-1 | 495-1 | 495-1
|  | Contingency Scenario | F494 | F494 | F494 | F494 | F494
F496 | 496-1 | Load (A) | 52.2117 | 89.5694 | 128.8002 | 168.7495 | 207.0014
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 9.4415 | 16.197 | 23.2912 | 30.5153 | 37.4325
|  | Hosting Capacity (A) | 500.7883 | 463.4306 | 424.1998 | 384.2505 | 345.9986
|  | Power Factor | 0.99992 | 0.99968 | 0.99926 | 0.99869 | 0.99799
F497 | 497-1 | Load (A) | 51.1069 | 88.5184 | 124.126 | 158.2083 | 189.4684
|  | Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Utilisation (%) | 7.1679 | 12.4149 | 17.409 | 22.1891 | 26.5734
|  | Hosting Capacity (A) | 661.8931 | 624.4816 | 588.874 | 554.7917 | 523.5316
|  | Power Factor | 0.99988 | 0.99998 | 0.99974 | 0.99931 | 0.9988
|  | N-1 Load (A) | 107.5521 | 175.7159 | 240.3803 | 301.9632 | 358.2883
|  | N-1 Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Contingency Utilisation (%) | 15.0844 | 24.6446 | 33.7139 | 42.3511 | 50.2508
|  | N-1 Hosting Capacity (A) | 605.4479 | 537.2841 | 472.6197 | 411.0368 | 354.7117
|  | N-1 Power Factor | 0.99988 | 0.99998 | 0.99974 | 0.99931 | 0.9988
|  | N-1 Limiting section | 497-1 | 497-1 | 497-1 | 497-1 | 497-1
|  | Contingency Scenario | F3250 | F3250 | F3250 | F3250 | F3250
F499 | 499-1 | Load (A) | 25.3007 | 71.2501 | 119.8105 | 167.1368 | 209.3397
|  | Rating (A) | 676 | 676 | 676 | 676 | 676
|  | Utilisation (%) | 3.7427 | 10.54 | 17.7234 | 24.7244 | 30.9674
|  | Hosting Capacity (A) | 650.6993 | 604.7499 | 556.1895 | 508.8632 | 466.6603
|  | Power Factor | 0.93805 | 0.9949 | 0.99893 | 0.99837 | 0.99778
|  | N-1 Load (A) | 43.3223 | 127.3499 | 215.0078 | 299.861 | 375.5097
|  | N-1 Rating (A) | 758 | 758 | 758 | 758 | 758
|  | Contingency Utilisation (%) | 6.4086 | 18.8387 | 31.8059 | 44.3581 | 55.5488
|  | N-1 Hosting Capacity (A) | 714.6777 | 630.6501 | 542.9922 | 458.139 | 382.4903
|  | N-1 Power Factor | 0.93805 | 0.9949 | 0.99893 | 0.99837 | 0.99778
|  | N-1 Limiting section | 499-1 | 499-1 | 499-1 | 499-1 | 499-1
|  | Contingency Scenario | F461 | F461 | F461 | F461 | F461
F504 | 504-1 | Load (A) | 41.7011 | 26.7452 | 19.8524 | 30.5225 | 47.0836
|  | Rating (A) | 601 | 601 | 601 | 601 | 601
|  | Utilisation (%) | 6.9386 | 4.4501 | 3.3032 | 5.0786 | 7.8342
|  | Hosting Capacity (A) | 559.2989 | 574.2548 | 581.1476 | 570.4775 | 553.9164
|  | Power Factor | 0.87902 | 0.66881 | 0.28409 | 0.78093 | 0.92345
|  | N-1 Load (A) | 61.5421 | 38.2619 | 27.1839 | 44.6459 | 70.3821
|  | N-1 Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Contingency Utilisation (%) | 10.24 | 6.3664 | 4.5231 | 7.4286 | 11.7108
|  | N-1 Hosting Capacity (A) | 651.4579 | 674.7381 | 685.8161 | 668.3541 | 642.6179
|  | N-1 Power Factor | 0.87902 | 0.66881 | 0.28409 | 0.78093 | 0.92345
|  | N-1 Limiting section | 504-1 | 504-1 | 504-1 | 504-1 | 504-1
|  | Contingency Scenario | F606 | F3393 | F480 | F480 | F606
F505 | 505-1 | Load (A) | 31.3675 | 22.2392 | 29.5712 | 48.3125 | 69.9277
|  | Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Utilisation (%) | 4.4811 | 3.177 | 4.2245 | 6.9018 | 9.9897
|  | Hosting Capacity (A) | 668.6325 | 677.7608 | 670.4288 | 651.6875 | 630.0723
|  | Power Factor | 0.74745 | 1 | 0.64055 | 0.88176 | 0.94831
|  | N-1 Load (A) | 41.9726 | 29.3239 | 39.2904 | 64.7703 | 96.0948
|  | N-1 Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Contingency Utilisation (%) | 5.9961 | 4.1891 | 5.6129 | 9.2529 | 13.7278
|  | N-1 Hosting Capacity (A) | 658.0274 | 670.6761 | 660.7096 | 635.2297 | 603.9052
|  | N-1 Power Factor | 0.74745 | 1 | 0.64055 | 0.88176 | 0.94831
|  | N-1 Limiting section | 505-1 | 505-1 | 505-1 | 505-1 | 505-1
|  | Contingency Scenario | F671 | F671 | F671 | F671 | F524
F506 | 506-1 | Load (A) | 57.6506 | 56.0548 | 55.35 | 54.4173 | 54.807
|  | Rating (A) | 720 | 720 | 720 | 720 | 720
|  | Utilisation (%) | 8.007 | 7.7854 | 7.6875 | 7.558 | 7.6121
|  | Hosting Capacity (A) | 662.3494 | 663.9452 | 664.65 | 665.5827 | 665.193
|  | Power Factor | 0.99324 | 0.99281 | 0.99259 | 0.99232 | 0.99245
|  | N-1 Load (A) | 99.3539 | 96.5771 | 95.3501 | 93.7272 | 94.4056
|  | N-1 Rating (A) | 787 | 787 | 787 | 787 | 787
|  | Contingency Utilisation (%) | 13.7991 | 13.4135 | 13.2431 | 13.0177 | 13.1119
|  | N-1 Hosting Capacity (A) | 687.6461 | 690.4229 | 691.6499 | 693.2728 | 692.5944
|  | N-1 Power Factor | 0.99324 | 0.99281 | 0.99259 | 0.99232 | 0.99245
|  | N-1 Limiting section | 506-1 | 506-1 | 506-1 | 506-1 | 506-1
|  | Contingency Scenario | F513 | F513 | F513 | F513 | F513
F507A | 507A-1 | Load (A) | 7.1322 | 6.4058 | 15.2653 | 25.5941 | 35.056
|  | Rating (A) | 735 | 735 | 735 | 735 | 735
|  | Utilisation (%) | 0.97036 | 0.87153 | 2.0769 | 3.4822 | 4.7695
|  | Hosting Capacity (A) | 727.8678 | 728.5942 | 719.7347 | 709.4059 | 699.944
|  | Power Factor | 0.7181 | 0.61853 | 0.93997 | 0.97547 | 0.98348
|  | N-1 Load (A) | 14.0083 | 11.6588 | 21.398 | 36.5993 | 50.3842
|  | N-1 Rating (A) | 858 | 858 | 858 | 858 | 858
|  | Contingency Utilisation (%) | 1.9059 | 1.5862 | 2.9113 | 4.9795 | 6.855
|  | N-1 Hosting Capacity (A) | 843.9917 | 846.3412 | 836.602 | 821.4007 | 807.6158
|  | N-1 Power Factor | 0.7181 | 0.61853 | 0.93997 | 0.97547 | 0.98348
|  | N-1 Limiting section | 507A-1 | 507A-1 | 507A-1 | 507A-1 | 507A-1
|  | Contingency Scenario | F703 | F3393 | F3393 | F3390 | F3390
F507B | 507B-1 | Load (A) | 9.3825 | 8.744 | 16.2449 | 25.9783 | 35.075
|  | Rating (A) | 727 | 727 | 727 | 727 | 727
|  | Utilisation (%) | 1.2906 | 1.2028 | 2.2345 | 3.5734 | 4.8246
|  | Hosting Capacity (A) | 717.6175 | 718.256 | 710.7551 | 701.0217 | 691.925
|  | Power Factor | 0.54592 | 0.45313 | 0.88331 | 0.96106 | 0.98295
|  | N-1 Load (A) | 15.2437 | 13.2953 | 22.3895 | 37.0494 | 50.4879
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 2.0968 | 1.8288 | 3.0797 | 5.0962 | 6.9447
|  | N-1 Hosting Capacity (A) | 784.7563 | 786.7047 | 777.6105 | 762.9506 | 749.5121
|  | N-1 Power Factor | 0.54592 | 0.45313 | 0.88331 | 0.96106 | 0.98295
|  | N-1 Limiting section | 507B-1 | 507B-1 | 507B-1 | 507B-1 | 507B-1
|  | Contingency Scenario | F480 | F3393 | F3390 | F3390 | F3390
F509A | 509A-1 | Load (A) | 37.5496 | 52.7637 | 68.3554 | 83.7806 | 98.0505
|  | Rating (A) | 721 | 721 | 721 | 721 | 721
|  | Utilisation (%) | 5.208 | 7.3181 | 9.4806 | 11.6201 | 13.5992
|  | Hosting Capacity (A) | 683.4504 | 668.2363 | 652.6446 | 637.2194 | 622.9495
|  | Power Factor | 0.92267 | 0.95999 | 0.97594 | 0.98414 | 0.98873
|  | N-1 Load (A) | 71.7743 | 102.1809 | 133.097 | 163.5731 | 191.7128
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 9.9548 | 14.1721 | 18.4601 | 22.687 | 26.5898
|  | N-1 Hosting Capacity (A) | 728.2257 | 697.8191 | 666.903 | 636.4269 | 608.2872
|  | N-1 Power Factor | 0.92267 | 0.95999 | 0.97594 | 0.98414 | 0.98873
|  | N-1 Limiting section | 509A-1 | 509A-1 | 509A-1 | 509A-1 | 509A-1
|  | Contingency Scenario | F510A | F510A | F510A | F510A | F510A
F510A | 510A-1 | Load (A) | 37.1935 | 52.2481 | 67.679 | 82.9464 | 97.0709
|  | Rating (A) | 721 | 721 | 721 | 721 | 721
|  | Utilisation (%) | 5.1586 | 7.2466 | 9.3868 | 11.5044 | 13.4634
|  | Hosting Capacity (A) | 683.8065 | 668.7519 | 653.321 | 638.0536 | 623.9291
|  | Power Factor | 0.92212 | 0.95969 | 0.97576 | 0.98402 | 0.98864
|  | N-1 Load (A) | 71.7734 | 102.1664 | 133.0708 | 163.5362 | 191.6665
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 9.9547 | 14.1701 | 18.4564 | 22.6819 | 26.5834
|  | N-1 Hosting Capacity (A) | 728.2266 | 697.8336 | 666.9292 | 636.4638 | 608.3335
|  | N-1 Power Factor | 0.92212 | 0.95969 | 0.97576 | 0.98402 | 0.98864
|  | N-1 Limiting section | 510A-1 | 510A-1 | 510A-1 | 510A-1 | 510A-1
|  | Contingency Scenario | F509A | F509A | F509A | F509A | F509A
F511 | 511-1 | Load (A) | 8.4436 | 3.1384 | 9.8376 | 18.8789 | 28.0312
|  | Rating (A) | 739 | 739 | 739 | 739 | 739
|  | Utilisation (%) | 1.1426 | 0.42469 | 1.3312 | 2.5547 | 3.7931
|  | Hosting Capacity (A) | 730.5564 | 735.8616 | 729.1624 | 720.1211 | 710.9688
|  | Power Factor | 0.93137 | 0.98777 | 0.95038 | 0.98787 | 0.99529
|  | N-1 Load (A) | 16.0549 | 3.1873 | 18.985 | 37.5035 | 56.0016
|  | N-1 Rating (A) | 753 | 753 | 753 | 753 | 753
|  | Contingency Utilisation (%) | 2.1725 | 0.4313 | 2.569 | 5.0749 | 7.578
|  | N-1 Hosting Capacity (A) | 736.9451 | 749.8127 | 734.015 | 715.4965 | 696.9984
|  | N-1 Power Factor | 0.93137 | 0.98777 | 0.95038 | 0.98787 | 0.99529
|  | N-1 Limiting section | 511-1 | 511-1 | 511-1 | 511-1 | 511-1
|  | Contingency Scenario | F514 | F514 | F514 | F514 | F514
F513 | 513-1 | Load (A) | 57.1945 | 55.6116 | 54.9126 | 53.9875 | 54.374
|  | Rating (A) | 720 | 720 | 720 | 720 | 720
|  | Utilisation (%) | 7.9437 | 7.7238 | 7.6267 | 7.4983 | 7.5519
|  | Hosting Capacity (A) | 662.8055 | 664.3884 | 665.0874 | 666.0125 | 665.626
|  | Power Factor | 0.99314 | 0.9927 | 0.99248 | 0.99221 | 0.99233
|  | N-1 Load (A) | 99.1466 | 96.3758 | 95.1515 | 93.532 | 94.209
|  | N-1 Rating (A) | 787 | 787 | 787 | 787 | 787
|  | Contingency Utilisation (%) | 13.7704 | 13.3855 | 13.2155 | 12.9906 | 13.0846
|  | N-1 Hosting Capacity (A) | 687.8534 | 690.6242 | 691.8485 | 693.468 | 692.791
|  | N-1 Power Factor | 0.99314 | 0.9927 | 0.99248 | 0.99221 | 0.99233
|  | N-1 Limiting section | 513-1 | 513-1 | 513-1 | 513-1 | 513-1
|  | Contingency Scenario | F506 | F506 | F506 | F506 | F506
F514 | 514-1 | Load (A) | 8.4861 | 3.1385 | 9.8892 | 18.986 | 28.1927
|  | Rating (A) | 739 | 739 | 739 | 739 | 739
|  | Utilisation (%) | 1.1483 | 0.42469 | 1.3382 | 2.5692 | 3.815
|  | Hosting Capacity (A) | 730.5139 | 735.8615 | 729.1108 | 720.014 | 710.8073
|  | Power Factor | 0.9321 | 0.99308 | 0.95093 | 0.98802 | 0.99535
|  | N-1 Load (A) | 16.0514 | 3.1697 | 18.9821 | 37.5022 | 56.0009
|  | N-1 Rating (A) | 753 | 753 | 753 | 753 | 753
|  | Contingency Utilisation (%) | 2.172 | 0.42891 | 2.5686 | 5.0747 | 7.5779
|  | N-1 Hosting Capacity (A) | 736.9486 | 749.8303 | 734.0179 | 715.4978 | 696.9991
|  | N-1 Power Factor | 0.9321 | 0.99308 | 0.95093 | 0.98802 | 0.99535
|  | N-1 Limiting section | 514-1 | 514-1 | 514-1 | 514-1 | 514-1
|  | Contingency Scenario | F511 | F511 | F511 | F511 | F511
F515 | 515 | Load (A) | 26.4046 | 21.0044 | 43.3948 | 72.2313 | 100.2645
|  | Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Utilisation (%) | 3.7721 | 3.0006 | 6.1993 | 10.3187 | 14.3235
|  | Hosting Capacity (A) | 673.5954 | 678.9956 | 656.6052 | 627.7687 | 599.7355
|  | Power Factor | 0.68336 | 0.4579 | 0.91518 | 0.97625 | 0.99119
|  | N-1 Load (A) | 36.3951 | 28.4345 | 61.1605 | 102.5407 | 142.604
|  | N-1 Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Contingency Utilisation (%) | 5.1993 | 4.0621 | 8.7372 | 14.6487 | 20.372
|  | N-1 Hosting Capacity (A) | 663.6049 | 671.5655 | 638.8395 | 597.4593 | 557.396
|  | N-1 Power Factor | 0.68336 | 0.4579 | 0.91518 | 0.97625 | 0.99119
|  | N-1 Limiting section | 515 | 515 | 515 | 515 | 515
|  | Contingency Scenario | F554 | F554 | F554 | F554 | F554
F515 | 515-1 | Load (A) | 29.4805 | 24.6622 | 45.1723 | 73.2106 | 100.8763
|  | Rating (A) | 740 | 740 | 740 | 740 | 740
|  | Utilisation (%) | 3.9838 | 3.3327 | 6.1044 | 9.8933 | 13.6319
|  | Hosting Capacity (A) | 710.5195 | 715.3378 | 694.8277 | 666.7894 | 639.1237
|  | Power Factor | 0.61225 | 0.39003 | 0.87934 | 0.96337 | 0.98535
|  | N-1 Load (A) | 39.3282 | 32.048 | 62.8413 | 103.4657 | 143.1852
|  | N-1 Rating (A) | 740 | 740 | 740 | 740 | 740
|  | Contingency Utilisation (%) | 5.3146 | 4.3308 | 8.4921 | 13.9818 | 19.3494
|  | N-1 Hosting Capacity (A) | 700.6718 | 707.952 | 677.1587 | 636.5343 | 596.8148
|  | N-1 Power Factor | 0.61225 | 0.39003 | 0.87934 | 0.96337 | 0.98535
|  | N-1 Limiting section | 515-1(1) | 515-1(1) | 515-1(1) | 515-1(1) | 515-1(1)
|  | Contingency Scenario | F554 | F554 | F554 | F554 | F554
F523 | 523A-1 | Load (A) | 7.7883 | 7.7883 | 7.7883 | 7.7883 | 7.7883
|  | Rating (A) | 650 | 650 | 650 | 650 | 650
|  | Utilisation (%) | 1.1982 | 1.1982 | 1.1982 | 1.1982 | 1.1982
|  | Hosting Capacity (A) | 642.2117 | 642.2117 | 642.2117 | 642.2117 | 642.2117
|  | Power Factor | 1 | 1 | 1 | 1 | 1
F524 | 524-1 | Load (A) | 22.7464 | 16.8571 | 21.0169 | 32.9424 | 47.148
|  | Rating (A) | 453 | 453 | 453 | 453 | 453
|  | Utilisation (%) | 5.0213 | 3.7212 | 4.6395 | 7.2721 | 10.4079
|  | Hosting Capacity (A) | 430.2536 | 436.1429 | 431.9831 | 420.0576 | 405.852
|  | Power Factor | 0.67821 | 1 | 0.62358 | 0.88021 | 0.95236
|  | N-1 Load (A) | 39.1357 | 28.3558 | 36.5046 | 58.4463 | 84.1017
|  | N-1 Rating (A) | 453 | 453 | 453 | 453 | 453
|  | Contingency Utilisation (%) | 8.6392 | 6.2596 | 8.0584 | 12.9021 | 18.5655
|  | N-1 Hosting Capacity (A) | 413.8643 | 424.6442 | 416.4954 | 394.5537 | 368.8983
|  | N-1 Power Factor | 0.67821 | 1 | 0.62358 | 0.88021 | 0.95236
|  | N-1 Limiting section | 524-1(4) | 524-1(4) | 524-1(4) | 524-1(4) | 524-1(4)
|  | Contingency Scenario | F505 | F505 | F505 | F505 | F505
F524 | 524-2 | Load (A) | 22.4933 | 16.5132 | 20.7474 | 32.7792 | 47.043
|  | Rating (A) | 410 | 410 | 410 | 410 | 410
|  | Utilisation (%) | 5.4862 | 4.0276 | 5.0604 | 7.9949 | 11.4739
|  | Hosting Capacity (A) | 387.5067 | 393.4868 | 389.2526 | 377.2208 | 362.957
|  | Power Factor | 0.68443 | 1 | 0.63124 | 0.88367 | 0.95346
|  | N-1 Load (A) | 38.8959 | 28.0127 | 36.2358 | 58.2816 | 83.9926
|  | N-1 Rating (A) | 410 | 410 | 410 | 410 | 410
|  | Contingency Utilisation (%) | 9.4868 | 6.8324 | 8.838 | 14.215 | 20.486
|  | N-1 Hosting Capacity (A) | 371.1041 | 381.9873 | 373.7642 | 351.7184 | 326.0074
|  | N-1 Power Factor | 0.68443 | 1 | 0.63124 | 0.88367 | 0.95346
|  | N-1 Limiting section | 524-2 | 524-2 | 524-2 | 524-2 | 524-2
|  | Contingency Scenario | F505 | F505 | F505 | F505 | F505
F527 | 527-1 | Load (A) | 47.8379 | 48.6008 | 49.3996 | 50.1985 | 50.9527
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 8.6506 | 8.7886 | 8.933 | 9.0775 | 9.2139
|  | Hosting Capacity (A) | 505.1621 | 504.3992 | 503.6004 | 502.8015 | 502.0473
|  | Power Factor | 0.99677 | 0.99851 | 0.99956 | 0.99998 | 0.99988
|  | N-1 Load (A) | 76.3007 | 74.0253 | 71.6351 | 69.1247 | 66.5985
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 13.7976 | 13.3861 | 12.9539 | 12.5 | 12.0431
|  | N-1 Hosting Capacity (A) | 476.6993 | 478.9747 | 481.3649 | 483.8753 | 486.4015
|  | N-1 Power Factor | 0.99677 | 0.99851 | 0.99956 | 0.99998 | 0.99988
|  | N-1 Limiting section | 527-1(1) | 527-1(1) | 527-1(1) | 527-1(1) | 527-1(1)
|  | Contingency Scenario | F663 | F663 | F663 | F663 | F663
F531 | 531-1 | Load (A) | 8.1558 | 15.1949 | 22.0624 | 28.5853 | 34.4393
|  | Rating (A) | 200 | 200 | 200 | 200 | 200
|  | Utilisation (%) | 4.0779 | 7.5974 | 11.0312 | 14.2927 | 17.2196
|  | Hosting Capacity (A) | 191.8442 | 184.8051 | 177.9376 | 171.4147 | 165.5607
|  | Power Factor | 0.99362 | 0.99856 | 0.99957 | 0.99989 | 0.99999
|  | N-1 Load (A) |  |  |  |  | 34.4398
|  | N-1 Rating (A) | 155 | 200 | 200 | 200 | 200
F533 | 533-1 | Load (A) | 2.4492 | 3.5016 | 4.3447 | 4.9976 | 5.4777
|  | Rating (A) | 78 | 78 | 78 | 78 | 78
|  | Utilisation (%) | 3.14 | 4.4892 | 5.5702 | 6.4072 | 7.0228
|  | Hosting Capacity (A) | 75.5508 | 74.4984 | 73.6553 | 73.0024 | 72.5223
|  | Power Factor | 0.99698 | 0.99844 | 0.99893 | 0.99915 | 0.99926
F539 | 539-1 | Load (A) | 14.4904 | 32.1343 | 50.4242 | 68.8474 | 86.4299
|  | Rating (A) | 495 | 495 | 495 | 495 | 495
|  | Utilisation (%) | 2.929 | 6.4921 | 10.1867 | 13.9086 | 17.4606
|  | Hosting Capacity (A) | 480.5096 | 462.8657 | 444.5758 | 426.1526 | 408.5701
|  | Power Factor | 0.99131 | 0.99973 | 0.99985 | 0.99911 | 0.99813
|  | N-1 Load (A) | 45.9747 | 86.7806 | 128.3354 | 169.9962 | 209.9648
|  | N-1 Rating (A) | 495 | 495 | 495 | 495 | 495
|  | Contingency Utilisation (%) | 9.2878 | 17.5314 | 25.9264 | 34.3427 | 42.4171
|  | N-1 Hosting Capacity (A) | 449.0253 | 408.2194 | 366.6646 | 325.0038 | 285.0352
|  | N-1 Power Factor | 0.99131 | 0.99973 | 0.99985 | 0.99911 | 0.99813
|  | N-1 Limiting section | 539-1(1) | 539-1(1) | 539-1(1) | 539-1(1) | 539-1(1)
|  | Contingency Scenario | F571 | F571 | F571 | F571 | F571
F540 | 540-1 | Load (A) | 51.7079 | 42.0432 | 31.2273 | 20.2641 | 13.5943
|  | Rating (A) | 704 | 704 | 704 | 704 | 704
|  | Utilisation (%) | 7.3449 | 5.972 | 4.4357 | 2.8784 | 1.931
|  | Hosting Capacity (A) | 652.2921 | 661.9568 | 672.7727 | 683.7359 | 690.4057
|  | Power Factor | 0.94974 | 0.92668 | 0.87244 | 0.69696 | 1
|  | N-1 Load (A) | 92.9081 | 73.9998 | 52.8781 | 30.9073 | 17.0085
|  | N-1 Rating (A) | 704 | 704 | 704 | 704 | 704
|  | Contingency Utilisation (%) | 13.1972 | 10.5113 | 7.5111 | 4.3902 | 2.416
|  | N-1 Hosting Capacity (A) | 611.0919 | 630.0002 | 651.1219 | 673.0927 | 686.9915
|  | N-1 Power Factor | 0.94974 | 0.92668 | 0.87244 | 0.69696 | 1
|  | N-1 Limiting section | 540-1 | 540-1 | 540-1 | 540-1 | 540-1
|  | Contingency Scenario | F622 | F622 | F622 | F622 | F622
F542 | 542-1 | Load (A) | 4.6787 | 30.3025 | 62.498 | 92.5533 | 118.838
|  | Rating (A) | 704 | 704 | 704 | 704 | 704
|  | Utilisation (%) | 0.66459 | 4.3043 | 8.8776 | 13.1468 | 16.8804
|  | Hosting Capacity (A) | 699.3213 | 673.6975 | 641.502 | 611.4467 | 585.162
|  | Power Factor | 0.75133 | 0.99582 | 0.99963 | 0.99979 | 0.99948
F543 | 543-1 | Load (A) | 2.9822 | 2.9833 | 2.9843 | 2.9853 | 2.9863
|  | Rating (A) | 836 | 836 | 836 | 836 | 836
|  | Utilisation (%) | 0.35672 | 0.35685 | 0.35697 | 0.3571 | 0.35721
|  | Hosting Capacity (A) | 833.0178 | 833.0167 | 833.0157 | 833.0147 | 833.0137
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 4.553 | 30.3741 | 62.5959 | 92.5547 | 118.664
|  | N-1 Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Contingency Utilisation (%) | 0.54462 | 3.7132 | 7.6523 | 11.3148 | 14.5066
|  | N-1 Hosting Capacity (A) | 813.447 | 787.6259 | 755.4041 | 725.4453 | 699.336
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 543-1 | 543-1(1) | 543-1(1) | 543-1(1) | 543-1(1)
|  | Contingency Scenario | F542 | F542 | F542 | F542 | F542
F543 | 543-3 | Load (A) | 2.2138 | 2.2146 | 2.2154 | 2.2162 | 2.2169
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 0.2725 | 0.2726 | 0.2727 | 0.27279 | 0.27288
|  | Hosting Capacity (A) | 815.7862 | 815.7854 | 815.7846 | 815.7838 | 815.7831
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 4.1196 | 30.3211 | 62.5925 | 92.5894 | 118.7251
|  | N-1 Rating (A) | 807 | 807 | 807 | 807 | 807
|  | Contingency Utilisation (%) | 0.50361 | 3.7573 | 7.7562 | 11.4733 | 14.7119
|  | N-1 Hosting Capacity (A) | 802.8804 | 776.6789 | 744.4075 | 714.4106 | 688.2749
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 543-3 | 543-3(1) | 543-3(1) | 543-3(1) | 543-3(1)
|  | Contingency Scenario | F542 | F542 | F542 | F542 | F542
F547 | 547-1 | Load (A) | 129.1106 | 129.0817 | 129.0522 | 129.0228 | 128.9953
|  | Rating (A) | 689 | 689 | 689 | 689 | 689
|  | Utilisation (%) | 18.7388 | 18.7346 | 18.7304 | 18.7261 | 18.7221
|  | Hosting Capacity (A) | 559.8894 | 559.9183 | 559.9478 | 559.9772 | 560.0047
|  | Power Factor | 0.99945 | 0.99945 | 0.99945 | 0.99945 | 0.99944
|  | N-1 Load (A) | 129.2131 | 129.1539 | 129.0937 | 129.0384 | 129.0137
|  | N-1 Rating (A) | 689 | 689 | 689 | 689 | 689
|  | Contingency Utilisation (%) | 18.7537 | 18.7451 | 18.7364 | 18.7284 | 18.7248
|  | N-1 Hosting Capacity (A) | 559.7869 | 559.8461 | 559.9063 | 559.9616 | 559.9863
|  | N-1 Power Factor | 0.99945 | 0.99945 | 0.99945 | 0.99945 | 0.99944
|  | N-1 Limiting section | 547-1 | 547-1 | 547-1 | 547-1 | 547-1
|  | Contingency Scenario | F548 | F548 | F548 | F596 | F596
F548 | 548-1 | Load (A) | 137.0186 | 108.5475 | 78.249 | 47.2021 | 20.539
|  | Rating (A) | 836 | 836 | 836 | 836 | 836
|  | Utilisation (%) | 16.3898 | 12.9841 | 9.3599 | 5.6462 | 2.4568
|  | Hosting Capacity (A) | 698.9814 | 727.4525 | 757.751 | 788.7979 | 815.461
|  | Power Factor | 0.98877 | 0.98196 | 0.96657 | 0.91527 | 0.53152
|  | N-1 Load (A) | 272.264 | 215.1214 | 154.1594 | 91.1465 | 55.8487
|  | N-1 Rating (A) | 963 | 963 | 963 | 963 | 963
|  | Contingency Utilisation (%) | 32.5675 | 25.7322 | 18.4401 | 10.9027 | 6.6805
|  | N-1 Hosting Capacity (A) | 690.736 | 747.8786 | 808.8406 | 871.8535 | 907.1513
|  | N-1 Power Factor | 0.98877 | 0.98196 | 0.96657 | 0.91527 | 0.53152
|  | N-1 Limiting section | 548-1 | 548-1 | 548-1 | 548-1 | 548-1
|  | Contingency Scenario | F594 | F594 | F594 | F594 | F547
F548 | 548-1_a | Load (A) | 136.4554 | 107.8357 | 77.2852 | 45.6842 | 17.1582
|  | Rating (A) | 836 | 836 | 836 | 836 | 836
|  | Utilisation (%) | 16.3224 | 12.899 | 9.2446 | 5.4646 | 2.0524
|  | Hosting Capacity (A) | 699.5446 | 728.1643 | 758.7148 | 790.3158 | 818.8418
|  | Power Factor | 0.99262 | 0.98821 | 0.9784 | 0.94546 | 0.63608
|  | N-1 Load (A) | 271.802 | 214.5314 | 153.3564 | 89.8738 | 54.8618
|  | N-1 Rating (A) | 836 | 836 | 836 | 836 | 836
|  | Contingency Utilisation (%) | 32.5122 | 25.6617 | 18.3441 | 10.7505 | 6.5624
|  | N-1 Hosting Capacity (A) | 564.198 | 621.4686 | 682.6436 | 746.1262 | 781.1382
|  | N-1 Power Factor | 0.99262 | 0.98821 | 0.9784 | 0.94546 | 0.63608
|  | N-1 Limiting section | 548-1_a | 548-1_a | 548-1_a | 548-1_a | 548-1_a
|  | Contingency Scenario | F594 | F594 | F594 | F594 | F547
F548 | 548-1_b | Load (A) | 136.4554 | 107.8357 | 77.2852 | 45.6842 | 17.0478
|  | Rating (A) | 836 | 836 | 836 | 836 | 836
|  | Utilisation (%) | 16.3204 | 12.8964 | 9.2411 | 5.4591 | 2.0392
|  | Hosting Capacity (A) | 699.5446 | 728.1643 | 758.7148 | 790.3158 | 818.9522
|  | Power Factor | 0.99262 | 0.98821 | 0.9784 | 0.94546 | 0.6402
|  | N-1 Load (A) | 271.7869 | 214.5123 | 153.3305 | 89.833 | 54.833
|  | N-1 Rating (A) | 836 | 836 | 836 | 836 | 836
|  | Contingency Utilisation (%) | 32.5104 | 25.6594 | 18.341 | 10.7456 | 6.559
|  | N-1 Hosting Capacity (A) | 564.2131 | 621.4877 | 682.6695 | 746.167 | 781.167
|  | N-1 Power Factor | 0.99262 | 0.98821 | 0.9784 | 0.94546 | 0.63608
|  | N-1 Limiting section | 548-1_a | 548-1_a | 548-1_a | 548-1_a | 548-1_a
|  | Contingency Scenario | F594 | F594 | F594 | F594 | F547
F550 | 550-1 | Load (A) | 162.7447 | 147.9847 | 131.8367 | 114.9797 | 98.5415
|  | Rating (A) | 668 | 668 | 668 | 668 | 668
|  | Utilisation (%) | 24.363 | 22.1534 | 19.736 | 17.2125 | 14.7517
|  | Hosting Capacity (A) | 505.2553 | 520.0153 | 536.1633 | 553.0203 | 569.4585
|  | Power Factor | 0.99826 | 0.99862 | 0.99892 | 0.9992 | 0.99891
|  | N-1 Load (A) | 325.6836 | 296.0961 | 263.7401 | 229.9769 | 196.9588
|  | N-1 Rating (A) | 789 | 789 | 789 | 789 | 789
|  | Contingency Utilisation (%) | 48.755 | 44.3258 | 39.4821 | 34.4277 | 29.4848
|  | N-1 Hosting Capacity (A) | 463.3164 | 492.9039 | 525.2599 | 559.0231 | 592.0412
|  | N-1 Power Factor | 0.99826 | 0.99862 | 0.99892 | 0.9992 | 0.99891
|  | N-1 Limiting section | 550-1 | 550-1 | 550-1 | 550-1 | 550-1
|  | Contingency Scenario | F551 | F551 | F551 | F551 | F551
F551 | 551-1 | Load (A) | 162.434 | 147.7022 | 131.585 | 114.7602 | 98.3536
|  | Rating (A) | 668 | 668 | 668 | 668 | 668
|  | Utilisation (%) | 24.3165 | 22.1111 | 19.6984 | 17.1797 | 14.7236
|  | Hosting Capacity (A) | 505.566 | 520.2978 | 536.415 | 553.2398 | 569.6464
|  | Power Factor | 0.99826 | 0.99861 | 0.99891 | 0.99919 | 0.9989
|  | N-1 Load (A) | 325.6855 | 296.0976 | 263.7413 | 229.9778 | 196.9594
|  | N-1 Rating (A) | 789 | 789 | 789 | 789 | 789
|  | Contingency Utilisation (%) | 48.7553 | 44.326 | 39.4822 | 34.4278 | 29.4849
|  | N-1 Hosting Capacity (A) | 463.3145 | 492.9024 | 525.2587 | 559.0222 | 592.0406
|  | N-1 Power Factor | 0.99826 | 0.99861 | 0.99891 | 0.99919 | 0.9989
|  | N-1 Limiting section | 551-1 | 551-1 | 551-1 | 551-1 | 551-1
|  | Contingency Scenario | F550 | F550 | F550 | F550 | F550
F552 | 552-1 | Load (A) | 23.2238 | 26.2477 | 34.2962 | 45.1798 | 57.0374
|  | Rating (A) | 598 | 598 | 598 | 598 | 598
|  | Utilisation (%) | 3.8836 | 4.3892 | 5.7351 | 7.5552 | 9.538
|  | Hosting Capacity (A) | 574.7762 | 571.7523 | 563.7038 | 552.8202 | 540.9626
|  | Power Factor | 1 | 0.50423 | 0.77055 | 0.88807 | 0.9401
|  | N-1 Load (A) | 53.7117 | 42.7644 | 51.9671 | 69.7416 | 88.8536
|  | N-1 Rating (A) | 598 | 598 | 598 | 598 | 598
|  | Contingency Utilisation (%) | 8.9819 | 7.1512 | 8.6901 | 11.6625 | 14.8585
|  | N-1 Hosting Capacity (A) | 544.2883 | 555.2356 | 546.0329 | 528.2584 | 509.1464
|  | N-1 Power Factor | 1 | 0.50423 | 0.77055 | 0.88807 | 0.9401
|  | N-1 Limiting section | 552-1 | 552-1 | 552-1 | 552-1 | 552-1
|  | Contingency Scenario | F547 | F547 | F570 | F570 | F570
F554 | 554-1 | Load (A) | 30.8713 | 25.714 | 47.6683 | 77.4848 | 106.8543
|  | Rating (A) | 716 | 716 | 716 | 716 | 716
|  | Utilisation (%) | 4.3116 | 3.5913 | 6.6576 | 10.8219 | 14.9238
|  | Hosting Capacity (A) | 685.1287 | 690.286 | 668.3317 | 638.5152 | 609.1457
|  | Power Factor | 0.62825 | 0.38644 | 0.87807 | 0.96187 | 0.98412
|  | N-1 Load (A) | 40.3626 | 32.7605 | 64.8576 | 107.0043 | 148.1659
|  | N-1 Rating (A) | 716 | 716 | 716 | 716 | 716
|  | Contingency Utilisation (%) | 5.6372 | 4.5755 | 9.0583 | 14.9447 | 20.6936
|  | N-1 Hosting Capacity (A) | 675.6374 | 683.2395 | 651.1424 | 608.9957 | 567.8341
|  | N-1 Power Factor | 0.62825 | 0.38644 | 0.87807 | 0.96187 | 0.98412
|  | N-1 Limiting section | 554-1 | 554-1 | 554-1 | 554-1 | 554-1
|  | Contingency Scenario | F515 | F515 | F515 | F515 | F515
F556 | 556-1 | Load (A) | 30.4956 | 29.9472 | 29.7192 | 29.411 | 29.584
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 3.7281 | 3.661 | 3.6332 | 3.5955 | 3.6166
|  | Hosting Capacity (A) | 787.5044 | 788.0528 | 788.2808 | 788.589 | 788.416
|  | Power Factor | 0.99614 | 0.99599 | 0.99592 | 0.99583 | 0.99589
|  | N-1 Load (A) | 45.6564 | 44.6807 | 44.264 | 43.7061 | 43.9836
|  | N-1 Rating (A) | 704 | 704 | 704 | 704 | 704
|  | Contingency Utilisation (%) | 5.5815 | 5.4622 | 5.4112 | 5.343 | 5.377
|  | N-1 Hosting Capacity (A) | 658.3436 | 659.3193 | 659.736 | 660.2939 | 660.0164
|  | N-1 Power Factor | 0.99614 | 0.99599 | 0.99592 | 0.99583 | 0.99589
|  | N-1 Limiting section | 556-1 | 556-1 | 556-1 | 556-1 | 556-1
|  | Contingency Scenario | F506 | F506 | F506 | F506 | F506
F558 | 558-1 | Load (A) | 12.3574 | 30.6821 | 49.6944 | 69.029 | 87.737
|  | Rating (A) | 680 | 680 | 680 | 680 | 680
|  | Utilisation (%) | 1.8173 | 4.5121 | 7.308 | 10.1513 | 12.9025
|  | Hosting Capacity (A) | 667.6426 | 649.3179 | 630.3056 | 610.971 | 592.263
|  | Power Factor | 0.99997 | 0.99993 | 0.99981 | 0.99962 | 0.99935
|  | N-1 Load (A) | 19.8451 | 51.641 | 84.4556 | 117.7228 | 149.8328
|  | N-1 Rating (A) | 680 | 680 | 680 | 680 | 680
|  | Contingency Utilisation (%) | 2.9184 | 7.5943 | 12.4199 | 17.3122 | 22.0342
|  | N-1 Hosting Capacity (A) | 660.1549 | 628.359 | 595.5444 | 562.2772 | 530.1672
|  | N-1 Power Factor | 0.99997 | 0.99993 | 0.99981 | 0.99962 | 0.99935
|  | N-1 Limiting section | 558-1 | 558-1 | 558-1 | 558-1 | 558-1
|  | Contingency Scenario | F414 | F414 | F414 | F414 | F414
F560 | 560-1 | Load (A) | 23.5441 | 35.3446 | 47.579 | 60.0284 | 72.1386
|  | Rating (A) | 527 | 527 | 527 | 527 | 527
|  | Utilisation (%) | 4.4676 | 6.7068 | 9.0283 | 11.3906 | 13.6885
|  | Hosting Capacity (A) | 503.4559 | 491.6554 | 479.421 | 466.9716 | 454.8614
|  | Power Factor | 0.99602 | 0.99989 | 0.99951 | 0.99811 | 0.99633
|  | N-1 Load (A) | 71.3969 | 107.1685 | 144.0132 | 181.3461 | 217.5421
|  | N-1 Rating (A) | 527 | 527 | 527 | 527 | 527
|  | Contingency Utilisation (%) | 13.5478 | 20.3356 | 27.327 | 34.411 | 41.2793
|  | N-1 Hosting Capacity (A) | 455.6031 | 419.8315 | 382.9868 | 345.6539 | 309.4579
|  | N-1 Power Factor | 0.99602 | 0.99989 | 0.99951 | 0.99811 | 0.99633
|  | N-1 Limiting section | 560-1(1) | 560-1(1) | 560-1(1) | 560-1(1) | 560-1(1)
|  | Contingency Scenario | F569 | F569 | F569 | F569 | F569
F560 | 560-14 | Load (A) | 9.6918 | 14.6156 | 19.6897 | 24.8402 | 29.8454
|  | Rating (A) | 367 | 367 | 367 | 367 | 367
|  | Utilisation (%) | 2.6408 | 3.9825 | 5.365 | 6.7685 | 8.1323
|  | Hosting Capacity (A) | 357.3082 | 352.3844 | 347.3103 | 342.1598 | 337.1546
|  | Power Factor | 0.9983 | 0.99678 | 0.9953 | 0.99387 | 0.99246
|  | N-1 Load (A) | 29.2414 | 44.0356 | 59.2392 | 74.6329 | 89.5498
|  | N-1 Rating (A) | 367 | 367 | 367 | 367 | 367
|  | Contingency Utilisation (%) | 7.9677 | 11.9988 | 16.1415 | 20.3359 | 24.4005
|  | N-1 Hosting Capacity (A) | 337.7586 | 322.9644 | 307.7608 | 292.3671 | 277.4502
|  | N-1 Power Factor | 0.9983 | 0.99678 | 0.9953 | 0.99387 | 0.99246
|  | N-1 Limiting section | 560-14(2) | 560-14(2) | 560-14(2) | 560-14(2) | 560-14(2)
|  | Contingency Scenario | F569 | F569 | F569 | F569 | F569
F560 | 560-15 | Load (A) | 13.7756 | 20.7784 | 28.0109 | 35.3598 | 42.5044
|  | Rating (A) | 351 | 351 | 351 | 351 | 351
|  | Utilisation (%) | 3.9247 | 5.9198 | 7.9803 | 10.074 | 12.1095
|  | Hosting Capacity (A) | 337.2244 | 330.2216 | 322.9891 | 315.6402 | 308.4956
|  | Power Factor | 0.99959 | 0.99972 | 0.99849 | 0.997 | 0.99548
|  | N-1 Load (A) | 41.8825 | 62.9944 | 84.7155 | 106.7153 | 128.0383
|  | N-1 Rating (A) | 351 | 351 | 351 | 351 | 351
|  | Contingency Utilisation (%) | 11.9323 | 17.9471 | 24.1355 | 30.4032 | 36.4781
|  | N-1 Hosting Capacity (A) | 309.1175 | 288.0056 | 266.2845 | 244.2847 | 222.9617
|  | N-1 Power Factor | 0.99959 | 0.99972 | 0.99849 | 0.997 | 0.99548
|  | N-1 Limiting section | 560-15(6) | 560-15(6) | 560-15(6) | 560-15(6) | 560-15(6)
|  | Contingency Scenario | F569 | F569 | F569 | F569 | F569
F560 | 560-16 | Load (A) | 25.3719 | 37.0646 | 49.2992 | 61.7897 | 73.9642
|  | Rating (A) | 983 | 983 | 983 | 983 | 983
|  | Utilisation (%) | 2.5811 | 3.7706 | 5.0152 | 6.2858 | 7.5243
|  | Hosting Capacity (A) | 957.6281 | 945.9354 | 933.7008 | 921.2103 | 909.0358
|  | Power Factor | 0.92411 | 0.95356 | 0.96491 | 0.97019 | 0.97265
|  | N-1 Load (A) | 70.716 | 106.915 | 144.0275 | 181.5856 | 217.9563
|  | N-1 Rating (A) | 983 | 983 | 983 | 983 | 983
|  | Contingency Utilisation (%) | 7.1939 | 10.8764 | 14.6518 | 18.4726 | 22.1726
|  | N-1 Hosting Capacity (A) | 912.284 | 876.085 | 838.9725 | 801.4144 | 765.0437
|  | N-1 Power Factor | 0.92411 | 0.95356 | 0.96491 | 0.97019 | 0.97265
|  | N-1 Limiting section | 560-16 | 560-16 | 560-16 | 560-16 | 560-16
|  | Contingency Scenario | F569 | F569 | F569 | F569 | F569
F560 | 560-3 | Load (A) | 23.4851 | 35.3413 | 47.6101 | 60.0963 | 72.2275
|  | Rating (A) | 600 | 600 | 600 | 600 | 600
|  | Utilisation (%) | 3.9142 | 5.8906 | 7.9366 | 10.016 | 12.0379
|  | Hosting Capacity (A) | 576.5149 | 564.6587 | 552.3899 | 539.9037 | 527.7725
|  | Power Factor | 0.9983 | 0.99995 | 0.99896 | 0.99725 | 0.99567
|  | N-1 Load (A) | 71.2926 | 107.1158 | 143.9914 | 181.3462 | 217.5628
|  | N-1 Rating (A) | 600 | 600 | 600 | 600 | 600
|  | Contingency Utilisation (%) | 11.8821 | 17.8526 | 23.9986 | 30.2244 | 36.2605
|  | N-1 Hosting Capacity (A) | 528.7074 | 492.8842 | 456.0086 | 418.6538 | 382.4372
|  | N-1 Power Factor | 0.9983 | 0.99995 | 0.99896 | 0.99749 | 0.99592
|  | N-1 Limiting section | 560-3 | 560-3 | 560-3 | 560-3 | 560-3
|  | Contingency Scenario | F569 | F569 | F569 | F569 | F569
F560 | 560-5 | Load (A) | 13.7748 | 20.7826 | 28.0197 | 35.3719 | 42.47
|  | Rating (A) | 704 | 704 | 704 | 704 | 704
|  | Utilisation (%) | 1.9636 | 2.951 | 3.9762 | 5.0188 | 6.0327
|  | Hosting Capacity (A) | 690.2252 | 683.2174 | 675.9803 | 668.6281 | 661.53
|  | Power Factor | 0.99965 | 0.99952 | 0.99818 | 0.99666 | 0.99608
|  | N-1 Load (A) | 41.9893 | 63.051 | 84.7427 | 106.7199 | 128.0325
|  | N-1 Rating (A) | 704 | 704 | 704 | 704 | 704
|  | Contingency Utilisation (%) | 5.9644 | 8.9561 | 12.0373 | 15.1591 | 18.1864
|  | N-1 Hosting Capacity (A) | 662.0107 | 640.949 | 619.2573 | 597.2801 | 575.9675
|  | N-1 Power Factor | 0.99614 | 0.90442 | 0.99907 | 0.99666 | 0.99514
|  | N-1 Limiting section | 560-5 | 560-15(7) | 560-5 | 560-15(2) | 560-15(2)
|  | Contingency Scenario | F569 | F569 | F569 | F569 | F569
F561 | 561-1 | Load (A) | 14.3168 | 21.9904 | 29.9535 | 38.0847 | 46.033
|  | Rating (A) | 786 | 786 | 786 | 786 | 786
|  | Utilisation (%) | 1.8215 | 2.7978 | 3.8109 | 4.8454 | 5.8566
|  | Hosting Capacity (A) | 771.6832 | 764.0096 | 756.0465 | 747.9153 | 739.967
|  | Power Factor | 0.9919 | 0.99608 | 0.99774 | 0.9986 | 0.99911
|  | N-1 Load (A) | 27.8219 | 42.9032 | 58.5312 | 74.4576 | 90.0414
|  | N-1 Rating (A) | 786 | 786 | 786 | 786 | 786
|  | Contingency Utilisation (%) | 3.5397 | 5.4584 | 7.4467 | 9.473 | 11.4556
|  | N-1 Hosting Capacity (A) | 758.1781 | 743.0968 | 727.4688 | 711.5424 | 695.9586
|  | N-1 Power Factor | 0.9919 | 0.99608 | 0.99774 | 0.9986 | 0.99943
|  | N-1 Limiting section | 561-1 | 561-1 | 561-1 | 561-1 | 561-1(3)
|  | Contingency Scenario | F656 | F656 | F656 | F656 | F656
F563 | 563-1 | Load (A) | 9.9388 | 13.735 | 24.2727 | 35.6145 | 46.4493
|  | Rating (A) | 371 | 371 | 371 | 371 | 371
|  | Utilisation (%) | 2.6789 | 3.7022 | 6.5425 | 9.5996 | 12.52
|  | Hosting Capacity (A) | 361.0612 | 357.265 | 346.7273 | 335.3855 | 324.5507
|  | Power Factor | 0.29954 | 0.73985 | 0.93194 | 0.97339 | 0.98737
|  | N-1 Load (A) | 13.1854 | 22.7016 | 43.6057 | 65.9647 | 86.9273
|  | N-1 Rating (A) | 429 | 429 | 429 | 429 | 429
|  | Contingency Utilisation (%) | 3.554 | 6.119 | 11.7536 | 17.7802 | 23.4305
|  | N-1 Hosting Capacity (A) | 415.8146 | 406.2984 | 385.3943 | 363.0353 | 342.0727
|  | N-1 Power Factor | 0.29954 | 0.73985 | 0.93194 | 0.97339 | 0.98737
|  | N-1 Limiting section | 563-1(2) | 563-1(2) | 563-1(2) | 563-1(2) | 563-1(2)
|  | Contingency Scenario | F558 | F414 | F564 | F564 | F564
F564 | 564-1 | Load (A) | 9.8323 | 13.5315 | 23.5739 | 34.4265 | 44.8097
|  | Rating (A) | 371 | 371 | 371 | 371 | 371
|  | Utilisation (%) | 2.6502 | 3.6473 | 6.3542 | 9.2794 | 12.0781
|  | Hosting Capacity (A) | 361.1677 | 357.4685 | 347.4261 | 336.5735 | 326.1903
|  | Power Factor | 0.29133 | 0.721 | 0.92165 | 0.9674 | 0.98344
|  | N-1 Load (A) | 12.8089 | 22.0743 | 43.5177 | 65.7909 | 86.6798
|  | N-1 Rating (A) | 429 | 429 | 429 | 429 | 429
|  | Contingency Utilisation (%) | 3.4525 | 5.9499 | 11.7298 | 17.7334 | 23.3638
|  | N-1 Hosting Capacity (A) | 416.1911 | 406.9257 | 385.4823 | 363.2091 | 342.3202
|  | N-1 Power Factor | 0.29133 | 0.721 | 0.92165 | 0.9674 | 0.98344
|  | N-1 Limiting section | 564-1(1) | 564-1(1) | 564-1(1) | 564-1(1) | 564-1(1)
|  | Contingency Scenario | F558 | F414 | F563 | F563 | F563
F565 | 565-1 | Load (A) | 17.1742 | 19.2933 | 24.6814 | 32.0079 | 40.0424
|  | Rating (A) | 851 | 851 | 851 | 851 | 851
|  | Utilisation (%) | 2.0181 | 2.2671 | 2.9003 | 3.7612 | 4.7053
|  | Hosting Capacity (A) | 833.8258 | 831.7067 | 826.3186 | 818.9921 | 810.9576
|  | Power Factor | 1 | 0.37125 | 0.65733 | 0.80151 | 0.87341
|  | N-1 Load (A) | 37.1116 | 29.742 | 37.2825 | 49.5069 | 62.7122
|  | N-1 Rating (A) | 851 | 851 | 851 | 851 | 851
|  | Contingency Utilisation (%) | 4.3609 | 3.495 | 4.381 | 5.8175 | 7.3692
|  | N-1 Hosting Capacity (A) | 813.8884 | 821.258 | 813.7175 | 801.4931 | 788.2878
|  | N-1 Power Factor | 1 | 0.37125 | 0.65733 | 0.80151 | 0.87341
|  | N-1 Limiting section | 565-1(1) | 565-1(1) | 565-1(1) | 565-1(1) | 565-1(1)
|  | Contingency Scenario | F547 | F547 | F552 | F552 | F552
F567 | 567-1 | Load (A) | 32.5061 | 19.3083 | 16.7979 | 30.0085 | 47.2807
|  | Rating (A) | 576 | 576 | 576 | 576 | 576
|  | Utilisation (%) | 5.6434 | 3.3521 | 2.9163 | 5.2098 | 8.2085
|  | Hosting Capacity (A) | 543.4939 | 556.6917 | 559.2021 | 545.9915 | 528.7193
|  | Power Factor | 0.88619 | 0.60476 | 0.39899 | 0.86453 | 0.95241
|  | N-1 Load (A) | 59.664 | 27.9781 | 20.3977 | 54.1012 | 91.3411
|  | N-1 Rating (A) | 643 | 643 | 643 | 643 | 643
|  | Contingency Utilisation (%) | 10.3583 | 4.8573 | 3.5413 | 9.3926 | 15.8578
|  | N-1 Hosting Capacity (A) | 583.336 | 615.0219 | 622.6023 | 588.8988 | 551.6589
|  | N-1 Power Factor | 0.88619 | 0.60476 | 0.39899 | 0.86453 | 0.95241
|  | N-1 Limiting section | 567-1 | 567-1 | 567-1 | 567-1 | 567-1
|  | Contingency Scenario | F568 | F568 | F568 | F568 | F568
F568 | 568-1 | Load (A) | 32.6722 | 19.331 | 16.8041 | 30.1848 | 47.6195
|  | Rating (A) | 576 | 576 | 576 | 576 | 576
|  | Utilisation (%) | 5.6723 | 3.3561 | 2.9174 | 5.2404 | 8.2673
|  | Hosting Capacity (A) | 543.3278 | 556.669 | 559.1959 | 545.8152 | 528.3805
|  | Power Factor | 0.88881 | 0.60934 | 0.40116 | 0.86568 | 0.95268
|  | N-1 Load (A) | 59.6205 | 27.8813 | 20.2639 | 54.0532 | 91.3161
|  | N-1 Rating (A) | 643 | 643 | 643 | 643 | 643
|  | Contingency Utilisation (%) | 10.3508 | 4.8405 | 3.518 | 9.3842 | 15.8535
|  | N-1 Hosting Capacity (A) | 583.3795 | 615.1187 | 622.7361 | 588.9468 | 551.6839
|  | N-1 Power Factor | 0.88881 | 0.60934 | 0.40116 | 0.86568 | 0.95268
|  | N-1 Limiting section | 568-1 | 568-1 | 568-1 | 568-1 | 568-1
|  | Contingency Scenario | F567 | F567 | F567 | F567 | F567
F569 | 569-1 | Load (A) | 48.4191 | 72.8763 | 98.1699 | 123.8869 | 148.8963
|  | Rating (A) | 582 | 582 | 582 | 582 | 582
|  | Utilisation (%) | 8.3194 | 12.5217 | 16.8677 | 21.2864 | 25.5836
|  | Hosting Capacity (A) | 533.5809 | 509.1237 | 483.8301 | 458.1131 | 433.1037
|  | Power Factor | 0.98563 | 0.9943 | 0.99767 | 0.99917 | 0.99982
|  | N-1 Load (A) | 71.1608 | 107.7853 | 145.505 | 183.7765 | 220.9586
|  | N-1 Rating (A) | 582 | 582 | 582 | 582 | 582
|  | Contingency Utilisation (%) | 12.2269 | 18.5198 | 25.0009 | 31.5767 | 37.9654
|  | N-1 Hosting Capacity (A) | 510.8392 | 474.2147 | 436.495 | 398.2235 | 361.0414
|  | N-1 Power Factor | 0.98563 | 0.9943 | 0.99767 | 0.99917 | 0.99982
|  | N-1 Limiting section | 569-1(5) | 569-1(5) | 569-1(5) | 569-1(5) | 569-1(5)
|  | Contingency Scenario | F560 | F560 | F560 | F560 | F560
F570 | 570-1 | Load (A) | 22.8183 | 25.7536 | 33.5843 | 44.1907 | 55.7562
|  | Rating (A) | 598 | 598 | 598 | 598 | 598
|  | Utilisation (%) | 3.8158 | 4.3066 | 5.6161 | 7.3897 | 9.3238
|  | Hosting Capacity (A) | 575.1817 | 572.2464 | 564.4157 | 553.8093 | 542.2438
|  | Power Factor | 1 | 0.50195 | 0.76857 | 0.88681 | 0.93932
|  | N-1 Load (A) | 52.5242 | 41.8459 | 51.5471 | 69.1262 | 88.0387
|  | N-1 Rating (A) | 672 | 672 | 672 | 672 | 672
|  | Contingency Utilisation (%) | 8.7833 | 6.9976 | 8.6199 | 11.5596 | 14.7222
|  | N-1 Hosting Capacity (A) | 619.4758 | 630.1541 | 620.4529 | 602.8738 | 583.9613
|  | N-1 Power Factor | 1 | 0.50195 | 0.76857 | 0.88681 | 0.93932
|  | N-1 Limiting section | 570-1 | 570-1 | 570-1 | 570-1 | 570-1
|  | Contingency Scenario | F547 | F547 | F552 | F552 | F552
F571 | 571-1 | Load (A) | 31.6427 | 54.9883 | 78.5985 | 102.3041 | 125.2306
|  | Rating (A) | 527 | 527 | 527 | 527 | 527
|  | Utilisation (%) | 6.0043 | 10.4342 | 14.9143 | 19.4127 | 23.7632
|  | Hosting Capacity (A) | 495.3573 | 472.0117 | 448.4015 | 424.6959 | 401.7694
|  | Power Factor | 0.99833 | 0.99966 | 0.99998 | 0.99994 | 0.99968
|  | N-1 Load (A) | 45.9312 | 87.0115 | 128.8494 | 170.8463 | 211.1841
|  | N-1 Rating (A) | 527 | 527 | 527 | 527 | 527
|  | Contingency Utilisation (%) | 8.7156 | 16.5107 | 24.4496 | 32.4186 | 40.0729
|  | N-1 Hosting Capacity (A) | 481.0688 | 439.9885 | 398.1506 | 356.1537 | 315.8159
|  | N-1 Power Factor | 0.99833 | 0.99966 | 0.99998 | 0.99994 | 0.99968
|  | N-1 Limiting section | 571-1(5) | 571-1(5) | 571-1(5) | 571-1(5) | 571-1(5)
|  | Contingency Scenario | F539 | F539 | F539 | F539 | F539
F575 | 575C-1 | Load (A) | 49.0351 | 41.095 | 32.8017 | 25.2031 | 19.229
|  | Rating (A) | 355 | 355 | 355 | 355 | 355
|  | Utilisation (%) | 13.8127 | 11.5761 | 9.2399 | 7.0995 | 5.4166
|  | Hosting Capacity (A) | 305.9649 | 313.905 | 322.1983 | 329.7969 | 335.771
|  | Power Factor | 0.99706 | 0.99486 | 0.99047 | 0.98184 | 0.96632
|  | N-1 Load (A) | 100.9068 | 84.3367 | 67.0105 | 51.0648 | 38.4477
|  | N-1 Rating (A) | 475 | 475 | 475 | 475 | 475
|  | Contingency Utilisation (%) | 28.4245 | 23.7568 | 18.8762 | 14.3844 | 10.8303
|  | N-1 Hosting Capacity (A) | 374.0932 | 390.6633 | 407.9895 | 423.9352 | 436.5523
|  | N-1 Power Factor | 0.99706 | 0.99486 | 0.99047 | 0.98184 | 0.96632
|  | N-1 Limiting section | 575C-1 | 575C-1 | 575C-1 | 575C-1 | 575C-1
|  | Contingency Scenario | F416 | F416 | F416 | F416 | F416
F581 | 581-1 | Load (A) | 129.6733 | 104.4305 | 76.9897 | 47.7846 | 18.5303
|  | Rating (A) | 661 | 661 | 661 | 661 | 661
|  | Utilisation (%) | 19.6178 | 15.7989 | 11.6474 | 7.2291 | 2.8034
|  | Hosting Capacity (A) | 531.3267 | 556.5695 | 584.0103 | 613.2154 | 642.4697
|  | Power Factor | 0.99957 | 0.99899 | 0.99771 | 0.99402 | 0.96777
|  | N-1 Load (A) | 247.7107 | 199.3276 | 146.7398 | 90.7568 | 52.435
|  | N-1 Rating (A) | 785 | 785 | 785 | 785 | 785
|  | Contingency Utilisation (%) | 37.4751 | 30.1555 | 22.1997 | 13.7302 | 7.9327
|  | N-1 Hosting Capacity (A) | 537.2893 | 585.6724 | 638.2602 | 694.2432 | 732.565
|  | N-1 Power Factor | 0.99957 | 0.99899 | 0.99771 | 0.99402 | 0.96777
|  | N-1 Limiting section | 581-1 | 581-1 | 581-1 | 581-1 | 581-1
|  | Contingency Scenario | F677 | F677 | F677 | F677 | F446C
F584 | 584-4 | Load (A) | 2.2095 | 2.2095 | 2.2095 | 2.2095 | 2.2095
|  | Rating (A) | 721 | 721 | 721 | 721 | 721
|  | Utilisation (%) | 0.30645 | 0.30645 | 0.30645 | 0.30645 | 0.30645
|  | Hosting Capacity (A) | 718.7905 | 718.7905 | 718.7905 | 718.7905 | 718.7905
|  | Power Factor | 1 | 1 | 1 | 1 | 1
F585 | 585-1 | Load (A) | 17.1757 | 27.1865 | 38.1046 | 49.374 | 60.3683
|  | Rating (A) | 622 | 622 | 622 | 622 | 622
|  | Utilisation (%) | 2.7614 | 4.3708 | 6.1261 | 7.9379 | 9.7055
|  | Hosting Capacity (A) | 604.8243 | 594.8135 | 583.8954 | 572.626 | 561.6317
|  | Power Factor | 0.84579 | 0.94444 | 0.97439 | 0.98658 | 0.99237
F586 | 586-1 | Load (A) | 17.2023 | 27.2031 | 38.1139 | 49.3777 | 60.3676
|  | Rating (A) | 622 | 622 | 622 | 622 | 622
|  | Utilisation (%) | 2.7656 | 4.3735 | 6.1276 | 7.9385 | 9.7054
|  | Hosting Capacity (A) | 604.7977 | 594.7969 | 583.8861 | 572.6223 | 561.6324
|  | Power Factor | 0.84532 | 0.94439 | 0.9745 | 0.98676 | 0.99258
F590 | 590-1 | Load (A) | 124.7993 | 109.6686 | 92.48 | 73.3754 | 53.4358
|  | Rating (A) | 705 | 705 | 705 | 705 | 705
|  | Utilisation (%) | 17.703 | 15.5558 | 13.1193 | 10.4099 | 7.5823
|  | Hosting Capacity (A) | 580.2007 | 595.3314 | 612.52 | 631.6246 | 651.5642
|  | Power Factor | 0.99835 | 0.99724 | 0.99553 | 0.99221 | 0.98521
|  | N-1 Load (A) | 249.4791 | 219.0256 | 184.4613 | 146.0017 | 105.7857
|  | N-1 Rating (A) | 705 | 705 | 705 | 705 | 705
|  | Contingency Utilisation (%) | 35.3871 | 31.0675 | 26.1647 | 20.7095 | 15.0051
|  | N-1 Hosting Capacity (A) | 455.5209 | 485.9744 | 520.5387 | 558.9983 | 599.2143
|  | N-1 Power Factor | 0.99835 | 0.99731 | 0.99553 | 0.99221 | 0.98485
|  | N-1 Limiting section | 590-1(1) | 590-1(1) | 590-1(1) | 590-1(1) | 590-1(6)
|  | Contingency Scenario | F591 | F591 | F591 | F591 | F591
F591 | 591-1 | Load (A) | 124.76 | 109.6258 | 92.4512 | 73.3654 | 53.4202
|  | Rating (A) | 705 | 705 | 705 | 705 | 705
|  | Utilisation (%) | 17.6973 | 15.5508 | 13.115 | 10.4064 | 7.5798
|  | Hosting Capacity (A) | 580.24 | 595.3742 | 612.5488 | 631.6346 | 651.5798
|  | Power Factor | 0.99836 | 0.99732 | 0.99554 | 0.99204 | 0.9852
|  | N-1 Load (A) | 249.4788 | 219.0253 | 184.4611 | 146.0015 | 105.7854
|  | N-1 Rating (A) | 705 | 705 | 705 | 705 | 705
|  | Contingency Utilisation (%) | 35.3871 | 31.0674 | 26.1647 | 20.7094 | 15.005
|  | N-1 Hosting Capacity (A) | 455.5212 | 485.9747 | 520.5389 | 558.9985 | 599.2146
|  | N-1 Power Factor | 0.99836 | 0.99732 | 0.99554 | 0.99221 | 0.98489
|  | N-1 Limiting section | 591-1(1) | 591-1(1) | 591-1(1) | 591-1(1) | 591-1(6)
|  | Contingency Scenario | F590 | F590 | F590 | F590 | F590
F593 | 593-1 | Load (A) | 128.8825 | 99.5992 | 68.0384 | 36.0246 | 19.1435
|  | Rating (A) | 696 | 696 | 696 | 696 | 696
|  | Utilisation (%) | 18.5176 | 14.3102 | 9.7756 | 5.176 | 2.7505
|  | Hosting Capacity (A) | 567.1175 | 596.4008 | 627.9616 | 659.9754 | 676.8565
|  | Power Factor | 0.98855 | 0.98007 | 0.95664 | 0.84214 | 0.24618
|  | N-1 Load (A) | 170.7242 | 132.2096 | 90.3687 | 47.2606 | 22.5791
|  | N-1 Rating (A) | 696 | 696 | 696 | 696 | 696
|  | Contingency Utilisation (%) | 24.5293 | 18.9956 | 12.984 | 6.7903 | 3.2441
|  | N-1 Hosting Capacity (A) | 525.2758 | 563.7904 | 605.6313 | 648.7394 | 673.4209
|  | N-1 Power Factor | 0.98855 | 0.98007 | 0.95664 | 0.84214 | 0.24618
|  | N-1 Limiting section | 593-1 | 593-1 | 593-1 | 593-1 | 593-1
|  | Contingency Scenario | F622 | F622 | F622 | F622 | F622
F594 | 594-1 | Load (A) | 136.1634 | 107.8736 | 77.7694 | 46.9255 | 20.453
|  | Rating (A) | 836 | 836 | 836 | 836 | 836
|  | Utilisation (%) | 16.2875 | 12.9035 | 9.3026 | 5.6131 | 2.4465
|  | Hosting Capacity (A) | 699.8366 | 728.1264 | 758.2306 | 789.0745 | 815.547
|  | Power Factor | 0.98871 | 0.98187 | 0.96641 | 0.91486 | 0.5304
|  | N-1 Load (A) | 272.2724 | 215.1303 | 154.1704 | 91.1632 | 55.5109
|  | N-1 Rating (A) | 963 | 963 | 963 | 963 | 963
|  | Contingency Utilisation (%) | 32.5685 | 25.7333 | 18.4414 | 10.9047 | 6.6401
|  | N-1 Hosting Capacity (A) | 690.7276 | 747.8697 | 808.8296 | 871.8368 | 907.4891
|  | N-1 Power Factor | 0.98871 | 0.98187 | 0.96641 | 0.91486 | 0.5304
|  | N-1 Limiting section | 594-1 | 594-1 | 594-1 | 594-1 | 594-1
|  | Contingency Scenario | F548 | F548 | F548 | F548 | F547
F594 | 594-1_a | Load (A) | 135.5991 | 107.1604 | 76.8037 | 45.4046 | 17.0694
|  | Rating (A) | 836 | 836 | 836 | 836 | 836
|  | Utilisation (%) | 16.22 | 12.8182 | 9.187 | 5.4312 | 2.0418
|  | Hosting Capacity (A) | 700.4009 | 728.8396 | 759.1963 | 790.5954 | 818.9306
|  | Power Factor | 0.9926 | 0.98818 | 0.97833 | 0.9453 | 0.63537
|  | N-1 Load (A) | 271.8097 | 214.5395 | 153.3661 | 89.8885 | 54.5213
|  | N-1 Rating (A) | 836 | 836 | 836 | 836 | 836
|  | Contingency Utilisation (%) | 32.5131 | 25.6626 | 18.3452 | 10.7522 | 6.5217
|  | N-1 Hosting Capacity (A) | 564.1903 | 621.4605 | 682.6339 | 746.1115 | 781.4787
|  | N-1 Power Factor | 0.9926 | 0.98818 | 0.97833 | 0.9453 | 0.63537
|  | N-1 Limiting section | 594-1_a | 594-1_a | 594-1_a | 594-1_a | 594-1_a
|  | Contingency Scenario | F548 | F548 | F548 | F548 | F547
F594 | 594-1_b | Load (A) | 135.5991 | 107.1604 | 76.7741 | 45.4046 | 16.9589
|  | Rating (A) | 836 | 836 | 836 | 836 | 836
|  | Utilisation (%) | 16.2179 | 12.8156 | 9.1835 | 5.4256 | 2.0286
|  | Hosting Capacity (A) | 700.4009 | 728.8396 | 759.2259 | 790.5954 | 819.0411
|  | Power Factor | 0.9926 | 0.98818 | 0.9787 | 0.9453 | 0.6395
|  | N-1 Load (A) | 271.7947 | 214.5203 | 153.3401 | 89.8475 | 54.4925
|  | N-1 Rating (A) | 836 | 836 | 836 | 836 | 836
|  | Contingency Utilisation (%) | 32.5113 | 25.6603 | 18.3421 | 10.7473 | 6.5182
|  | N-1 Hosting Capacity (A) | 564.2053 | 621.4797 | 682.6599 | 746.1525 | 781.5075
|  | N-1 Power Factor | 0.9926 | 0.98818 | 0.9787 | 0.9453 | 0.63537
|  | N-1 Limiting section | 594-1_a | 594-1_a | 594-1_b | 594-1_a | 594-1_a
|  | Contingency Scenario | F548 | F548 | F548 | F548 | F547
F595 | 595-1 | Load (A) | 8.0284 | 17.9791 | 32.8791 | 48.7706 | 64.4686
|  | Rating (A) | 720 | 720 | 720 | 720 | 720
|  | Utilisation (%) | 1.1151 | 2.4971 | 4.5665 | 6.7737 | 8.954
|  | Hosting Capacity (A) | 711.9716 | 702.0209 | 687.1209 | 671.2294 | 655.5314
|  | Power Factor | 0.99996 | 0.90029 | 0.97413 | 0.99037 | 0.99592
|  | N-1 Load (A) | 8.1989 | 33.3041 | 64.5119 | 96.9519 | 128.9594
|  | N-1 Rating (A) | 720 | 720 | 720 | 720 | 720
|  | Contingency Utilisation (%) | 1.1387 | 4.6256 | 8.96 | 13.4655 | 17.911
|  | N-1 Hosting Capacity (A) | 711.8011 | 686.6959 | 655.4881 | 623.0481 | 591.0406
|  | N-1 Hosting Capacity (A) | -718.8613 | -715.3744 | -711.04 | -706.5345 | -702.089
|  | N-1 Power Factor | 0.99996 | 0.90029 | 0.97413 | 0.99037 | 0.99592
|  | N-1 Limiting section | 595-1 | 595-1 | 595-1 | 595-1 | 595-1
|  | Contingency Scenario | F596 | F596 | F596 | F596 | F596
F596 | 596-1 | Load (A) | 7.9939 | 18.0615 | 33.0803 | 49.0863 | 64.8941
|  | Rating (A) | 720 | 720 | 720 | 720 | 720
|  | Utilisation (%) | 1.1103 | 2.5085 | 4.5945 | 6.8175 | 9.0131
|  | Hosting Capacity (A) | 712.0061 | 701.9385 | 686.9197 | 670.9137 | 655.1059
|  | Power Factor | 0.99943 | 0.90232 | 0.97477 | 0.99065 | 0.99606
|  | N-1 Load (A) | 8.1593 | 33.2959 | 64.5092 | 96.9507 | 128.9561
|  | N-1 Rating (A) | 720 | 720 | 720 | 720 | 720
|  | Contingency Utilisation (%) | 1.1332 | 4.6244 | 8.9596 | 13.4654 | 17.9106
|  | N-1 Hosting Capacity (A) | 711.8407 | 686.7041 | 655.4908 | 623.0493 | 591.0439
|  | N-1 Power Factor | 0.99943 | 0.90232 | 0.97477 | 0.99065 | 0.99606
|  | N-1 Limiting section | 596-1 | 596-1 | 596-1 | 596-1 | 596-1
|  | Contingency Scenario | F595 | F595 | F595 | F595 | F595
F597 | 597-1 | Load (A) | 10.5319 | 29.5234 | 49.896 | 70.9942 | 91.3575
|  | Rating (A) | 700 | 700 | 700 | 700 | 700
|  | Utilisation (%) | 1.5046 | 4.2176 | 7.1327 | 10.142 | 13.0511
|  | Hosting Capacity (A) | 689.4681 | 670.4766 | 650.104 | 629.0058 | 608.6425
|  | Power Factor | 0.9459 | 0.99472 | 0.99969 | 0.99937 | 0.99896
|  | N-1 Load (A) | 10.5323
|  | N-1 Rating (A) | 700 | 700 | 700 | 700 | 700
F599 | 599-1 | Load (A) | 1.7547 | 1.7547 | 1.7548 | 1.7549 | 1.755
|  | Rating (A) | 443 | 443 | 443 | 443 | 443
|  | Utilisation (%) | 0.39608 | 0.39611 | 0.39613 | 0.39615 | 0.39617
|  | Hosting Capacity (A) | 441.2453 | 441.2453 | 441.2452 | 441.2451 | 441.245
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 1.755 | 1.7553 | 1.7556 | 1.7559 | 1.7562
|  | N-1 Rating (A) | 443 | 443 | 443 | 443 | 443
|  | Contingency Utilisation (%) | 0.39615 | 0.39623 | 0.3963 | 0.39637 | 0.39644
|  | N-1 Hosting Capacity (A) | 441.245 | 441.2447 | 441.2444 | 441.2441 | 441.2438
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 599-1(7) | 599-1(7) | 599-1(7) | 599-1(7) | 599-1(7)
|  | Contingency Scenario | F688 | F688 | F688 | F688 | F688
F604 | 604-1 | Load (A) | 39.5892 | 30.9904 | 24.0422 | 19.6135 | 18.4551
|  | Rating (A) | 432 | 432 | 432 | 432 | 432
|  | Utilisation (%) | 9.1642 | 7.1737 | 5.5653 | 4.5402 | 4.272
|  | Hosting Capacity (A) | 392.4108 | 401.0096 | 407.9578 | 412.3865 | 413.5449
|  | Power Factor | 0.88633 | 0.80226 | 0.63569 | 0.3292 | 0.73189
|  | N-1 Load (A) | 55.8599 | 41.6792 | 29.8891 | 21.7259 | 19.5767
|  | N-1 Rating (A) | 491 | 491 | 491 | 491 | 491
|  | Contingency Utilisation (%) | 12.9305 | 9.648 | 6.9188 | 5.0291 | 4.5317
|  | N-1 Hosting Capacity (A) | 435.1401 | 449.3208 | 461.1109 | 469.2741 | 471.4233
|  | N-1 Power Factor | 0.88633 | 0.80226 | 0.63569 | 0.3292 | 0.73189
|  | N-1 Limiting section | 604-1 | 604-1 | 604-1 | 604-1 | 604-1
|  | Contingency Scenario | F605 | F683 | F683 | F683 | F683
F605 | 605-1 | Load (A) | 39.6247 | 31.0128 | 24.0526 | 19.6148 | 18.4538
|  | Rating (A) | 432 | 432 | 432 | 432 | 432
|  | Utilisation (%) | 9.1724 | 7.1789 | 5.5677 | 4.5405 | 4.2717
|  | Hosting Capacity (A) | 392.3753 | 400.9872 | 407.9474 | 412.3852 | 413.5462
|  | Power Factor | 0.88656 | 0.80262 | 0.63616 | 0.32956 | 0.73858
|  | N-1 Load (A) | 55.8847 | 41.7173 | 29.9092 | 21.7308 | 19.5769
|  | N-1 Rating (A) | 491 | 491 | 491 | 491 | 491
|  | Contingency Utilisation (%) | 12.9363 | 9.6568 | 6.9234 | 5.0303 | 4.5317
|  | N-1 Hosting Capacity (A) | 435.1153 | 449.2827 | 461.0908 | 469.2692 | 471.4231
|  | N-1 Power Factor | 0.88656 | 0.80262 | 0.63616 | 0.32956 | 0.73858
|  | N-1 Limiting section | 605-1 | 605-1 | 605-1 | 605-1 | 605-1
|  | Contingency Scenario | F604 | F683 | F683 | F683 | F683
F606 | 606-1 | Load (A) | 41.8752 | 26.8353 | 19.8976 | 30.6364 | 47.2879
|  | Rating (A) | 601 | 601 | 601 | 601 | 601
|  | Utilisation (%) | 6.9676 | 4.4651 | 3.3107 | 5.0976 | 7.8682
|  | Hosting Capacity (A) | 559.1248 | 574.1647 | 581.1024 | 570.3636 | 553.7121
|  | Power Factor | 0.87951 | 0.66972 | 0.2827 | 0.78172 | 0.92382
|  | N-1 Load (A) | 61.6582 | 38.4191 | 27.2791 | 44.8376 | 70.5218
|  | N-1 Rating (A) | 713 | 713 | 713 | 713 | 713
|  | Contingency Utilisation (%) | 10.2593 | 6.3925 | 4.539 | 7.4605 | 11.7341
|  | N-1 Hosting Capacity (A) | 651.3418 | 674.5809 | 685.7209 | 668.1624 | 642.4782
|  | N-1 Power Factor | 0.87951 | 0.66972 | 0.2827 | 0.78172 | 0.92382
|  | N-1 Limiting section | 606-1 | 606-1 | 606-1 | 606-1 | 606-1
|  | Contingency Scenario | F504 | F3393 | F480 | F480 | F504
F608 | 608-1 | Load (A) | 35.5016 | 56.7784 | 77.9533 | 98.4614 | 117.1924
|  | Rating (A) | 412 | 412 | 412 | 412 | 412
|  | Utilisation (%) | 8.6182 | 13.7812 | 18.9207 | 23.8984 | 28.4448
|  | Hosting Capacity (A) | 376.4984 | 355.2216 | 334.0467 | 313.5386 | 294.8076
|  | Power Factor | 0.99992 | 0.99994 | 0.99961 | 0.99912 | 0.99854
F612 | 612-1 | Load (A) | 15.9099 | 37.2362 | 60.1997 | 84.4693 | 108.9265
|  | Rating (A) | 766 | 766 | 766 | 766 | 766
|  | Utilisation (%) | 2.077 | 4.8611 | 7.859 | 11.0273 | 14.2202
|  | Hosting Capacity (A) | 750.0901 | 728.7638 | 705.8003 | 681.5307 | 657.0735
|  | Power Factor | 0.99992 | 0.99995 | 0.99969 | 0.99926 | 0.99867
|  | N-1 Load (A) | 31.8168 | 74.4575 | 120.3629 | 168.8715 | 217.7484
|  | N-1 Rating (A) | 766 | 766 | 766 | 766 | 766
|  | Contingency Utilisation (%) | 4.1536 | 9.7203 | 15.7132 | 22.0459 | 28.4267
|  | N-1 Hosting Capacity (A) | 734.1832 | 691.5425 | 645.6371 | 597.1285 | 548.2516
|  | N-1 Power Factor | 0.99992 | 0.99995 | 0.99969 | 0.99926 | 0.99867
|  | N-1 Limiting section | 612-1 | 612-1 | 612-1 | 612-1 | 612-1
|  | Contingency Scenario | F613 | F613 | F613 | F613 | F613
F613 | 613-1 | Load (A) | 15.9099 | 37.2362 | 60.1997 | 84.4693 | 108.9265
|  | Rating (A) | 766 | 766 | 766 | 766 | 766
|  | Utilisation (%) | 2.077 | 4.8611 | 7.859 | 11.0273 | 14.2202
|  | Hosting Capacity (A) | 750.0901 | 728.7638 | 705.8003 | 681.5307 | 657.0735
|  | Power Factor | 0.99992 | 0.99995 | 0.99969 | 0.99926 | 0.99867
|  | N-1 Load (A) | 31.8168 | 74.4575 | 120.3629 | 168.8715 | 217.7484
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 4.1536 | 9.7203 | 15.7132 | 22.0459 | 28.4267
|  | N-1 Hosting Capacity (A) | 768.1832 | 725.5425 | 679.6371 | 631.1285 | 582.2516
|  | N-1 Power Factor | 0.99992 | 0.99995 | 0.99969 | 0.99926 | 0.99867
|  | N-1 Limiting section | 613-1 | 613-1 | 613-1 | 613-1 | 613-1
|  | Contingency Scenario | F612 | F612 | F612 | F612 | F612
F616 | 616-1 | Load (A) | 144.1174 | 142.9621 | 142.2709 | 141.9627 | 141.9674
|  | Rating (A) | 407 | 407 | 407 | 407 | 407
|  | Utilisation (%) | 35.4097 | 35.1258 | 34.956 | 34.8803 | 34.8814
|  | Hosting Capacity (A) | 262.8826 | 264.0379 | 264.7291 | 265.0373 | 265.0326
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 224.0141 | 222.1669 | 221.0628 | 220.5722 | 220.5829
|  | N-1 Rating (A) | 440 | 440 | 440 | 440 | 440
|  | Contingency Utilisation (%) | 55.0403 | 54.5865 | 54.3152 | 54.1946 | 54.1973
|  | N-1 Hosting Capacity (A) | 215.9859 | 217.8331 | 218.9372 | 219.4278 | 219.4171
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 616-1 | 616-1 | 616-1 | 616-1 | 616-1
|  | Contingency Scenario | F617 | F617 | F617 | F617 | F617
F617 | 617-1 | Load (A) | 148.7578 | 147.5622 | 146.847 | 146.5281 | 146.5333
|  | Rating (A) | 407 | 407 | 407 | 407 | 407
|  | Utilisation (%) | 36.5498 | 36.2561 | 36.0803 | 36.002 | 36.0033
|  | Hosting Capacity (A) | 258.2422 | 259.4378 | 260.153 | 260.4719 | 260.4667
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 227.0734 | 225.1976 | 224.0764 | 223.5784 | 223.5895
|  | N-1 Rating (A) | 440 | 440 | 440 | 440 | 440
|  | Contingency Utilisation (%) | 55.792 | 55.3311 | 55.0556 | 54.9333 | 54.936
|  | N-1 Hosting Capacity (A) | 212.9266 | 214.8024 | 215.9236 | 216.4216 | 216.4105
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 617-1 | 617-1 | 617-1 | 617-1 | 617-1
|  | Contingency Scenario | F616 | F616 | F616 | F616 | F616
F618 | 618-1 | Load (A) | 27.522 | 8.5064 | 11.8137 | 31.6395 | 51.0563
|  | Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Utilisation (%) | 3.3645 | 1.0399 | 1.4442 | 3.8679 | 6.2416
|  | Hosting Capacity (A) | 790.478 | 809.4936 | 806.1863 | 786.3605 | 766.9437
|  | Power Factor | 0.99702 | 0.95751 | 0.97842 | 0.99787 | 0.99965
|  | N-1 Load (A) | 45.248 | 13.8011 | 49.6068 | 87.784 | 123.0821
|  | N-1 Rating (A) | 818 | 818 | 818 | 818 | 818
|  | Contingency Utilisation (%) | 5.5315 | 1.6872 | 6.0644 | 10.7315 | 15.0467
|  | N-1 Hosting Capacity (A) | 772.752 | 804.1989 | 768.3932 | 730.216 | 694.9179
|  | N-1 Power Factor | 0.99702 | 0.95751 | 0.97842 | 0.99787 | 0.99965
|  | N-1 Limiting section | 618-1 | 618-1 | 618-1 | 618-1 | 618-1
|  | Contingency Scenario | F619 | F619 | F542 | F542 | F542
F619 | 619-1 | Load (A) | 17.7534 | 5.515 | 7.6412 | 20.4121 | 32.952
|  | Rating (A) | 550 | 553 | 553 | 550 | 550
|  | Utilisation (%) | 3.2279 | 0.99728 | 1.3818 | 3.7113 | 5.9913
|  | Hosting Capacity (A) | 532.2466 | 547.485 | 545.3588 | 529.5879 | 517.048
|  | Power Factor | 0.99747 | 0.95282 | 0.97681 | 0.99844 | 0.99978
|  | N-1 Load (A) | 45.2827 | 13.9487 | 32.0167 | 56.6724 | 83.8776
|  | N-1 Rating (A) | 550 | 550 | 550 | 550 | 550
|  | Contingency Utilisation (%) | 8.2332 | 2.5224 | 5.8212 | 10.3041 | 15.2505
|  | N-1 Hosting Capacity (A) | 504.7173 | 536.0513 | 517.9833 | 493.3276 | 466.1224
|  | N-1 Power Factor | 0.99747 | 0.95282 | 0.98313 | 0.99844 | 0.99978
|  | N-1 Limiting section | 619-1(1) | 619-1 | 619-1(1) | 619-1(1) | 619-1(1)
|  | Contingency Scenario | F618 | F618 | F542 | F542 | F618
F620 | 620-1 | Load (A) | 39.9499 | 30.6373 | 21.1261 | 18.9465 | 15.2129
|  | Rating (A) | 324 | 324 | 324 | 400 | 400
|  | Utilisation (%) | 12.3302 | 9.456 | 6.5204 | 4.7366 | 3.8032
|  | Hosting Capacity (A) | 284.0501 | 293.3627 | 302.8739 | 381.0535 | 384.7871
|  | Power Factor | 0.99973 | 0.99928 | 0.9981 | 0.6094 | 0.88354
|  | N-1 Load (A) | 78.1169 | 59.8605 | 41.2068 | 22.5752 | 15.7102
|  | N-1 Rating (A) | 359 | 359 | 359 | 359 | 359
|  | Contingency Utilisation (%) | 24.1102 | 18.4755 | 12.7182 | 6.9676 | 3.9276
|  | N-1 Hosting Capacity (A) | 280.8831 | 299.1395 | 317.7932 | 336.4248 | 343.2898
|  | N-1 Power Factor | 0.99973 | 0.99928 | 0.9981 | 0.99312 | 0.88354
|  | N-1 Limiting section | 620-1(1) | 620-1(1) | 620-1(1) | 620-1(1) | 620-1
|  | Contingency Scenario | F621 | F621 | F621 | F621 | F621
F621 | 621-1 | Load (A) | 38.023 | 29.149 | 24.8247 | 18.4638 | 15.1645
|  | Rating (A) | 324 | 324 | 400 | 400 | 400
|  | Utilisation (%) | 11.7355 | 8.9966 | 6.2062 | 4.6159 | 3.7911
|  | Hosting Capacity (A) | 285.977 | 294.851 | 375.1753 | 381.5362 | 384.8355
|  | Power Factor | 0.99956 | 0.99967 | 0.80877 | 0.59573 | 0.88203
|  | N-1 Load (A) | 78.076 | 59.8385 | 41.1957 | 22.569 | 15.6837
|  | N-1 Rating (A) | 359 | 359 | 359 | 359 | 359
|  | Contingency Utilisation (%) | 24.0975 | 18.4687 | 12.7147 | 6.9657 | 3.9209
|  | N-1 Hosting Capacity (A) | 280.924 | 299.1615 | 317.8043 | 336.431 | 343.3163
|  | N-1 Power Factor | 0.99956 | 0.99967 | 0.99893 | 0.99455 | 0.88203
|  | N-1 Limiting section | 621-1(1) | 621-1(1) | 621-1(1) | 621-1(1) | 621-1
|  | Contingency Scenario | F620 | F620 | F620 | F620 | F620
F622 | 622-1 | Load (A) | 93.1543 | 73.5991 | 52.3021 | 31.0731 | 19.8898
|  | Rating (A) | 738 | 738 | 738 | 738 | 738
|  | Utilisation (%) | 12.6225 | 9.9728 | 7.087 | 4.2105 | 2.6951
|  | Hosting Capacity (A) | 644.8457 | 664.4009 | 685.6979 | 706.9269 | 718.1102
|  | Power Factor | 0.98498 | 0.97189 | 0.93574 | 0.78271 | 1
|  | N-1 Load (A) | 157.2206 | 122.8455 | 85.4717 | 47.574 | 26.8425
|  | N-1 Rating (A) | 738 | 738 | 738 | 738 | 738
|  | Contingency Utilisation (%) | 21.3036 | 16.6457 | 11.5815 | 6.4463 | 3.6372
|  | N-1 Hosting Capacity (A) | 580.7794 | 615.1545 | 652.5283 | 690.426 | 711.1575
|  | N-1 Power Factor | 0.98498 | 0.97189 | 0.93574 | 0.78271 | 1
|  | N-1 Limiting section | 622-1 | 622-1 | 622-1 | 622-1 | 622-1
|  | Contingency Scenario | F593 | F593 | F593 | F593 | F593
F623 | 623-1 | Load (A) | 93.1543 | 73.5991 | 52.3021 | 31.0731 | 19.8898
|  | Rating (A) | 738 | 738 | 738 | 738 | 738
|  | Utilisation (%) | 12.6225 | 9.9728 | 7.087 | 4.2105 | 2.6951
|  | Hosting Capacity (A) | 644.8457 | 664.4009 | 685.6979 | 706.9269 | 718.1102
|  | Power Factor | 0.98498 | 0.97189 | 0.93574 | 0.78271 | 1
|  | N-1 Load (A) | 157.2206 | 122.8455 | 85.4717 | 47.574 | 26.8425
|  | N-1 Rating (A) | 738 | 738 | 738 | 738 | 738
|  | Contingency Utilisation (%) | 21.3036 | 16.6457 | 11.5815 | 6.4463 | 3.6372
|  | N-1 Hosting Capacity (A) | 580.7794 | 615.1545 | 652.5283 | 690.426 | 711.1575
|  | N-1 Power Factor | 0.98498 | 0.97189 | 0.93574 | 0.78271 | 1
|  | N-1 Limiting section | 623-1(2) | 623-1(2) | 623-1(2) | 623-1(2) | 623-1(2)
|  | Contingency Scenario | F593 | F593 | F593 | F593 | F593
F628 | 628-1 | Load (A) | 113.3719 | 108.6778 | 101.0643 | 91.5562 | 83.1794
|  | Rating (A) | 415 | 415 | 415 | 415 | 415
|  | Utilisation (%) | 27.3185 | 26.1874 | 24.3528 | 22.0617 | 20.0432
|  | Hosting Capacity (A) | 301.6281 | 306.3222 | 313.9357 | 323.4438 | 331.8206
|  | Power Factor | 0.99841 | 0.99854 | 0.99873 | 0.99895 | 0.99913
|  | N-1 Load (A) | 229.7759 | 220.1518 | 204.5711 | 185.1603 | 168.0988
|  | N-1 Rating (A) | 415 | 415 | 415 | 415 | 415
|  | Contingency Utilisation (%) | 55.3677 | 53.0486 | 49.2942 | 44.6169 | 40.5057
|  | N-1 Hosting Capacity (A) | 185.2241 | 194.8482 | 210.4289 | 229.8397 | 246.9012
|  | N-1 Power Factor | 0.99841 | 0.99854 | 0.99873 | 0.99895 | 0.99913
|  | N-1 Limiting section | 628-1(1) | 628-1(1) | 628-1(1) | 628-1(1) | 628-1(1)
|  | Contingency Scenario | F649 | F649 | F649 | F649 | F649
F631 | 631 | Load (A) | 43.5348 | 33.9361 | 27.0672 | 25.9496 | 31.2471
|  | Rating (A) | 420 | 420 | 420 | 420 | 420
|  | Utilisation (%) | 10.3654 | 8.08 | 6.4446 | 6.1785 | 7.4398
|  | Hosting Capacity (A) | 376.4652 | 386.0639 | 392.9328 | 394.0504 | 388.7529
|  | Power Factor | 0.7785 | 0.61408 | 0.27097 | 0.24908 | 0.63816
|  | N-1 Load (A) | 65.2435 | 45.7173 | 32.1976 | 40.2575 | 51.593
|  | N-1 Rating (A) | 420 | 420 | 420 | 420 | 420
|  | Contingency Utilisation (%) | 15.5342 | 10.8851 | 7.6661 | 9.5851 | 12.284
|  | N-1 Hosting Capacity (A) | 354.7565 | 374.2827 | 387.8024 | 379.7425 | 368.407
|  | N-1 Power Factor | 0.7785 | 0.61408 | 0.27097 | 0.24908 | 0.63816
|  | N-1 Limiting section | 631 | 631 | 631 | 631 | 631
|  | Contingency Scenario | F632 | F632 | F663 | F527 | F527
F632 | 632 | Load (A) | 43.3723 | 33.8553 | 27.0536 | 25.9435 | 31.1793
|  | Rating (A) | 420 | 420 | 420 | 420 | 420
|  | Utilisation (%) | 10.3268 | 8.0608 | 6.4413 | 6.177 | 7.4236
|  | Hosting Capacity (A) | 376.6277 | 386.1447 | 392.9464 | 394.0565 | 388.8207
|  | Power Factor | 0.77676 | 0.61187 | 0.26947 | 0.24768 | 0.63577
|  | N-1 Load (A) | 65.2017 | 45.7346 | 32.1316 | 40.1131 | 51.3589
|  | N-1 Rating (A) | 420 | 420 | 420 | 420 | 420
|  | Contingency Utilisation (%) | 15.5242 | 10.8892 | 7.6504 | 9.5507 | 12.2283
|  | N-1 Hosting Capacity (A) | 354.7983 | 374.2654 | 387.8684 | 379.8869 | 368.6411
|  | N-1 Power Factor | 0.77676 | 0.61187 | 0.26947 | 0.24768 | 0.63577
|  | N-1 Limiting section | 632 | 632 | 632 | 632 | 632
|  | Contingency Scenario | F631 | F631 | F663 | F527 | F527
F635 | 635-1 | Load (A) | 29.7848 | 1.0284 | 29.1199 | 57.8315 | 83.5033
|  | Rating (A) | 523 | 523 | 523 | 523 | 523
|  | Utilisation (%) | 5.695 | 0.19664 | 5.5679 | 11.059 | 15.9662
|  | Hosting Capacity (A) | 493.2152 | 521.9716 | 493.8801 | 465.1685 | 439.4967
|  | Power Factor | 0.9998 | 0.5212 | 0.99978 | 0.99997 | 0.99978
F636 | 636-1 | Load (A) | 31.493 | 29.1377 | 26.4716 | 23.5518 | 20.5903
|  | Rating (A) | 725 | 725 | 725 | 725 | 725
|  | Utilisation (%) | 4.3439 | 4.019 | 3.6513 | 3.2485 | 2.84
|  | Hosting Capacity (A) | 693.507 | 695.8623 | 698.5284 | 701.4482 | 704.4097
|  | Power Factor | 0.98512 | 0.98218 | 0.97776 | 0.97105 | 0.96103
|  | N-1 Load (A) | 62.0509 | 57.274 | 51.8534 | 45.8982 | 39.8142
|  | N-1 Rating (A) | 725 | 725 | 725 | 725 | 725
|  | Contingency Utilisation (%) | 8.5587 | 7.8999 | 7.1522 | 6.3308 | 5.4916
|  | N-1 Hosting Capacity (A) | 662.9491 | 667.726 | 673.1466 | 679.1018 | 685.1858
|  | N-1 Power Factor | 0.98512 | 0.98218 | 0.97776 | 0.97105 | 0.96103
|  | N-1 Limiting section | 636-1 | 636-1 | 636-1 | 636-1 | 636-1
|  | Contingency Scenario | F3280 | F3280 | F3280 | F3280 | F3280
F637 | 637-1 | Load (A) | 72.8602 | 62.2607 | 50.8833 | 39.0213 | 27.5538
|  | Rating (A) | 716 | 716 | 716 | 716 | 716
|  | Utilisation (%) | 10.176 | 8.6956 | 7.1066 | 5.4499 | 3.8483
|  | Hosting Capacity (A) | 643.1398 | 653.7393 | 665.1167 | 676.9787 | 688.4462
|  | Power Factor | 0.99032 | 0.98579 | 0.97743 | 0.95974 | 0.91566
|  | N-1 Load (A) | 145.1571 | 123.7109 | 100.6169 | 76.3806 | 52.5843
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 20.2733 | 17.2781 | 14.0526 | 10.6677 | 7.3442
|  | N-1 Hosting Capacity (A) | 654.8429 | 676.2891 | 699.3831 | 723.6194 | 747.4157
|  | N-1 Power Factor | 0.99032 | 0.98579 | 0.97743 | 0.95974 | 0.91566
|  | N-1 Limiting section | 637-1 | 637-1 | 637-1 | 637-1 | 637-1
|  | Contingency Scenario | F638 | F638 | F638 | F638 | F638
F638 | 638-1 | Load (A) | 73.105 | 62.4685 | 51.0512 | 39.147 | 27.6372
|  | Rating (A) | 716 | 716 | 716 | 716 | 716
|  | Utilisation (%) | 10.2102 | 8.7247 | 7.1301 | 5.4675 | 3.8599
|  | Hosting Capacity (A) | 642.895 | 653.5315 | 664.9488 | 676.853 | 688.3628
|  | Power Factor | 0.99036 | 0.98586 | 0.97754 | 0.95992 | 0.91601
|  | N-1 Load (A) | 145.1544 | 123.7079 | 100.6132 | 76.3757 | 52.5771
|  | N-1 Rating (A) | 800 | 800 | 800 | 800 | 800
|  | Contingency Utilisation (%) | 20.273 | 17.2776 | 14.0521 | 10.667 | 7.3432
|  | N-1 Hosting Capacity (A) | 654.8456 | 676.2921 | 699.3868 | 723.6243 | 747.4229
|  | N-1 Power Factor | 0.99036 | 0.98586 | 0.97754 | 0.95992 | 0.91601
|  | N-1 Limiting section | 638-1 | 638-1 | 638-1 | 638-1 | 638-1
|  | Contingency Scenario | F637 | F637 | F637 | F637 | F637
F639 | 639-1 | Load (A) | 21.4242 | 17.1357 | 25.143 | 39.7341 | 56.1007
|  | Rating (A) | 503 | 503 | 503 | 503 | 503
|  | Utilisation (%) | 4.2593 | 3.4067 | 4.9986 | 7.8994 | 11.1532
|  | Hosting Capacity (A) | 481.5758 | 485.8643 | 477.857 | 463.2659 | 446.8993
|  | Power Factor | 0.61368 | 0.99984 | 0.74294 | 0.91142 | 0.9608
|  | N-1 Load (A) | 31.2409 | 17.5719 | 40.9136 | 74.0934 | 108.6743
|  | N-1 Rating (A) | 585 | 585 | 585 | 585 | 585
|  | Contingency Utilisation (%) | 6.2109 | 3.4934 | 8.1339 | 14.7303 | 21.6052
|  | N-1 Hosting Capacity (A) | 553.7591 | 567.4281 | 544.0864 | 510.9066 | 476.3257
|  | N-1 Power Factor | 0.61368 | 0.99984 | 0.74294 | 0.91142 | 0.9608
|  | N-1 Limiting section | 639-1 | 639-1 | 639-1 | 639-1 | 639-1
|  | Contingency Scenario | F653 | F653 | F653 | F653 | F653
F641 | 641-1 | Load (A) | 16.1152 | 12.8412 | 11.6904 | 13.1294 | 16.1517
|  | Rating (A) | 703 | 703 | 703 | 703 | 703
|  | Utilisation (%) | 2.2923 | 1.8266 | 1.6629 | 1.8676 | 2.2975
|  | Hosting Capacity (A) | 686.8848 | 690.1588 | 691.3096 | 689.8706 | 686.8483
|  | Power Factor | 0.69202 | 0.41602 | 1 | 0.46103 | 0.69653
|  | N-1 Load (A) | 24.5947 | 15.2785 | 11.6951 | 16.2542 | 24.7331
|  | N-1 Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Contingency Utilisation (%) | 3.4985 | 2.1733 | 1.6636 | 2.3121 | 3.5182
|  | N-1 Hosting Capacity (A) | 755.4053 | 764.7215 | 768.3049 | 763.7458 | 755.2669
|  | N-1 Power Factor | 0.69202 | 0.41602 | 1 | 0.46103 | 0.69653
|  | N-1 Limiting section | 641-1(7) | 641-1(7) | 641-1(7) | 641-1(7) | 641-1(7)
|  | Contingency Scenario | F642 | F642 | F617 | F642 | F642
F642 | 642-1 | Load (A) | 15.8354 | 12.6561 | 11.5532 | 12.9665 | 15.9186
|  | Rating (A) | 703 | 703 | 703 | 703 | 703
|  | Utilisation (%) | 2.2526 | 1.8003 | 1.6434 | 1.8444 | 2.2644
|  | Hosting Capacity (A) | 687.1646 | 690.3439 | 691.4468 | 690.0335 | 687.0814
|  | Power Factor | 0.69065 | 0.41444 | 1 | 0.45642 | 0.69163
|  | N-1 Load (A) | 24.5855 | 15.2675 | 11.5578 | 16.2438 | 24.7252
|  | N-1 Rating (A) | 780 | 780 | 780 | 780 | 780
|  | Contingency Utilisation (%) | 3.4972 | 2.1718 | 1.6441 | 2.3106 | 3.5171
|  | N-1 Hosting Capacity (A) | 755.4145 | 764.7325 | 768.4422 | 763.7562 | 755.2748
|  | N-1 Power Factor | 0.69065 | 0.41444 | 1 | 0.45642 | 0.69163
|  | N-1 Limiting section | 642-1(7) | 642-1(7) | 642-1(7) | 642-1(7) | 642-1(7)
|  | Contingency Scenario | F641 | F641 | F617 | F641 | F641
F643 | 643-1 | Load (A) | 56.7103 | 44.5752 | 30.0853 | 13.6242 | 6.1117
|  | Rating (A) | 711 | 711 | 711 | 711 | 711
|  | Utilisation (%) | 7.9761 | 6.2694 | 4.2314 | 1.9162 | 0.8596
|  | Hosting Capacity (A) | 654.2897 | 666.4248 | 680.9147 | 697.3758 | 704.8883
|  | Power Factor | 0.99921 | 0.99794 | 0.99367 | 0.96156 | 0.78128
|  | N-1 Load (A) | 113.5211 | 89.0399 | 59.804 | 26.4077 | 10.2471
|  | N-1 Rating (A) | 760 | 760 | 760 | 760 | 760
|  | Contingency Utilisation (%) | 15.9664 | 12.5232 | 8.4113 | 3.7142 | 1.4412
|  | N-1 Hosting Capacity (A) | 646.4789 | 670.9601 | 700.196 | 733.5923 | 749.7529
|  | N-1 Power Factor | 0.99962 | 0.99954 | 0.99367 | 0.96156 | 0.78128
|  | N-1 Limiting section | 643-1(1) | 643-1(1) | 643-1 | 643-1 | 643-1
|  | Contingency Scenario | F674 | F674 | F674 | F674 | F674
F645 | 645-1 | Load (A) | 5.3007 | 5.3007 | 5.3007 | 5.3007 | 5.3007
|  | Rating (A) | 433 | 433 | 433 | 433 | 433
|  | Utilisation (%) | 1.2242 | 1.2242 | 1.2242 | 1.2242 | 1.2242
|  | Hosting Capacity (A) | 427.6993 | 427.6993 | 427.6993 | 427.6993 | 427.6993
|  | Power Factor | 1 | 1 | 1 | 1 | 1
F646A | 646A-1 | Load (A) | 29.1431 | 29.1431 | 29.1431 | 29.1431 | 29.1431
|  | Rating (A) | 424 | 424 | 424 | 424 | 424
|  | Utilisation (%) | 6.8734 | 6.8734 | 6.8734 | 6.8734 | 6.8734
|  | Hosting Capacity (A) | 394.8569 | 394.8569 | 394.8569 | 394.8569 | 394.8569
|  | Power Factor | 0.86726 | 0.86726 | 0.86726 | 0.86726 | 0.86726
F646A | 646B-1 | Load (A) | 25.3639 | 25.3639 | 25.3639 | 25.3639 | 25.3639
|  | Rating (A) | 300 | 300 | 300 | 300 | 300
|  | Utilisation (%) | 8.4546 | 8.4546 | 8.4546 | 8.4546 | 8.4546
|  | Hosting Capacity (A) | 274.6361 | 274.6361 | 274.6361 | 274.6361 | 274.6361
|  | Power Factor | 0.99637 | 0.99637 | 0.99637 | 0.99637 | 0.99637
F647 | 647-1 | Load (A) | 46.4419 | 76.3793 | 105.8031 | 133.4918 | 157.804
|  | Rating (A) | 479 | 479 | 479 | 479 | 479
|  | Utilisation (%) | 9.6989 | 15.9543 | 22.0883 | 27.8689 | 32.9445
|  | Hosting Capacity (A) | 432.5581 | 402.6207 | 373.1969 | 345.5082 | 321.196
|  | Power Factor | 1 | 0.99951 | 0.99842 | 0.99751 | 0.99653
|  | N-1 Load (A) | 49.8032 | 106.2556 | 161.0707 | 212.7337 | 258.3148
|  | N-1 Rating (A) | 479 | 479 | 479 | 479 | 479
|  | Contingency Utilisation (%) | 10.3973 | 22.1828 | 33.6265 | 44.412 | 53.9279
|  | N-1 Hosting Capacity (A) | 429.1968 | 372.7444 | 317.9293 | 266.2663 | 220.6852
|  | N-1 Power Factor | 0.99969 | 0.9992 | 0.99842 | 0.99751 | 0.99653
|  | N-1 Limiting section | 647-1(10) | 647-1(10) | 647-1(10) | 647-1(10) | 647-1(10)
|  | Contingency Scenario | F694 | F694 | F694 | F694 | F694
F649 | 649-1 | Load (A) | 114.7471 | 109.9976 | 102.2941 | 92.6736 | 84.1979
|  | Rating (A) | 415 | 415 | 415 | 415 | 415
|  | Utilisation (%) | 27.6499 | 26.5054 | 24.6492 | 22.331 | 20.2887
|  | Hosting Capacity (A) | 300.2529 | 305.0024 | 312.7059 | 322.3264 | 330.8021
|  | Power Factor | 0.99849 | 0.99861 | 0.9988 | 0.99902 | 0.99919
|  | N-1 Load (A) | 229.7566 | 220.1358 | 204.5596 | 185.1533 | 168.0948
|  | N-1 Rating (A) | 415 | 415 | 415 | 415 | 415
|  | Contingency Utilisation (%) | 55.363 | 53.0448 | 49.2915 | 44.6153 | 40.5048
|  | N-1 Hosting Capacity (A) | 185.2434 | 194.8642 | 210.4404 | 229.8467 | 246.9052
|  | N-1 Power Factor | 0.99849 | 0.99861 | 0.9988 | 0.99902 | 0.99919
|  | N-1 Limiting section | 649-1(1) | 649-1(1) | 649-1(1) | 649-1(1) | 649-1(1)
|  | Contingency Scenario | F628 | F628 | F628 | F628 | F628
F650 | 650-1 | Load (A) | 17.2472 | 7.3168 | 23.0369 | 42.7135 | 62.0798
|  | Rating (A) | 650 | 650 | 650 | 650 | 650
|  | Utilisation (%) | 2.6534 | 1.1257 | 3.5441 | 6.5713 | 9.5507
|  | Hosting Capacity (A) | 632.7528 | 642.6832 | 626.9631 | 607.2865 | 587.9202
|  | Power Factor | 0.91612 | 0.34785 | 0.95932 | 0.99069 | 0.99696
|  | N-1 Load (A) | 32.5602 | 13.3385 | 44.612 | 84.363 | 123.1073
|  | N-1 Rating (A) | 740 | 740 | 740 | 740 | 740
|  | Contingency Utilisation (%) | 5.0093 | 2.0521 | 6.8634 | 12.9789 | 18.9396
|  | N-1 Hosting Capacity (A) | 707.4398 | 726.6615 | 695.388 | 655.637 | 616.8927
|  | N-1 Power Factor | 0.91612 | 0.34785 | 0.95932 | 0.99069 | 0.99696
|  | N-1 Limiting section | 650-1 | 650-1 | 650-1 | 650-1 | 650-1
|  | Contingency Scenario | F651 | F597 | F651 | F651 | F651
F651 | 651-1 | Load (A) | 17.0729 | 7.2891 | 22.7887 | 42.2299 | 61.3696
|  | Rating (A) | 650 | 650 | 650 | 650 | 650
|  | Utilisation (%) | 2.6266 | 1.1214 | 3.506 | 6.4969 | 9.4415
|  | Hosting Capacity (A) | 632.9271 | 642.7109 | 627.2113 | 607.7701 | 588.6304
|  | Power Factor | 0.91482 | 0.34515 | 0.9586 | 0.9905 | 0.99689
|  | N-1 Load (A) | 32.5762 | 13.2091 | 44.6223 | 84.3671 | 123.1084
|  | N-1 Rating (A) | 740 | 740 | 740 | 740 | 740
|  | Contingency Utilisation (%) | 5.0117 | 2.0322 | 6.865 | 12.9795 | 18.9398
|  | N-1 Hosting Capacity (A) | 707.4238 | 726.7909 | 695.3777 | 655.6329 | 616.8916
|  | N-1 Power Factor | 0.91482 | 0.34515 | 0.9586 | 0.9905 | 0.99689
|  | N-1 Limiting section | 651-1 | 651-1 | 651-1 | 651-1 | 651-1
|  | Contingency Scenario | F650 | F597 | F650 | F650 | F650
F652 | 652-1 | Load (A) | 177.8024 | 177.8024 | 177.8024 | 177.8024 | 177.8024
|  | Rating (A) | 450 | 450 | 450 | 450 | 450
|  | Utilisation (%) | 39.5117 | 39.5117 | 39.5117 | 39.5117 | 39.5117
|  | Hosting Capacity (A) | 272.1976 | 272.1976 | 272.1976 | 272.1976 | 272.1976
|  | Power Factor | 0.9989 | 0.9989 | 0.9989 | 0.9989 | 0.9989
F653 | 653-1 | Load (A) | 21.4242 | 17.1357 | 25.143 | 39.7341 | 56.1007
|  | Rating (A) | 503 | 503 | 503 | 503 | 503
|  | Utilisation (%) | 4.2593 | 3.4067 | 4.9986 | 7.8994 | 11.1532
|  | Hosting Capacity (A) | 481.5758 | 485.8643 | 477.857 | 463.2659 | 446.8993
|  | Power Factor | 0.61368 | 0.99984 | 0.74294 | 0.91142 | 0.9608
|  | N-1 Load (A) | 31.2409 | 17.5719 | 40.9136 | 74.0934 | 108.6743
|  | N-1 Rating (A) | 585 | 585 | 585 | 585 | 585
|  | Contingency Utilisation (%) | 6.2109 | 3.4934 | 8.1339 | 14.7303 | 21.6052
|  | N-1 Hosting Capacity (A) | 553.7591 | 567.4281 | 544.0864 | 510.9066 | 476.3257
|  | N-1 Power Factor | 0.61368 | 0.99984 | 0.74294 | 0.91142 | 0.9608
|  | N-1 Limiting section | 653-1 | 653-1 | 653-1 | 653-1 | 653-1
|  | Contingency Scenario | F639 | F639 | F639 | F639 | F639
F656 | 656-1 | Load (A) | 13.6346 | 21.0447 | 28.7081 | 36.5284 | 44.1705
|  | Rating (A) | 270 | 270 | 270 | 270 | 270
|  | Utilisation (%) | 5.0498 | 7.7943 | 10.6326 | 13.529 | 16.3594
|  | Hosting Capacity (A) | 256.3654 | 248.9553 | 241.2919 | 233.4716 | 225.8295
|  | Power Factor | 0.99884 | 0.99872 | 0.99854 | 0.99833 | 0.99811
|  | N-1 Load (A) | 27.7776 | 42.8279 | 58.3891 | 74.2225 | 89.6953
|  | N-1 Rating (A) | 270 | 270 | 270 | 270 | 270
|  | Contingency Utilisation (%) | 10.288 | 15.8622 | 21.6256 | 27.4898 | 33.2205
|  | N-1 Hosting Capacity (A) | 242.2224 | 227.1721 | 211.6109 | 195.7775 | 180.3047
|  | N-1 Power Factor | 0.99884 | 0.99872 | 0.99854 | 0.99833 | 0.99811
|  | N-1 Limiting section | 656-1 | 656-1 | 656-1 | 656-1 | 656-1
|  | Contingency Scenario | F561 | F561 | F561 | F561 | F561
F658 | 658-1 | Load (A) | 130.1543 | 130.1543 | 130.1543 | 130.1543 | 130.1543
|  | Rating (A) | 701 | 701 | 701 | 701 | 701
|  | Utilisation (%) | 18.5706 | 18.5706 | 18.5706 | 18.5706 | 18.5706
|  | Hosting Capacity (A) | 570.8457 | 570.8457 | 570.8457 | 570.8457 | 570.8457
|  | Power Factor | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992
F660 | 660-1 | Load (A) | 23.617 | 11.4896 | 1.0362 | 13.3541 | 25.2354
|  | Rating (A) | 676 | 676 | 676 | 676 | 676
|  | Utilisation (%) | 3.4936 | 1.6996 | 0.15328 | 1.9755 | 3.733
|  | Hosting Capacity (A) | 652.383 | 664.5104 | 674.9638 | 662.6459 | 650.7646
|  | Power Factor | 0.99955 | 0.99889 | 0.88102 | 0.99911 | 0.99956
|  | N-1 Load (A) | 47.5015 | 23.1056 | 2.0834 | 26.8464 | 50.7244
|  | N-1 Rating (A) | 751 | 751 | 751 | 751 | 751
|  | Contingency Utilisation (%) | 7.0269 | 3.418 | 0.30819 | 3.9714 | 7.5036
|  | N-1 Hosting Capacity (A) | 703.4985 | 727.8944 | 748.9166 | 724.1536 | 700.2756
|  | N-1 Power Factor | 0.99955 | 0.99889 | 0.88102 | 0.99911 | 0.99956
|  | N-1 Limiting section | 660-1 | 660-1 | 660-1 | 660-1 | 660-1
|  | Contingency Scenario | F661 | F661 | F661 | F661 | F661
F661 | 661-1 | Load (A) | 23.8694 | 11.6124 | 1.0472 | 13.4968 | 25.5051
|  | Rating (A) | 676 | 676 | 676 | 676 | 676
|  | Utilisation (%) | 3.531 | 1.7178 | 0.15492 | 1.9966 | 3.7729
|  | Hosting Capacity (A) | 652.1306 | 664.3876 | 674.9528 | 662.5032 | 650.4949
|  | Power Factor | 0.99955 | 0.99889 | 0.88102 | 0.99911 | 0.99956
|  | N-1 Load (A) | 47.5012 | 23.1055 | 2.0834 | 26.8465 | 50.7247
|  | N-1 Rating (A) | 751 | 751 | 751 | 751 | 751
|  | Contingency Utilisation (%) | 7.0268 | 3.418 | 0.30819 | 3.9714 | 7.5037
|  | N-1 Hosting Capacity (A) | 703.4988 | 727.8945 | 748.9166 | 724.1535 | 700.2753
|  | N-1 Power Factor | 0.99955 | 0.99889 | 0.88102 | 0.99911 | 0.99956
|  | N-1 Limiting section | 661-1 | 661-1 | 661-1 | 661-1 | 661-1
|  | Contingency Scenario | F660 | F660 | F660 | F660 | F660
F662 | 662-1 | Load (A) | 58.4072 | 52.4916 | 46.4089 | 40.2562 | 34.3674
|  | Rating (A) | 656 | 656 | 656 | 656 | 656
|  | Utilisation (%) | 8.9035 | 8.0018 | 7.0745 | 6.1366 | 5.2389
|  | Hosting Capacity (A) | 597.5928 | 603.5084 | 609.5911 | 615.7438 | 621.6326
|  | Power Factor | 0.98662 | 0.97991 | 0.96938 | 0.95222 | 0.92424
|  | N-1 Load (A) | 87.7228 | 78.517 | 70.3629 | 64.2498 | 58.2099
|  | N-1 Rating (A) | 737 | 737 | 737 | 737 | 737
|  | Contingency Utilisation (%) | 13.3724 | 11.969 | 10.7261 | 9.7942 | 8.8735
|  | N-1 Hosting Capacity (A) | 649.2772 | 658.483 | 666.6371 | 672.7502 | 678.7901
|  | N-1 Power Factor | 0.98662 | 0.97991 | 0.96938 | 0.95222 | 0.92424
|  | N-1 Limiting section | 662-1 | 662-1 | 662-1 | 662-1 | 662-1
|  | Contingency Scenario | F663 | F663 | F527 | F527 | F527
F663 | 663-1 | Load (A) | 59.0825 | 53.0906 | 46.9283 | 40.6929 | 34.7221
|  | Rating (A) | 656 | 656 | 656 | 656 | 656
|  | Utilisation (%) | 9.0065 | 8.0931 | 7.1537 | 6.2032 | 5.293
|  | Hosting Capacity (A) | 596.9175 | 602.9094 | 609.0717 | 615.3071 | 621.2779
|  | Power Factor | 0.98702 | 0.98046 | 0.97014 | 0.95329 | 0.92576
|  | N-1 Load (A) | 88.2202 | 78.9568 | 71.1832 | 64.9939 | 58.8784
|  | N-1 Rating (A) | 737 | 737 | 737 | 737 | 737
|  | Contingency Utilisation (%) | 13.4482 | 12.0361 | 10.8511 | 9.9076 | 8.9754
|  | N-1 Hosting Capacity (A) | 648.7798 | 658.0432 | 665.8168 | 672.0061 | 678.1216
|  | N-1 Power Factor | 0.98702 | 0.98046 | 0.97014 | 0.95329 | 0.92576
|  | N-1 Limiting section | 663-1 | 663-1 | 663-1 | 663-1 | 663-1
|  | Contingency Scenario | F662 | F662 | F527 | F527 | F527
F664 | 664-1 | Load (A) | 25.2057 | 25.2245 | 25.2439 | 25.2635 | 25.2817
|  | Rating (A) | 410 | 410 | 410 | 410 | 410
|  | Utilisation (%) | 6.1477 | 6.1523 | 6.1571 | 6.1618 | 6.1663
|  | Hosting Capacity (A) | 384.7943 | 384.7755 | 384.7561 | 384.7365 | 384.7183
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 25.219 | 25.2551 | 25.2924 | 25.33 | 25.3652
|  | N-1 Rating (A) | 410 | 410 | 410 | 410 | 410
|  | Contingency Utilisation (%) | 6.151 | 6.1598 | 6.1689 | 6.178 | 6.1866
|  | N-1 Hosting Capacity (A) | 384.781 | 384.7449 | 384.7076 | 384.67 | 384.6348
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 664-1 | 664-1 | 664-1 | 664-1 | 664-1
|  | Contingency Scenario | F505 | F505 | F505 | F505 | F505
F667 | 667-1 | Load (A) | 27.7124 | 27.7124 | 27.7124 | 27.7124 | 27.7124
|  | Rating (A) | 426 | 426 | 426 | 426 | 426
|  | Utilisation (%) | 6.5053 | 6.5053 | 6.5053 | 6.5053 | 6.5053
|  | Hosting Capacity (A) | 398.2876 | 398.2876 | 398.2876 | 398.2876 | 398.2876
|  | Power Factor | 1 | 1 | 1 | 1 | 1
F668 | 668-1 | Load (A) | 27.8479 | 27.8479 | 27.8479 | 27.8479 | 27.8479
|  | Rating (A) | 426 | 426 | 426 | 426 | 426
|  | Utilisation (%) | 6.5371 | 6.5371 | 6.5371 | 6.5371 | 6.5371
|  | Hosting Capacity (A) | 398.1521 | 398.1521 | 398.1521 | 398.1521 | 398.1521
|  | Power Factor | 1 | 1 | 1 | 1 | 1
F671 | 671-1 | Load (A) | 17.7909 | 21.8392 | 16.3842 | 27.717 | 40.6184
|  | Rating (A) | 507 | 900 | 507 | 507 | 507
|  | Utilisation (%) | 3.5091 | 2.4324 | 3.2316 | 5.4712 | 8.014
|  | Hosting Capacity (A) | 489.2091 | 878.1608 | 490.6158 | 479.283 | 466.3816
|  | Power Factor | 0.72024 | 1 | 0.73724 | 0.93532 | 0.97916
|  | N-1 Load (A) | 32.2007 | 21.9724 | 29.8946 | 49.9894 | 72.8882
|  | N-1 Rating (A) | 507 | 507 | 507 | 507 | 507
|  | Contingency Utilisation (%) | 6.3512 | 4.3338 | 5.8964 | 9.8598 | 14.3764
|  | N-1 Hosting Capacity (A) | 474.7993 | 485.0276 | 477.1054 | 457.0106 | 434.1118
|  | N-1 Power Factor | 0.72024 | 1 | 0.73724 | 0.93532 | 0.97886
|  | N-1 Limiting section | 671-1(6) | 671-1(6) | 671-1(6) | 671-1(15) | 671-1(6)
|  | Contingency Scenario | F505 | F505 | F505 | F505 | F505
F673 | 673-1 | Load (A) | 3.5425 | 3.5481 | 3.5534 | 3.5581 | 3.5621
|  | Rating (A) | 960 | 960 | 960 | 960 | 960
|  | Utilisation (%) | 0.36901 | 0.3696 | 0.37014 | 0.37063 | 0.37105
|  | Hosting Capacity (A) | 956.4575 | 956.4519 | 956.4466 | 956.4419 | 956.4379
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 3.5664 | 3.5794 | 3.5909 | 3.6009 | 3.6088
|  | N-1 Rating (A) | 636 | 636 | 636 | 636 | 636
|  | Contingency Utilisation (%) | 0.3715 | 0.37285 | 0.37405 | 0.3751 | 0.37592
|  | N-1 Hosting Capacity (A) | 632.4336 | 632.4206 | 632.4091 | 632.3991 | 632.3912
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 673-1(5) | 673-1(5) | 673-1(5) | 673-1(5) | 673-1(5)
|  | Contingency Scenario | F445 | F445 | F445 | F445 | F445
F674 | 674-1 | Load (A) | 56.5631 | 44.4779 | 30.0199 | 13.5959 | 6.1019
|  | Rating (A) | 711 | 711 | 711 | 711 | 711
|  | Utilisation (%) | 7.9587 | 6.2557 | 4.2222 | 1.9122 | 0.85821
|  | Hosting Capacity (A) | 654.4369 | 666.5221 | 680.9801 | 697.4041 | 704.8981
|  | Power Factor | 0.99962 | 0.99794 | 0.99366 | 0.96148 | 0.78077
|  | N-1 Load (A) | 113.5218 | 89.0403 | 59.8038 | 26.4072 | 10.246
|  | N-1 Rating (A) | 760 | 760 | 760 | 760 | 760
|  | Contingency Utilisation (%) | 15.9665 | 12.5232 | 8.4112 | 3.7141 | 1.4411
|  | N-1 Hosting Capacity (A) | 646.4782 | 670.9597 | 700.1962 | 733.5928 | 749.754
|  | N-1 Power Factor | 0.99962 | 0.99953 | 0.99803 | 0.96148 | 0.78077
|  | N-1 Limiting section | 674-1 | 674-1 | 674-1 | 674-1(2) | 674-1(2)
|  | Contingency Scenario | F643 | F643 | F643 | F643 | F643
F675 | 675-1 | Load (A) | 17.2166 | 17.2176 | 17.2187 | 17.2197 | 17.2206
|  | Rating (A) | 492 | 492 | 492 | 492 | 492
|  | Utilisation (%) | 3.4993 | 3.4995 | 3.4997 | 3.4999 | 3.5001
|  | Hosting Capacity (A) | 474.7834 | 474.7824 | 474.7813 | 474.7803 | 474.7794
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 17.2196 | 17.2212 | 17.2227 | 17.2241 | 17.2255
|  | N-1 Rating (A) | 492 | 492 | 492 | 492 | 492
|  | Contingency Utilisation (%) | 3.4999 | 3.5002 | 3.5005 | 3.5008 | 3.5011
|  | N-1 Hosting Capacity (A) | 474.7804 | 474.7788 | 474.7773 | 474.7759 | 474.7745
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 675-1 | 675-1 | 675-1 | 675-1 | 675-1
|  | Contingency Scenario | F552 | F552 | F552 | F552 | F552
F676 | 676-1 | Load (A) | 17.0901 | 17.0911 | 17.0921 | 17.0931 | 17.094
|  | Rating (A) | 492 | 492 | 492 | 492 | 492
|  | Utilisation (%) | 3.4736 | 3.4738 | 3.474 | 3.4742 | 3.4744
|  | Hosting Capacity (A) | 474.9099 | 474.9089 | 474.9079 | 474.9069 | 474.906
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 17.0931 | 17.0946 | 17.0961 | 17.0976 | 17.0989
|  | N-1 Rating (A) | 492 | 492 | 492 | 492 | 492
|  | Contingency Utilisation (%) | 3.4742 | 3.4745 | 3.4748 | 3.4751 | 3.4754
|  | N-1 Hosting Capacity (A) | 474.9069 | 474.9054 | 474.9039 | 474.9024 | 474.9011
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 676-1(1) | 676-1(1) | 676-1(1) | 676-1(1) | 676-1(1)
|  | Contingency Scenario | F552 | F552 | F552 | F552 | F552
F677 | 677-1 | Load (A) | 129.3118 | 104.1398 | 76.776 | 47.6532 | 18.4834
|  | Rating (A) | 661 | 661 | 661 | 661 | 661
|  | Utilisation (%) | 19.5631 | 15.7549 | 11.6151 | 7.2093 | 2.7963
|  | Hosting Capacity (A) | 531.6882 | 556.8602 | 584.224 | 613.3468 | 642.5166
|  | Power Factor | 0.99956 | 0.99898 | 0.99769 | 0.99397 | 0.96752
|  | N-1 Load (A) | 247.6506 | 199.2791 | 146.704 | 90.7347 | 52.2901
|  | N-1 Rating (A) | 785 | 785 | 785 | 785 | 785
|  | Contingency Utilisation (%) | 37.4661 | 30.1481 | 22.1943 | 13.7269 | 7.9108
|  | N-1 Hosting Capacity (A) | 537.3494 | 585.7209 | 638.296 | 694.2653 | 732.7099
|  | N-1 Power Factor | 0.99956 | 0.99898 | 0.99769 | 0.99397 | 0.96752
|  | N-1 Limiting section | 677-1 | 677-1 | 677-1 | 677-1 | 677-1
|  | Contingency Scenario | F581 | F581 | F581 | F581 | F446C
F679 | 679-1 | Load (A) | 29.8691 | 27.4436 | 25.0446 | 22.9292 | 21.3914
|  | Rating (A) | 605 | 605 | 605 | 605 | 605
|  | Utilisation (%) | 4.937 | 4.5361 | 4.1396 | 3.79 | 3.5358
|  | Hosting Capacity (A) | 575.1309 | 577.5564 | 579.9554 | 582.0708 | 583.6086
|  | Power Factor | 0.97537 | 0.97015 | 0.96338 | 0.9555 | 0.94819
|  | N-1 Load (A) | 58.1567 | 53.211 | 48.299 | 43.9449 | 40.7618
|  | N-1 Rating (A) | 605 | 605 | 605 | 605 | 605
|  | Contingency Utilisation (%) | 9.6127 | 8.7952 | 7.9833 | 7.2636 | 6.7375
|  | N-1 Hosting Capacity (A) | 546.8433 | 551.789 | 556.701 | 561.0551 | 564.2382
|  | N-1 Power Factor | 0.97537 | 0.97015 | 0.96338 | 0.9555 | 0.94819
|  | N-1 Limiting section | 679-1(1) | 679-1(1) | 679-1(1) | 679-1(1) | 679-1(1)
|  | Contingency Scenario | F3818 | F3818 | F3818 | F3818 | F3818
F680 | 680-1 | Load (A) | 58.287 | 53.3877 | 48.5283 | 44.2284 | 41.0907
|  | Rating (A) | 750 | 750 | 750 | 750 | 750
|  | Utilisation (%) | 7.7716 | 7.1184 | 6.4704 | 5.8971 | 5.4788
|  | Hosting Capacity (A) | 691.713 | 696.6123 | 701.4717 | 705.7716 | 708.9093
|  | Power Factor | 0.991 | 0.98845 | 0.98508 | 0.98109 | 0.97732
F681 | 681-1 | Load (A) | 7.3609 | 19.898 | 34.1081 | 48.7897 | 63.1601
|  | Rating (A) | 661 | 661 | 661 | 661 | 661
|  | Utilisation (%) | 1.1136 | 3.0103 | 5.1601 | 7.3812 | 9.5552
|  | Hosting Capacity (A) | 653.6391 | 641.102 | 626.8919 | 612.2103 | 597.8399
|  | Power Factor | 0.70834 | 0.96765 | 0.99072 | 0.99658 | 0.99869
|  | N-1 Load (A) | 11.386 | 37.9454 | 66.2043 | 95.222 | 123.5835
|  | N-1 Rating (A) | 790 | 790 | 790 | 790 | 790
|  | Contingency Utilisation (%) | 1.7225 | 5.7406 | 10.0158 | 14.4057 | 18.6965
|  | N-1 Hosting Capacity (A) | 778.614 | 752.0546 | 723.7957 | 694.778 | 666.4165
|  | N-1 Power Factor | 0.70834 | 0.96765 | 0.99072 | 0.99658 | 0.99869
|  | N-1 Limiting section | 681-1 | 681-1 | 681-1 | 681-1 | 681-1
|  | Contingency Scenario | F682 | F682 | F682 | F682 | F682
F682 | 682-1 | Load (A) | 7.1342 | 19.0971 | 32.7004 | 46.7626 | 60.5291
|  | Rating (A) | 661 | 661 | 661 | 661 | 661
|  | Utilisation (%) | 1.0793 | 2.8891 | 4.9471 | 7.0745 | 9.1572
|  | Hosting Capacity (A) | 653.8658 | 641.9029 | 628.2996 | 614.2374 | 600.4709
|  | Power Factor | 0.69973 | 0.9659 | 0.99008 | 0.99628 | 0.99852
|  | N-1 Load (A) | 11.3532 | 37.9337 | 66.1986 | 95.2284 | 123.5988
|  | N-1 Rating (A) | 790 | 790 | 790 | 790 | 790
|  | Contingency Utilisation (%) | 1.7176 | 5.7388 | 10.0149 | 14.4067 | 18.6988
|  | N-1 Hosting Capacity (A) | 778.6468 | 752.0663 | 723.8014 | 694.7716 | 666.4012
|  | N-1 Power Factor | 0.69973 | 0.9659 | 0.99008 | 0.99628 | 0.99852
|  | N-1 Limiting section | 682-1 | 682-1 | 682-1 | 682-1 | 682-1
|  | Contingency Scenario | F681 | F681 | F681 | F681 | F681
F683 | 683-1 | Load (A) | 39.0076 | 30.8805 | 24.5249 | 20.7521 | 20.0502
|  | Rating (A) | 478 | 478 | 478 | 478 | 478
|  | Utilisation (%) | 8.1606 | 6.4604 | 5.1307 | 4.3414 | 4.1946
|  | Hosting Capacity (A) | 438.9924 | 447.1195 | 453.4751 | 457.2479 | 457.9498
|  | Power Factor | 0.88596 | 0.79393 | 0.61593 | 0.30979 | 0.27232
|  | N-1 Load (A) | 54.6974 | 40.9848 | 29.3528 | 21.4194
|  | N-1 Rating (A) | 478 | 478 | 478 | 478 | 478
|  | Contingency Utilisation (%) | 11.443 | 8.5742 | 6.1407 | 4.481
|  | N-1 Hosting Capacity (A) | 423.3026 | 437.0152 | 448.6472 | 456.5806 | #VALUE!
|  | N-1 Power Factor | 0.88596 | 0.79393 | 0.61593 | 0.30979
|  | N-1 Limiting section | 683-1 | 683-1 | 683-1 | 683-1
|  | Contingency Scenario | F605 | F605 | F605 | F605
F687 | 687-1 | Load (A) | 8.2601 | 15.4006 | 24.958 | 35.1808 | 45.3017
|  | Rating (A) | 758 | 758 | 758 | 758 | 758
|  | Utilisation (%) | 1.0897 | 2.0317 | 3.2926 | 4.6413 | 5.9765
|  | Hosting Capacity (A) | 749.7399 | 742.5994 | 733.042 | 722.8192 | 712.6983
|  | Power Factor | 0.48565 | 0.91075 | 0.97701 | 0.99317 | 0.99813
|  | N-1 Load (A) | 18.395 | 40.5549 | 67.653 | 96.049 | 123.9662
|  | N-1 Rating (A) | 758 | 758 | 758 | 758 | 758
|  | Contingency Utilisation (%) | 2.4268 | 5.3502 | 8.9252 | 12.6714 | 16.3544
|  | N-1 Hosting Capacity (A) | 739.605 | 717.4451 | 690.347 | 661.951 | 634.0338
|  | N-1 Power Factor | 0.48565 | 0.91075 | 0.97701 | 0.99317 | 0.99813
|  | N-1 Limiting section | 687-1(1) | 687-1(1) | 687-1(1) | 687-1(1) | 687-1(1)
|  | Contingency Scenario | F688 | F688 | F688 | F688 | F688
F687 | 687-2 | Load (A) | 2.2527 | 2.2527 | 2.2527 | 2.2527 | 2.2527
|  | Rating (A) | 495 | 495 | 495 | 495 | 495
|  | Utilisation (%) | 0.4551 | 0.4551 | 0.4551 | 0.4551 | 0.4551
|  | Hosting Capacity (A) | 492.7473 | 492.7473 | 492.7473 | 492.7473 | 492.7473
|  | Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 2.2528 | 2.2528 | 2.2529 | 2.2529 | 2.2529
|  | N-1 Rating (A) | 495 | 495 | 495 | 495 | 495
|  | Contingency Utilisation (%) | 0.45511 | 0.45512 | 0.45512 | 0.45513 | 0.45513
|  | N-1 Hosting Capacity (A) | 492.7472 | 492.7472 | 492.7471 | 492.7471 | 492.7471
|  | N-1 Power Factor | 1 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 687-2(2) | 687-2(2) | 687-2(2) | 687-2(2) | 687-2(2)
|  | Contingency Scenario | F688 | F688 | F688 | F688 | F688
F687 | 687-3 | Load (A) | 5.6698 | 14.3745 | 24.4749 | 34.9515 | 45.2191
|  | Rating (A) | 636 | 636 | 636 | 636 | 636
|  | Utilisation (%) | 0.89148 | 2.2601 | 3.8483 | 5.4955 | 7.1099
|  | Hosting Capacity (A) | 630.3302 | 621.6255 | 611.5251 | 601.0485 | 590.7809
|  | Power Factor | 0.70751 | 0.97575 | 0.99628 | 0.99967 | 0.99995
|  | N-1 Load (A) | 15.8219 | 39.4823 | 67.0525 | 95.668 | 123.7134
|  | N-1 Rating (A) | 636 | 636 | 636 | 636 | 636
|  | Contingency Utilisation (%) | 2.4877 | 6.2079 | 10.5428 | 15.0421 | 19.4518
|  | N-1 Hosting Capacity (A) | 620.1781 | 596.5177 | 568.9475 | 540.332 | 512.2866
|  | N-1 Power Factor | 0.70751 | 0.97575 | 0.99628 | 0.99967 | 0.99995
|  | N-1 Limiting section | 687-3 | 687-3 | 687-3 | 687-3 | 687-3
|  | Contingency Scenario | F688 | F688 | F688 | F688 | F688
F688 | 688-1 | Load (A) | 10.1949 | 25.1977 | 42.7269 | 60.9347 | 78.7869
|  | Rating (A) | 636 | 636 | 636 | 636 | 636
|  | Utilisation (%) | 1.603 | 3.9619 | 6.7181 | 9.5809 | 12.3879
|  | Hosting Capacity (A) | 625.8051 | 610.8023 | 593.2731 | 575.0653 | 557.2131
|  | Power Factor | 0.60763 | 0.93958 | 0.97797 | 0.98915 | 0.99385
|  | N-1 Load (A) | 15.8004 | 39.4817 | 67.0698 | 95.7076 | 123.7797
|  | N-1 Rating (A) | 636 | 636 | 636 | 636 | 636
|  | Contingency Utilisation (%) | 2.4843 | 6.2078 | 10.5456 | 15.0484 | 19.4622
|  | N-1 Hosting Capacity (A) | 620.1996 | 596.5183 | 568.9302 | 540.2924 | 512.2203
|  | N-1 Power Factor | 0.60763 | 0.93958 | 0.97797 | 0.98915 | 0.99385
|  | N-1 Limiting section | 688-1(1) | 688-1(1) | 688-1(1) | 688-1(1) | 688-1(1)
|  | Contingency Scenario | F687 | F687 | F687 | F687 | F687
F689 | 689-1 | Load (A) | 9.2967 | 9.2967 | 9.2967 | 9.2967 | 9.2967
|  | Rating (A) | 538 | 538 | 538 | 538 | 538
|  | Utilisation (%) | 1.728 | 1.728 | 1.728 | 1.728 | 1.728
|  | Hosting Capacity (A) | 528.7033 | 528.7033 | 528.7033 | 528.7033 | 528.7033
|  | Power Factor | 1 | 1 | 1 | 1 | 1
F690 | 690-1 | Load (A) | 26.9309 | 40.6808 | 54.6533 | 68.6841 | 82.1907
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 4.87 | 7.3564 | 9.8831 | 12.4203 | 14.8627
|  | Hosting Capacity (A) | 526.0691 | 512.3192 | 498.3467 | 484.3159 | 470.8093
|  | Power Factor | 0.99932 | 0.9999 | 1 | 0.99992 | 0.99975
|  | N-1 Load (A) | 48.2106 | 72.8325 | 97.8439 | 122.9504 | 147.1132
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 8.718 | 13.1704 | 17.6933 | 22.2333 | 26.6028
|  | N-1 Hosting Capacity (A) | 504.7894 | 480.1675 | 455.1561 | 430.0496 | 405.8868
|  | N-1 Power Factor | 0.99932 | 0.9999 | 1 | 0.99992 | 0.99975
|  | N-1 Limiting section | 690-1 | 690-1 | 690-1 | 690-1 | 690-1
|  | Contingency Scenario | F691 | F691 | F691 | F691 | F691
F691 | 691-1 | Load (A) | 21.3105 | 32.1895 | 43.2455 | 54.3478 | 65.0354
|  | Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Utilisation (%) | 3.8536 | 5.8209 | 7.8202 | 9.8278 | 11.7605
|  | Hosting Capacity (A) | 531.6895 | 520.8105 | 509.7545 | 498.6522 | 487.9646
|  | Power Factor | 0.99936 | 0.99993 | 0.99999 | 0.99988 | 0.9997
|  | N-1 Load (A) | 48.2071 | 72.8135 | 97.807 | 122.8928 | 147.033
|  | N-1 Rating (A) | 553 | 553 | 553 | 553 | 553
|  | Contingency Utilisation (%) | 8.7174 | 13.167 | 17.6866 | 22.2229 | 26.5882
|  | N-1 Hosting Capacity (A) | 504.7929 | 480.1865 | 455.193 | 430.1072 | 405.967
|  | N-1 Power Factor | 0.99936 | 0.99993 | 0.99999 | 0.99988 | 0.9997
|  | N-1 Limiting section | 691-1 | 691-1 | 691-1 | 691-1 | 691-1
|  | Contingency Scenario | F690 | F690 | F690 | F690 | F690
F692 | 692-1 | Load (A) | 25.3339 | 26.3742 | 30.3049 | 36.6078 | 44.2474
|  | Rating (A) | 421 | 421 | 421 | 421 | 421
|  | Utilisation (%) | 6.0176 | 6.2647 | 7.1983 | 8.6954 | 10.5101
|  | Hosting Capacity (A) | 395.6661 | 394.6258 | 390.6951 | 384.3922 | 376.7526
|  | Power Factor | 0.99142 | 0.28502 | 0.55718 | 0.73191 | 0.83089
|  | N-1 Load (A) | 25.4755 | 29.4722 | 42.1704 | 59.1609 | 77.5934
|  | N-1 Rating (A) | 465 | 465 | 465 | 465 | 465
|  | Contingency Utilisation (%) | 6.0512 | 7.0005 | 10.0167 | 14.0525 | 18.4307
|  | N-1 Hosting Capacity (A) | 439.5245 | 435.5278 | 422.8296 | 405.8391 | 387.4066
|  | N-1 Power Factor | 0.99142 | 0.28502 | 0.55718 | 0.73191 | 0.83089
|  | N-1 Limiting section | 692-1 | 692-1 | 692-1 | 692-1 | 692-1
|  | Contingency Scenario | F693 | F693 | F693 | F693 | F693
F693 | 693-1 | Load (A) | 25.334 | 26.392 | 30.3839 | 36.7727 | 44.5044
|  | Rating (A) | 421 | 421 | 421 | 421 | 421
|  | Utilisation (%) | 6.0176 | 6.2689 | 7.2171 | 8.7346 | 10.5711
|  | Hosting Capacity (A) | 395.666 | 394.608 | 390.6161 | 384.2273 | 376.4956
|  | Power Factor | 0.99877 | 0.28726 | 0.56046 | 0.73483 | 0.83313
|  | N-1 Load (A) |  | 29.2878 | 42.0431 | 59.0721 | 77.528
|  | N-1 Rating (A) | 465 | 465 | 465 | 465 | 465
|  | Contingency Utilisation (%) |  | 6.9567 | 9.9865 | 14.0314 | 18.4152
|  | N-1 Hosting Capacity (A) |  | 435.7122 | 422.9569 | 405.9279 | 387.472
|  | N-1 Power Factor |  | 0.28726 | 0.56046 | 0.73483 | 0.83313
|  | N-1 Limiting section |  | 693-1 | 693-1 | 693-1 | 693-1
|  | Contingency Scenario |  | F692 | F692 | F692 | F692
F694 | 694-1 | Load (A) | 23.5398 | 37.9309 | 60.322 | 83.1269 | 103.6954
|  | Rating (A) | 531 | 531 | 531 | 531 | 531
|  | Utilisation (%) | 4.4331 | 7.1433 | 11.3601 | 15.6548 | 19.5283
|  | Hosting Capacity (A) | 507.4602 | 493.0691 | 470.678 | 447.8731 | 427.3046
|  | Power Factor | 1 | 0.79727 | 0.93209 | 0.96975 | 0.98403
|  | N-1 Load (A) | 54.9202 | 108.923 | 163.4332 | 216.2315 | 262.8514
|  | N-1 Rating (A) | 531 | 531 | 531 | 531 | 531
|  | Contingency Utilisation (%) | 10.3428 | 20.5128 | 30.7784 | 40.7216 | 49.5012
|  | N-1 Hosting Capacity (A) | 476.0798 | 422.077 | 367.5668 | 314.7685 | 268.1486
|  | N-1 Power Factor | 1 | 0.79727 | 0.93209 | 0.96975 | 0.98403
|  | N-1 Limiting section | 694-1 | 694-1 | 694-1 | 694-1 | 694-1
|  | Contingency Scenario | F647 | F647 | F647 | F647 | F647
F700 | 700-1 | Load (A) | 114.2357 | 113.3355 | 112.8011 | 112.5685 | 112.5818
|  | Rating (A) | 517 | 517 | 517 | 517 | 517
|  | Utilisation (%) | 22.0959 | 21.9218 | 21.8184 | 21.7734 | 21.776
|  | Hosting Capacity (A) | 402.7643 | 403.6645 | 404.1989 | 404.4315 | 404.4182
|  | Power Factor | 0.23799 | 1 | 1 | 1 | 1
|  | N-1 Load (A) | 177.4649 | 176.0172 | 175.1561 | 174.7792 | 174.7973
|  | N-1 Rating (A) | 517 | 517 | 517 | 517 | 517
|  | Contingency Utilisation (%) | 34.3259 | 34.0459 | 33.8793 | 33.8064 | 33.8099
|  | N-1 Hosting Capacity (A) | 339.5351 | 340.9828 | 341.8439 | 342.2208 | 342.2027
|  | N-1 Power Factor | 0.23799 | 1 | 1 | 1 | 1
|  | N-1 Limiting section | 700-1 | 700-1 | 700-1 | 700-1 | 700-1
|  | Contingency Scenario | F617 | F617 | F617 | F617 | F617
F703 | F703-1 | Load (A) | 50.5729 | 38.7218 | 26.9784 | 21.9298 | 26.6865
|  | Rating (A) | 400 | 400 | 400 | 400 | 400
|  | Utilisation (%) | 12.6432 | 9.6805 | 6.7446 | 5.4825 | 6.6716
|  | Hosting Capacity (A) | 349.4271 | 361.2782 | 373.0216 | 378.0702 | 373.3135
|  | Power Factor | 0.9085 | 0.82989 | 0.5843 | 1 | 0.58276
|  | N-1 Load (A) | 80.026 | 59.3535 | 53.2611 | 47.6094 | 52.9341
|  | N-1 Rating (A) | 451 | 451 | 451 | 451 | 451
|  | Contingency Utilisation (%) | 20.0065 | 14.8384 | 13.3153 | 11.9024 | 13.2335
|  | N-1 Hosting Capacity (A) | 370.974 | 391.6465 | 397.7389 | 403.3906 | 398.0659
|  | N-1 Power Factor | 0.9085 | 0.82989 | 0.5843 | 1 | 0.58276
|  | N-1 Limiting section | F703-1 | F703-1 | F703-1 | F703-1 | F703-1
|  | Contingency Scenario | F410 | F410 | F571 | F571 | F539