## Coversheet
Generation Application Checklist - Under 5MVA following NER process 5A - Class A1 Generators
This document is to be used by the Proponent and Energex to determine whether a generation connection has included all of the required information, and to allow tracking of comments and issues.
Proponents are to make note of:
STNW1175
Please note this list is a general list and may not reflect all requirements in some cases. Please discuss specific questions with your project sponsor prior to application.
Release:
2023-09-10
ver3.2

## Application review checklist
Item | Description | Customer Check | NSP Comment | Reference | Status
Documentation completeness checklist
All Classes
1 | Energex Technical Assessment
2 | Completed Application Form
3 | Payment - does the customer wish to have an invoice issued during the completeness review?
4 | Single line diagrams of the proposed: • Connection arrangement and generating system clearly showing the connection point including primary electrical SLD for all collector circuits (if relevant), switching arrangements for each generating unit, including demonstration of break-before-make units or bumpless make-before-break switch arrangements, if applicable.
• Revenue meter location
• Protection systems and grid protection relay(s)
• SCADA and communications SLD if required
5 | EG unit information as relevant (see the relevant tab in this document)
6 | Verification of voltage control or power factor control mode
7 | Confirmation of operating mode (e.g. standby, bumpless, parallel) as defined in STNW1175
8 | Details of Interlocking, if relevant, including evidence of compliance with standards

## Rotating Machines
Rotating machines
| Data Description | Units
1 | Type of generator | Text
2 | Connection arrangement | Text
3 | Rotor type | Text
4 | Nominal rated output | kVA, kW, kVAr
5 | Nominal terminal voltage (line to neutral) | V or kV
6 | Highest voltage (line to neutral) | V or kV
7 | Rated lightning impulse withstand voltage | kVp
8 | Rated short duration power frequency withstand voltage | kV
9 | Maximum current | kA
10 | Rated short time withstand current | kA for seconds
11 | Ambient conditions for maximum current and withstand current | Text
12 | Synchronous reactance - D Axis (Xd) | PU
13 | Synchronous reactance - Q axis (Xq) | PU
14 | Transient reactance - D Axis (X'd) | PU
15 | Transient reactance - Q Axis (X'q) | PU
16 | Subtransient reactance - D Axis (X''d) | PU
17 | Subtransient reactance - Q Axis (X''q) | PU
18 | Open circuit transient time constant - D Axis | Seconds
19 | Open circuit transient time constant - Q Axis | Seconds
20 | Open circuit subtransient time constant - D Axis | Seconds
21 | Open circuit subtransient time constant - Q Axis | Seconds
22 | Armature resistance | PU
23 | Negative sequence resistance | PU
24 | Locked Rotor impedance (resistance and reactance) | PU
25 | Zero Sequence reactance | PU
26 | Grounding impedance (resistance and reactance) | Ohms
27 | Saturation co-efficient at 1.0PU and 1.2PU | -
28 | Mechanical inertia constant | Seconds
29 | Fault contribution from the EG unit(s) at the Distribution System boundary | kA
30 | Description of the proposed voltage, active power (P) and Reactive power (Q) control system including details of the operation and performance of the system under normal conditions, fault conditions, and distribution system disturbance conditions | Text

## IES
Inverter energy systems
| Data Description | Units
1 | Inverter model and associated data sheets | Text
2 | Inverter islanding protection details | Text
3 | Inverter reactive control capabilities | Text
4 | Panel capacity | W / kW
5 | Inverter capacity | kVA
6 | Information on inverter configuration - single or three-phase systems, number of inverters, electrical schematic if embedded in sub-boards | Text and diagrams
7 | Battery details, planned operating modes and dispatch schedule as applicable | Text and diagrams