## Limitations not addressed
Limitations Not Addressed
The following limitations currently do not have or require a planned solution.
Energex has contingency plans in place and is actively monitoring load developments in the supply area.
Location:
Links to maps of Energex’s network showing the location of all Energex’s bulk supply and zone substations can be found in the body of the DAPR.
Supply Point | Class | Limitation | Comments
Ashgrove West BS | Toowong ZS | N-1 limitation for the loss of a 33/11 kV 25MVA transformer | Monitoring load development.
Beenleigh BS | Coomera ZS | N-1 limitation for the loss of a 33/11 kV 25MVA transformer | Monitoring load development.
Belmont BS | Eight Mile Plains ZS Bus 2 | NCC limitation and N-1 limitation for the loss of a 33/11 kV 25MVA transformer | Monitoring load development.
Brendale BS | Whiteside ZS | N-1 limitation for the loss of a 33/11 kV 15MVA transformer | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Caboolture BS | Bribie Island ZS | N-1 limitation for the loss of a 33/11 kV 15MVA transformer | Monitoring load development.
Caboolture BS | Morayfield | N-1 limitation for the loss of a 33/11 kV 25MVA transformer | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Caboolture BS | Morayfield North | N-1 limitation for the loss of a 33/11 kV 25MVA transformer | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Coomera BS | Pimpama | N-1 limitation for the loss of a 33/11 kV 25MVA transformer | Monitoring load development.
Griffin BS | Mango Hill ZS Bus 2 | N-1 limitation for the loss of a 33/11 kV 25MVA transformer | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Griffin BS | Petrie ZS | N-1 limitation for the loss of a 33/11 kV 25MVA transformer | Monitoring load development.
Griffin BS | Kallangur ZS | NCC limitation | Monitoring load development.
Lytton BS | Fishermans Island B ZS | NCC limitation | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Palmwoods 132kV CP | Mooloolaba ZS | N-1 limitation for the loss of a 132/11 kV 30MVA transformer | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Palmwoods 132kV CP | Landsborough ZS | N-1 limitation for the loss of a 33/11 kV 25MVA transformer | Monitoring load development.
Palmwoods 132kV CP | Bells Creek Central ZS | N-1 limitation for the loss of a 110/11 kV 60MVA transformer | Monitoring load development.
Palmwoods 132kV CP | Nambour BS | N-1 limitation for the loss of a 132/33 kV 60MVA transformer | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Beaudesert BS | 33kV Feeder | Feeder 314 overloads when JBB TR2 is out of service | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Beenleigh BS | 33kV Feeder | Feeder 3751 exceeds NCC rating | Operational strategy to deploy generators.
Belmont BS | 33kV Feeder | Feeder 647 overloads when 694 is out of service | Monitoring load development.
Brown Plains BS | 33kV Feeder | Feeder 406A overloads when 453 is out of service | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Burleigh Heads BS | 33kV Feeder | Feeder 3755 exceeds NCC rating | Operational strategy to transfer load and deploy generators.
Burleigh Heads BS | 33kV Feeder | Feeder 453 exceeds NCC rating | Operational strategy to transfer load and deploy generators.
Caboolture BS | 33kV Feeder | Feeder 350 overloads when 412 is out of service | Operational strategy to remotely reconfigure network under contingency.
Caboolture BS | 33kV Feeder | Feeder 412 overloads when 350 is out of service | Operational strategy to remotely reconfigure network under contingency.
Caboolture BS | 33kV Feeder | Feeder 448 overloads when 322 is out of service | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Caboolture BS | 33kV Feeder | Feeder 461 overloads when 499 is out of service | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Caboolture BS | 33kV Feeder | Feeder 499 overloads when 461 is out of service | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Cleveland BS | 33kV Feeder | Feeder 413 overloads when 372 is out of service | Monitoring load development.
Doboy BS | 33kV Feeder | Feeder 581 overloads when 677 is out of service | Monitoring load development.
Doboy BS | 33kV Feeder | Feeder 677 overloads when 581 is out of service | Monitoring load development.
Griffin BS | 33 kV Feeder | Feeder 320 overloads when 3359 or MHL TR1 is out of service | Monitoring load development.
Griffin BS | 33 kV Feeder | Feeder 3359 overloads when 320 is out of service | Monitoring load development.
Hays Inlet BS | 33 kV Feeder | Feeder 305 overloads when 497 is out of service | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Hays Inlet BS | 33 kV Feeder | Feeder 311 overloads when 305 is out of service | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Hays Inlet BS | 33 kV Feeder | Feeder 3250 overloads when 497 is out of service | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Hays Inlet BS | 33 kV Feeder | Feeder 3251 overloads when 448 is out of service | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Hays Inlet BS | 33 kV Feeder | Feeder 326 overlaods when 325 is out of service | Monitoring load development.
Hays Inlet BS | 33 kV Feeder | Feeder 497 overloads when 3250 is out of service | Planning studies currently in progress, mitigation works likely to be beyond FY2028/29.
Hays Inlet BS | 33kV Feeder | Feeder 305 exceeds NCC rating | Operational strategy to transfer load and deploy generators.
Molendinar BS | 33kV Feeder | Feeder 389 overloads when 474A is out of service | Monitoring load development.
Molendinar BS | 33kV Feeder | Feeder 474A overloads when 394 is out of service | Monitoring load development.
Molendinar BS | 33kV Feeder | Feeder 474A exceeds NCC rating | Operational strategy to transfer load and deploy generators.
Nambour BS | 33kV Feeder | Feeder 344 exceeds NCC rating | Monitoring load development.
Runcorn BS | 33kV Feeder | Feeder 694 overloads when 647 is out of service | Monitoring load development.
Abermain CP | 110kV Feeder | Feeder F7259/1 exceeds NCC rating | Operational strategy to transfer load and deploy generators.
Postmans Ridge CP | 110kV Feeder | Feeder F726 exceeds NCC rating | Operational strategy to transfer load and deploy generators.