## Notes
Sub-Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2022-23 to 2026-27)
This workbook provides 5 year forecast capacity and loading information for sub-transmission feeders in the Energex network.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation due to COVID 19 impacts. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
The following sections list the 33kV feeders, their forecast loads, power factor, customer category and available load transfers. The feeder loads are calculated from load flow results using forecast substation demands. For the transmission and sub-transmission feeders, load flow studies are conducted for system normal and single contingency situations.
The forecast and capacity cut-off date for the winter season is 1 June of each year, and for the summer season is 1 December of each year. For example, 2023 winter forecast includes all committed projects with a proposed commissioning date up to 1 June 2023, and the 2022/23 summer forecast includes all committed projects with a proposed commissioning date up to 1 December 2022.
Assessment of 33kV feeders is performed under four possible risk periods: winter day, winter night, summer day and summer night. For the summer table, the worst case (highest) load between summer day and summer night has been represented in the table.
Peak, reconciled, compensated load forecasts have been used in the 33kV feeder analyses, with 50 PoE forecast load used for single contingency studies, and 10 PoE forecast load used for system normal studies.
Feeder capacities are shown for ECC and NCC. These ratings have also been adjusted for known committed projects. All load transfers associated with contingent condition include acceptable feeder voltage profiles.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
Interconnected feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
Power Factor (System Normal) | Lowest power factor along the feeder at 10 PoE Peak Load. Where the Power Factor is either 0 the feeder is a normally open feeder that does not have load under System Normal conditions.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween summer day and summer night.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites. It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders to meet this criteria and 10MVA (170A) is available for Rural feeders. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.

## 33kV Feeders - Summer
Bulk Supply Name | Feeder | From Substation | To Substation | Attributes | 2023 | 2024 | 2025 | 2026 | 2027 | Security Standard | Transfers | Hours above 95%
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | NCC Rating (A) | 505 | 505 | 505 | 505 | 505 | Urban | 70
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | 10 POE Load (A) | 166.375 | 162.3582 | 159.1555 | 157.5577 | 154.369
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | Power Factor | 0.97355 | 0.97477 | 0.97486 | 0.97546 | 0.97549
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | ECC Rating (A) | 505 | 505 | 505 | 505 | 505
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | 50 POE Load (A) | 370.237 | 364.2343 | 385.0485 | 382.0116 | 378.1543
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | 10 POE Load (A) | 0.19673 | 0.1968 | 0.19688 | 0.19693 | 0.19699
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | Power Factor | 1.4767e-05 | 1.4767e-05 | 1.4767e-05 | 1.4767e-05 | 1.4767e-05
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | 50 POE Load (A) | 330.3528 | 326.4109 | 359.2052 | 357.177 | 355.1143
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | NCC Rating (A) | 710 | 710 | 710 | 710 | 710 | Urban | 70
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | 10 POE Load (A) | 167.3429 | 163.3129 | 160.0997 | 158.4966 | 155.2973
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | Power Factor | 0.97794 | 0.97888 | 0.97886 | 0.97933 | 0.97935
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | ECC Rating (A) | 710 | 710 | 710 | 710 | 710
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | 50 POE Load (A) | 336.3003 | 328.1197 | 322.0187 | 317.9674 | 312.1034
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | NCC Rating (A) | 473 | 473 | 473 | 473 | 473 | Rural | 170
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | 10 POE Load (A) | 0.82851 | 0.82851 | 0.82851 | 0.82851 | 0.82851
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | Power Factor | -6.9808e-06 | -6.9808e-06 | -6.981e-06 | -6.9808e-06 | -6.981e-06
Abermain Bulk | 364-1 | Marburg | Rosewood | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Abermain Bulk | 364-1 | Marburg | Rosewood | 10 POE Load (A) | 84.2327 | 96.9894 | 111.6905 | 116.0822 | 116.4085
Abermain Bulk | 364-1 | Marburg | Rosewood | Power Factor | 0.99943 | 0.99977 | 1 | 0.99979 | 0.99959
Abermain Bulk | 364-1 | Marburg | Rosewood | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
Abermain Bulk | 364-1 | Marburg | Rosewood | 50 POE Load (A) | 144.3703 | 170.1802 | 194.7307 | 206.8327 | 207.3863
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | NCC Rating (A) | 746 | 746 | 746 | 746 | 746 | Rural | 170
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | 10 POE Load (A) | 368.2489 | 418.3654 | 473.967 | 496.2039 | 502.4561
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | Power Factor | 0.95219 | 0.95059 | 0.9413 | 0.93844 | 0.93685
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | ECC Rating (A) | 746 | 746 | 746 | 746 | 746
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | 50 POE Load (A) | 688.0621 | 802.6297 | 920.8537 | 976.8678 | 988.1318
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | 10 POE Load (A) | 0.0093803 | 0.0093383 | 0.0092746 | 0.0092458 | 0.0092323
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | Power Factor | 2.0182e-05 | 2.0181e-05 | 2.0182e-05 | 2.0181e-05 | 2.0183e-05
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | NCC Rating (A) | 804 | 804 | 804 | 804 | 804 | Rural | 170
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | 10 POE Load (A) | 368.6135 | 418.7456 | 474.3628 | 496.6086 | 502.8606
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | Power Factor | 0.95306 | 0.95153 | 0.94253 | 0.93982 | 0.93831
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | 50 POE Load (A) | 688.4364 | 803.0198 | 921.258 | 977.2792 | 988.5432
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | 10 POE Load (A) | 402.1985 | 456.9216 | 517.6334 | 541.9151 | 548.741
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | Power Factor | 0.93201 | 0.92901 | 0.91315 | 0.90689 | 0.9036
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | 50 POE Load (A) | 690.9994 | 803.9519 | 919.4936 | 973.7329 | 984.2671
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Rural | 170
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | 10 POE Load (A) | 402.2756 | 457.0018 | 517.7165 | 542 | 548.8258
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | Power Factor | 0.95567 | 0.95128 | 0.94652 | 0.94371 | 0.94374
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | 50 POE Load (A) | 691.0762 | 804.0312 | 919.5753 | 973.8157 | 984.3497
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | 10 POE Load (A) | 0.021063 | 0.020974 | 0.02084 | 0.02078 | 0.020751
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | Power Factor | 9.0274e-06 | 9.0274e-06 | 9.0276e-06 | 9.0276e-06 | 9.0272e-06
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | NCC Rating (A) | 530 | 530 | 530 | 530 | 530 | Rural | 170
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | 10 POE Load (A) | 260.5678 | 255.4117 | 168.3903 | 253.6079 | 252.4988
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | Power Factor | 0.94857 | 0.94862 | 0.94864 | 0.94867 | 0.94866
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | ECC Rating (A) | 530 | 530 | 530 | 530 | 530
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | 50 POE Load (A) | 432.1421 | 424.6847 | 254.5045 | 417.7993 | 416.1044
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | HighSec | 0
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | 10 POE Load (A) | 198.6922 | 194.7199 | 113.2588 | 191.6361 | 190.9431
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | Power Factor | 0.94007 | 0.94013 | 0.94015 | 0.94018 | 0.94017
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | 50 POE Load (A) | 436.6 | 428.9851 | 256.4434 | 421.8602 | 419.9324
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 499 | 499 | 499 | 499 | 499 | Urban | 70
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | 10 POE Load (A) | 213.1146 | 213.1146 | 213.1146 | 214.019 | 214.019
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | Power Factor | 0.99291 | 0.99269 | 0.99243 | 0.99242 | 0.99201
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | ECC Rating (A) | 499 | 499 | 499 | 499 | 499
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | 50 POE Load (A) | 420.4719 | 420.4719 | 420.4719 | 422.499 | 422.499
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 499 | 499 | 499 | 499 | 499 | Urban | 70
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | 10 POE Load (A) | 216.7362 | 216.7362 | 216.7362 | 217.656 | 217.656
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | Power Factor | 0.99354 | 0.99333 | 0.99308 | 0.99307 | 0.99268
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | ECC Rating (A) | 499 | 499 | 499 | 499 | 499
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | 50 POE Load (A) | 420.105 | 420.105 | 420.105 | 422.1264 | 422.1264
Abermain Bulk | 387-1 | Abermain BS | Marburg | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170
Abermain Bulk | 387-1 | Abermain BS | Marburg | 10 POE Load (A) | 172.4647 | 188.2071 | 209.5119 | 222.2788 | 230.4785
Abermain Bulk | 387-1 | Abermain BS | Marburg | Power Factor | 0.99526 | 0.99485 | 0.99293 | 0.99218 | 0.99159
Abermain Bulk | 387-1 | Abermain BS | Marburg | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
Abermain Bulk | 387-1 | Abermain BS | Marburg | 50 POE Load (A) | 230.9355 | 259.0664 | 290.9809 | 310.0353 | 318.9614
Abermain Bulk | 3901-1 | Karrabin | Amberley | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Abermain Bulk | 3901-1 | Karrabin | Amberley | 10 POE Load (A) | 190.5274 | 241.0214 | 296.091 | 316.8794 | 321.2949
Abermain Bulk | 3901-1 | Karrabin | Amberley | Power Factor | 0.94294 | 0.94046 | 0.92968 | 0.92846 | 0.92765
Abermain Bulk | 3901-1 | Karrabin | Amberley | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Abermain Bulk | 3901-1 | Karrabin | Amberley | 50 POE Load (A) | 357.9259 | 459.8433 | 562.0873 | 606.2306 | 611.7948
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | HighSec | 0
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | 10 POE Load (A) | 32.4517 | 32.049 | 112.0412 | 28.1996 | 27.5271
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | Power Factor | 0.92186 | 0.88882 | 0.87205 | 0.84476 | 0.8555
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | 50 POE Load (A) | 267.0794 | 263.1698 | 255.1603 | 257.3138 | 255.4193
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Rural | 170
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | 10 POE Load (A) | 66.5763 | 52.7066 | 48.9207 | 52.0922 | 62.1543
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | Power Factor | 0.81532 | 0.96689 | 0.96186 | 0.96135 | 0.94015
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | 50 POE Load (A) | 236.3493 | 247.7828 | 261.0482 | 276.9182 | 298.9257
Abermain Bulk | 436-2 | 436 Tee1 | Ebeneezer | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Abermain Bulk | 436-2 | 436 Tee1 | Ebeneezer | 10 POE Load (A) | 0.17112 | 0.17052 | 0.16879 | 0.16795 | 0.16733
Abermain Bulk | 436-2 | 436 Tee1 | Ebeneezer | Power Factor | 5.5134e-06 | 5.5137e-06 | 5.5134e-06 | 5.5136e-06 | 5.5134e-06
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | 10 POE Load (A) | 66.9784 | 52.8847 | 49.11 | 52.2813 | 62.3858
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | Power Factor | 0.81367 | 0.96575 | 0.96024 | 0.9601 | 0.93958
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | 50 POE Load (A) | 236.5367 | 247.8683 | 261.1384 | 277.0127 | 299.0421
Abermain Bulk | 445-1 | Abermain BS | Moggill | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Abermain Bulk | 445-1 | Abermain BS | Moggill | 10 POE Load (A) | 226.0835 | 220.6296 | 216.2812 | 214.1117 | 209.7821
Abermain Bulk | 445-1 | Abermain BS | Moggill | Power Factor | 0.97339 | 0.9744 | 0.97438 | 0.97488 | 0.97491
Abermain Bulk | 445-1 | Abermain BS | Moggill | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Abermain Bulk | 445-1 | Abermain BS | Moggill | 50 POE Load (A) | 329.1902 | 321.4286 | 315.6294 | 311.9429 | 306.1656
Abermain Bulk | 475-1 | Karrabin | Amberley | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Abermain Bulk | 475-1 | Karrabin | Amberley | 10 POE Load (A) | 187.7131 | 237.4613 | 291.7175 | 312.1989 | 316.5492
Abermain Bulk | 475-1 | Karrabin | Amberley | Power Factor | 0.94379 | 0.94132 | 0.93062 | 0.92941 | 0.9286
Abermain Bulk | 475-1 | Karrabin | Amberley | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Abermain Bulk | 475-1 | Karrabin | Amberley | 50 POE Load (A) | 357.6492 | 459.5717 | 561.8668 | 606.0493 | 611.6171
Abermain Bulk | 673-1 | Moggill | Kenmore | NCC Rating (A) | 960 | 960 | 960 | 960 | 960 | Urban | 70
Abermain Bulk | 673-1 | Moggill | Kenmore | 10 POE Load (A) | 3.4206 | 3.4231 | 3.4256 | 3.4274 | 3.4292
Abermain Bulk | 673-1 | Moggill | Kenmore | Power Factor | 2.3519e-06 | 2.3519e-06 | 2.3519e-06 | 2.3519e-06 | 2.3519e-06
Abermain Bulk | 673-1 | Moggill | Kenmore | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Abermain Bulk | 673-1 | Moggill | Kenmore | 50 POE Load (A)
Algester Bulk | 3400-1 | Algester BS | Calamvale | NCC Rating (A) | 694 | 694 | 694 | 694 | 694 | Urban | 70
Algester Bulk | 3400-1 | Algester BS | Calamvale | 10 POE Load (A) | 368.4803 | 363.7675 | 359.0643 | 356.2469 | 352.4957
Algester Bulk | 3400-1 | Algester BS | Calamvale | Power Factor | 0.98506 | 0.98529 | 0.98534 | 0.98542 | 0.9851
Algester Bulk | 3400-1 | Algester BS | Calamvale | ECC Rating (A) | 765 | 765 | 765 | 765 | 765
Algester Bulk | 3400-1 | Algester BS | Calamvale | 50 POE Load (A) | 648.252 | 638.913 | 631.4554 | 625.8699 | 620.291
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 687 | 687 | 687 | 687 | 687 | Urban | 70
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | 10 POE Load (A) | 170.9543 | 169.199 | 167.4445 | 166.5675 | 165.6907
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | Power Factor | 0.98766 | 0.98778 | 0.9879 | 0.98796 | 0.98801
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | ECC Rating (A) | 739 | 739 | 739 | 739 | 739
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | 50 POE Load (A) | 307.7892 | 306.0324 | 302.52 | 300.7643 | 299.0092
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 687 | 687 | 687 | 687 | 687 | Urban | 70
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | 10 POE Load (A) | 171.4443 | 169.684 | 167.9244 | 167.0449 | 166.1656
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | Power Factor | 0.98767 | 0.98779 | 0.98791 | 0.98797 | 0.98803
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | ECC Rating (A) | 739 | 739 | 739 | 739 | 739
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | 50 POE Load (A) | 307.7871 | 306.0303 | 302.5179 | 300.7623 | 299.0072
Algester Bulk | 3405-1 | Algester BS | Calamvale | NCC Rating (A) | 694 | 694 | 694 | 694 | 694 | Urban | 70
Algester Bulk | 3405-1 | Algester BS | Calamvale | 10 POE Load (A) | 368.9038 | 364.1855 | 359.4769 | 356.6563 | 352.9007
Algester Bulk | 3405-1 | Algester BS | Calamvale | Power Factor | 0.98506 | 0.98529 | 0.98533 | 0.98542 | 0.98509
Algester Bulk | 3405-1 | Algester BS | Calamvale | ECC Rating (A) | 765 | 765 | 765 | 765 | 765
Algester Bulk | 3405-1 | Algester BS | Calamvale | 50 POE Load (A) | 648.2462 | 638.9074 | 631.45 | 625.8647 | 620.2858
Archerfield Bulk | 597-1 | Rocklea | Salisbury | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Archerfield Bulk | 597-1 | Rocklea | Salisbury | 10 POE Load (A) | 222.7223 | 219.0167 | 217.1641 | 215.3155 | 211.6255
Archerfield Bulk | 597-1 | Rocklea | Salisbury | Power Factor | 0.97236 | 0.97309 | 0.97326 | 0.9733 | 0.97317
Archerfield Bulk | 597-1 | Rocklea | Salisbury | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Archerfield Bulk | 597-1 | Rocklea | Salisbury | 50 POE Load (A) | 188.2635 | 186.4276 | 182.7691 | 182.7691 | 179.1163
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | NCC Rating (A) | 523 | 523 | 523 | 523 | 523 | Urban | 70
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | 10 POE Load (A) | 390.8376 | 386.9893 | 381.4834 | 379.65 | 377.5955
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | Power Factor | 0.98704 | 0.98822 | 0.98936 | 0.9906 | 0.99139
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | ECC Rating (A) | 523 | 523 | 523 | 523 | 523
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | 50 POE Load (A)
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | 10 POE Load (A) | 279.2817 | 275.6074 | 272.8662 | 271.0324 | 268.273
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | Power Factor | 0.97026 | 0.97078 | 0.97104 | 0.97129 | 0.97132
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | 50 POE Load (A) | 489.3218 | 483.8916 | 476.6397 | 476.6397 | 469.3952
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | 10 POE Load (A) | 276.0851 | 272.453 | 269.7434 | 267.9306 | 265.2029
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | Power Factor | 0.97033 | 0.97085 | 0.97111 | 0.97135 | 0.97139
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | 50 POE Load (A) | 489.3498 | 483.9188 | 476.6661 | 476.6661 | 469.4207
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | NCC Rating (A) | 476 | 476 | 476 | 476 | 476 | Urban | 70
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | 10 POE Load (A) | 13.6173 | 13.6173 | 13.6173 | 13.6173 | 13.6173
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | Power Factor | 4.2657e-05 | 4.2657e-05 | 4.2657e-05 | 4.2657e-05 | 4.2657e-05
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | ECC Rating (A) | 476 | 476 | 476 | 476 | 476
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | 50 POE Load (A)
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 598 | 598 | 598 | 598 | 598 | Urban | 70
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | 10 POE Load (A) | 190.2147 | 187.5758 | 184.94 | 183.6233 | 181.6496
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | Power Factor | 0.99993 | 0.99995 | 0.99995 | 0.99995 | 0.99994
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | ECC Rating (A) | 598 | 598 | 598 | 598 | 598
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | 50 POE Load (A) | 250.9692 | 247.8938 | 244.8213 | 242.7747 | 239.7072
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 851 | 851 | 851 | 851 | 851 | Urban | 70
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | 10 POE Load (A) | 131.2894 | 129.4716 | 127.6559 | 126.7489 | 125.3892
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | Power Factor | 0.99044 | 0.99061 | 0.99064 | 0.99069 | 0.9905
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | ECC Rating (A) | 851 | 851 | 851 | 851 | 851
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | 50 POE Load (A) | 175.3855 | 173.2269 | 171.0702 | 169.6335 | 167.48
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 598 | 598 | 598 | 598 | 598 | Urban | 70
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | 10 POE Load (A) | 185.7973 | 183.2193 | 180.6444 | 179.3581 | 177.43
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | Power Factor | 0.99994 | 0.99995 | 0.99996 | 0.99996 | 0.99995
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | ECC Rating (A) | 672 | 672 | 672 | 672 | 672
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | 50 POE Load (A) | 248.5649 | 245.5192 | 242.4766 | 240.4498 | 237.4121
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 622 | 622 | 622 | 622 | 622 | Urban | 70
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | 10 POE Load (A) | 159.9035 | 157.2835 | 155.5378 | 153.7928 | 152.0486
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | Power Factor | 0.99088 | 0.99107 | 0.9912 | 0.99138 | 0.9914
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | ECC Rating (A) | 622 | 622 | 622 | 622 | 622
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | 50 POE Load (A)
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 622 | 622 | 622 | 622 | 622 | Urban | 70
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | 10 POE Load (A) | 160.0512 | 157.4245 | 155.6745 | 153.9253 | 152.1769
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | Power Factor | 0.99002 | 0.99023 | 0.99037 | 0.99057 | 0.9906
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | ECC Rating (A) | 622 | 622 | 622 | 622 | 622
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | 50 POE Load (A)
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | 10 POE Load (A) | 361.0802 | 358.3964 | 355.6379 | 354.7318 | 352.9589
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | Power Factor | 0.98007 | 0.98036 | 0.98055 | 0.98086 | 0.98064
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | 50 POE Load (A) | 636.8933 | 631.4652 | 627.8493 | 626.0423 | 622.4298
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | 10 POE Load (A) | 361.0087 | 358.2869 | 355.5677 | 354.6618 | 352.851
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | Power Factor | 0.98002 | 0.98031 | 0.9805 | 0.98081 | 0.98058
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | 50 POE Load (A) | 636.8924 | 631.4643 | 627.8485 | 626.0415 | 622.429
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | NCC Rating (A) | 492 | 492 | 492 | 492 | 492 | Urban | 70
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | 10 POE Load (A) | 17.1926 | 17.193 | 17.1933 | 17.1936 | 17.1937
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | Power Factor | 3.5471e-05 | 3.5471e-05 | 3.5471e-05 | 3.5471e-05 | 3.5471e-05
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | ECC Rating (A) | 492 | 492 | 492 | 492 | 492
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | 50 POE Load (A)
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | NCC Rating (A) | 492 | 492 | 492 | 492 | 492 | Urban | 70
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | 10 POE Load (A) | 17.0662 | 17.0667 | 17.067 | 17.0672 | 17.0674
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | Power Factor | 3.5079e-05 | 3.5079e-05 | 3.5079e-05 | 3.5079e-05 | 3.5079e-05
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | ECC Rating (A) | 492 | 492 | 492 | 492 | 492
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | 50 POE Load (A)
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | 10 POE Load (A) | 1.3762 | 1.3762 | 1.3762 | 1.3762 | 1.3762
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | Power Factor | 0.00013446 | 0.00013446 | 0.00013446 | 0.00013446 | 0.00013446
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | 50 POE Load (A)
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | 10 POE Load (A) | 92.587 | 92.607 | 92.6269 | 92.6474 | 92.6612
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | Power Factor | 0.9803 | 0.97992 | 0.97951 | 0.9796 | 0.97907
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | 50 POE Load (A) | 81.8091 | 81.8334 | 79.8323 | 81.8993 | 81.915
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | 10 POE Load (A) | 90.6426 | 105.3185 | 111.543 | 111.543 | 111.543
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | Power Factor | 0.99313 | 0.98932 | 0.98583 | 0.99365 | 0.99346
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | 50 POE Load (A) | 148.4015 | 171.3944 | 183.6273 | 183.6273 | 183.6273
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | 10 POE Load (A) | 61.0394 | 70.8977 | 75.0879 | 75.0879 | 75.0879
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | Power Factor | 0.99995 | 0.99982 | 0.99904 | 0.99998 | 0.99999
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | 50 POE Load (A) | 149.6262 | 173.093 | 185.5974 | 185.5974 | 185.5974
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | 10 POE Load (A) | 292.3113 | 295.2128 | 298.1587 | 302.0797 | 305.0513
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | Power Factor | 0.91648 | 0.91539 | 0.91393 | 0.91289 | 0.91107
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | 50 POE Load (A) | 402.5628 | 408.4894 | 416.4261 | 424.4034 | 430.4135
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Rural | 170
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | 10 POE Load (A) | 300.0602 | 302.976 | 305.9732 | 309.9263 | 312.9495
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | Power Factor | 0.95086 | 0.94999 | 0.94882 | 0.94798 | 0.94651
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | 50 POE Load (A) | 545.0268 | 551.6718 | 557.0142 | 565.1222 | 569.1214
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | 10 POE Load (A) | 148.9567 | 153.8654 | 156.8334 | 162.7723 | 165.7702
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | Power Factor | 0.94358 | 0.94261 | 0.94129 | 0.94038 | 0.93871
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | 50 POE Load (A) | 406.0758 | 412.6896 | 420.0169 | 428.0712 | 434.079
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | 10 POE Load (A) | 152.4731 | 150.4973 | 150.5287 | 148.5588 | 148.5792
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | Power Factor | 0.98239 | 0.98241 | 0.98241 | 0.98242 | 0.98237
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | 50 POE Load (A) | 302.0988 | 302.1223 | 297.7039 | 297.8218 | 295.5238
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | NCC Rating (A) | 766 | 766 | 766 | 766 | 766 | Urban | 70
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | 10 POE Load (A) | 410.4876 | 412.3949 | 407.0599 | 404.9967 | 402.2853
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | Power Factor | 0.99418 | 0.99446 | 0.99479 | 0.99503 | 0.99506
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | ECC Rating (A) | 766 | 766 | 766 | 766 | 766
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | 50 POE Load (A) | 662.8255 | 668.7918 | 660.942 | 657.0253 | 651.1512
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | NCC Rating (A) | 807 | 807 | 807 | 807 | 807 | Urban | 70
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | 10 POE Load (A) | 78.4104 | 73.0158 | 72.6973 | 72.8348 | 73.9814
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | Power Factor | 0.99997 | 1 | 0.99996 | 0.99983 | 0.9997
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | 50 POE Load (A) | 477.4295 | 471.8851 | 467.5006 | 465.315 | 463.4107
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | 10 POE Load (A)
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | Power Factor | 0.97112 | 0.9713 | 0.97143 | 0.97153 | 0.97154
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | 50 POE Load (A)
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | 10 POE Load (A) | 94.6227 | 97.2206 | 96.3408 | 96.3408 | 95.4815
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | Power Factor | 0.96909 | 0.96928 | 0.96942 | 0.96953 | 0.96954
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | 50 POE Load (A) | 184.6255 | 189.9835 | 188.1961 | 188.1961 | 186.41
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | 10 POE Load (A) | 1.4196 | 1.4196 | 1.4196 | 1.4196 | 1.4196
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | Power Factor | 0.00010523 | 0.00010523 | 0.00010523 | 0.00010523 | 0.00010523
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | 50 POE Load (A) | 331.9331 | 342.2022 | 352.1187 | 364.6574 | 370.9873
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Urban | 70
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | 10 POE Load (A) | 247.7903 | 243.4707 | 243.4707 | 241.3975 | 241.3975
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | Power Factor | 0.98574 | 0.98577 | 0.98575 | 0.98575 | 0.98566
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | 50 POE Load (A) | 401.8697 | 399.3554 | 393.8776 | 393.8776 | 388.566
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | NCC Rating (A) | 439 | 439 | 439 | 439 | 439 | Urban | 70
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | 10 POE Load (A) | 82.9614 | 80.9466 | 80.9466 | 79.0188 | 79.0187
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | Power Factor | 0.98956 | 0.98956 | 0.98951 | 0.98948 | 0.98938
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | ECC Rating (A) | 439 | 439 | 439 | 439 | 439
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | 50 POE Load (A) | 82.812 | 80.723 | 80.5108 | 80.5108 | 78.3494
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | NCC Rating (A) | 812 | 812 | 812 | 812 | 812 | Urban | 70
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | 10 POE Load (A) | 165.1518 | 162.8428 | 162.8428 | 162.6993 | 162.6993
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | Power Factor | 0.98244 | 0.98246 | 0.98246 | 0.98247 | 0.98243
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | ECC Rating (A) | 812 | 812 | 812 | 812 | 812
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | 50 POE Load (A) | 319.6365 | 319.2103 | 313.9395 | 313.9395 | 310.7702
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | NCC Rating (A) | 807 | 807 | 807 | 807 | 807 | Urban | 70
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | 10 POE Load (A) | 283.5924 | 287.1827 | 283.2247 | 281.5663 | 279.0563
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | Power Factor | 0.98654 | 0.98697 | 0.98739 | 0.98774 | 0.98775
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | ECC Rating (A) | 807 | 807 | 807 | 807 | 807
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | 50 POE Load (A) | 681.0199 | 686.7621 | 678.4589 | 674.3192 | 668.5671
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | NCC Rating (A) | 774 | 774 | 774 | 774 | 774 | Urban | 70
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | 10 POE Load (A) | 283.8514 | 287.4279 | 283.4688 | 281.8237 | 279.3145
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | Power Factor | 0.98912 | 0.98948 | 0.98985 | 0.99014 | 0.99015
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | ECC Rating (A) | 774 | 774 | 774 | 774 | 774
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | 50 POE Load (A) | 681.2639 | 687.0053 | 678.7013 | 674.5612 | 668.8099
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | NCC Rating (A) | 848 | 848 | 848 | 848 | 848 | Urban | 70
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | 10 POE Load (A) | 0.92549 | 0.9254 | 0.92569 | 0.92575 | 0.92604
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | Power Factor | -2.6742e-06 | -2.6744e-06 | -2.6738e-06 | -2.6749e-06 | -2.6743e-06
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | ECC Rating (A) | 712 | 712 | 712 | 712 | 712
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | 50 POE Load (A) | 310.5782 | 306.8793 | 301.1757 | 299.2594 | 295.4662
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | 10 POE Load (A) | 98.7928 | 101.4665 | 100.5689 | 100.5689 | 99.6717
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | Power Factor | 0.99898 | 0.99898 | 0.99898 | 0.99898 | 0.99898
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | 50 POE Load (A) | 184.516 | 189.8672 | 188.0821 | 188.0821 | 186.2983
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | NCC Rating (A) | 740 | 740 | 740 | 740 | 740 | Rural | 170
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | 10 POE Load (A) | 94.2386 | 96.8135 | 95.9548 | 95.9547 | 95.0964
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | Power Factor | 0.96927 | 0.9695 | 0.96968 | 0.96981 | 0.96982
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | 50 POE Load (A) | 184.2207 | 189.5757 | 187.7893 | 187.7893 | 186.0043
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 713
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | 10 POE Load (A) | 709.7772 | 704.2694 | 700.5757 | 698.7303 | 700.5037
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | Power Factor | 0.97436 | 0.97421 | 0.97398 | 0.97375 | 0.97333
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | 50 POE Load (A) | 713 | 707 | 705 | 702 | 703
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | 10 POE Load (A) | 363.5432 | 359.8724 | 356.2264 | 354.4049 | 352.625
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | Power Factor | 0.98338 | 0.98358 | 0.98378 | 0.98387 | 0.98397
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | 50 POE Load (A) | 347.271 | 344.9517 | 344.8565 | 344.729 | 346.7423
Beerwah Bulk | 324-1 | Woodford | Kilcoy | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Rural | 170
Beerwah Bulk | 324-1 | Woodford | Kilcoy | 10 POE Load (A) | 451.8993 | 246.688 | 73.6569 | 73.0079 | 73.0079
Beerwah Bulk | 324-1 | Woodford | Kilcoy | Power Factor | 0.98421 | 0.98381 | 0.98355 | 0.98349 | 0.98285
Beerwah Bulk | 324-1 | Woodford | Kilcoy | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
Beerwah Bulk | 324-1 | Woodford | Kilcoy | 50 POE Load (A) | 234.7447 | 225.8007
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Rural | 170
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | 10 POE Load (A) | 518.967 | 277.4115 | 228.6096 | 226.3584 | 226.3584
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | Power Factor | 0.93197 | 0.93077 | 0.92999 | 0.92982 | 0.92789
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | 50 POE Load (A) | 263.5714 | 250.3795 | 213.4954 | 211.2376 | 208.9894
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | NCC Rating (A) | 155 | 155 |  |  |  | Rural | 170
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | 10 POE Load (A) | 1.1707 | 1.1679
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | Power Factor | 0.00025447 | 0.00025447 | 0.00025447 | 0.00025447 | 0.00025447
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | 50 POE Load (A)
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | 10 POE Load (A) | 1.5517 | 1.5524 | 1.5532 | 1.5532 | 1.5539
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | Power Factor | 0.00031257 | 0.00031257 | 0.00031257 | 0.00031257 | 0.00031257
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | 50 POE Load (A)
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | NCC Rating (A) | 330 | 330 | 330 | 330 | 330 | Rural | 170
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | 10 POE Load (A) | 211.255 | 209.1045 | 206.9614 | 204.8257 | 204.8257
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | Power Factor | 0.9852 | 0.98533 | 0.98538 | 0.98543 | 0.98531
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | ECC Rating (A) | 300 | 300 | 300 | 300 | 300
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | 50 POE Load (A)
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Rural | 170
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | 10 POE Load (A) | 210.8414 | 208.6932 | 206.5524 | 204.419 | 204.419
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | Power Factor | 0.97108 | 0.97142 | 0.97156 | 0.97169 | 0.97136
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | 50 POE Load (A)
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | 10 POE Load (A) | 225.9077 | 242.6666 | 240.7958 | 240.7958 | 240.7958
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | Power Factor | 0.97974 | 0.97749 | 0.97634 | 0.97517 | 0.9747
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | 50 POE Load (A) | 518.615 | 548.5169 | 559.8346 | 569.8801 | 585.0266
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | 10 POE Load (A) | 92.2381 | 90.6131 | 89.7477 | 88.9364 | 88.414
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | Power Factor | 0.98478 | 0.98341 | 0.98225 | 0.98032 | 0.9795
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | 50 POE Load (A) | 172.8748 | 170.9538 | 168.8308 | 168.1911 | 166.506
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | 420 | 420 | 420 | 420 | 420 | Urban | 70
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | 10 POE Load (A)
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | ECC Rating (A) | 465 | 465 | 465 | 465 | 465
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | 50 POE Load (A)
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | 420 | 420 | 420 | 420 | 420 | Urban | 70
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | 10 POE Load (A)
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | ECC Rating (A) | 452 | 452 | 452 | 452 | 452
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | 50 POE Load (A)
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | NCC Rating (A) | 479 | 479 | 479 | 479 | 479 | Urban | 260
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | 10 POE Load (A) | 298.3785 | 419.0142 | 415.673 | 413.4943 | 413.4943
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | Power Factor | 0.98198 | 0.97216 | 0.97213 | 0.97211 | 0.97179
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | ECC Rating (A) | 479 | 479 | 479 | 479 | 479
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | 50 POE Load (A) | 547.2375 | 824.1718 | 814.3552 | 814.3552 | 817.619
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 70
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | 10 POE Load (A) | 277.0647 | 273.4701 | 269.1174 | 267.3217 | 263.7334
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | Power Factor | 0.96712 | 0.96766 | 0.968 | 0.96845 | 0.96824
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | ECC Rating (A) | 751 | 751 | 751 | 751 | 751
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | 50 POE Load (A) | 519.9692 | 512.7073 | 505.4547 | 500.021 | 494.5922
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 70
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | 10 POE Load (A) | 280.0258 | 276.3928 | 271.9935 | 270.1787 | 266.552
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | Power Factor | 0.96712 | 0.96766 | 0.968 | 0.96845 | 0.96824
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | ECC Rating (A) | 751 | 751 | 751 | 751 | 751
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | 50 POE Load (A) | 519.9152 | 512.655 | 505.4039 | 499.9714 | 494.5439
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 656 | 656 | 656 | 656 | 656 | Urban | 70
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | 10 POE Load (A) | 231.0726 | 228.3812 | 226.1393 | 224.7952 | 224.1982
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | Power Factor | 0.97679 | 0.97728 | 0.97753 | 0.978 | 0.97772
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | ECC Rating (A) | 737 | 737 | 737 | 737 | 737
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | 50 POE Load (A) | 302.3084 | 298.9131 | 295.7468 | 294.6161 | 292.8092
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 656 | 656 | 656 | 656 | 656 | Urban | 70
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | 10 POE Load (A) | 233.8095 | 231.086 | 228.8174 | 227.4572 | 226.8531
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | Power Factor | 0.97666 | 0.97715 | 0.9774 | 0.97787 | 0.97759
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | ECC Rating (A) | 737 | 737 | 737 | 737 | 737
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | 50 POE Load (A) | 304.0321 | 300.6175 | 297.4331 | 296.296 | 294.4788
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 421 | 421 | 421 | 421 | 421 | Urban | 70
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | 10 POE Load (A) | 180.5584 | 178.7852 | 177.0131 | 176.1274 | 175.2421
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | Power Factor | 0.97315 | 0.97334 | 0.97343 | 0.97352 | 0.97371
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | ECC Rating (A) | 465 | 465 | 465 | 465 | 465
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | 50 POE Load (A) | 333.4147 | 329.8488 | 328.0667 | 326.2852 | 322.7241
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 421 | 421 | 421 | 421 | 421 | Urban | 70
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | 10 POE Load (A) | 182.0447 | 180.2566 | 178.4696 | 177.5765 | 176.6836
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | Power Factor | 0.97344 | 0.97363 | 0.97372 | 0.97382 | 0.974
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | ECC Rating (A) | 465 | 465 | 465 | 465 | 465
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | 50 POE Load (A) | 333.3988 | 329.8333 | 328.0514 | 326.2701 | 322.7093
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | 10 POE Load (A) | 260.1822 | 255.7467 | 251.3175 | 248.6632 | 246.0111
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | Power Factor | 0.97875 | 0.97901 | 0.9791 | 0.97925 | 0.97917
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | ECC Rating (A) | 824 | 824 | 824 | 824 | 824
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | 50 POE Load (A) | 488.56 | 480.7085 | 472.8889 | 467.0445 | 461.2173
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Rural | 170
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | 10 POE Load (A) | 307.3204 | 302.3484 | 298.2933 | 295.8183 | 292.1095
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | Power Factor | 0.96437 | 0.96464 | 0.96477 | 0.96488 | 0.96468
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | 50 POE Load (A) | 614.8262 | 603.4242 | 594.6842 | 589.3429 | 583.2519
Brendale Bulk | 309-2 | 309 Tee1 | Samford | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Rural | 170
Brendale Bulk | 309-2 | 309 Tee1 | Samford | 10 POE Load (A) | 87.9824 | 85.8597 | 84.8117 | 83.4741 | 83.1445
Brendale Bulk | 309-2 | 309 Tee1 | Samford | Power Factor | 0.96706 | 0.96773 | 0.96764 | 0.96793 | 0.96845
Brendale Bulk | 309-2 | 309 Tee1 | Samford | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
Brendale Bulk | 309-2 | 309 Tee1 | Samford | 50 POE Load (A) | 292.8871 | 286.8033 | 282.7419 | 278.8093 | 276.7567
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | 10 POE Load (A) | 222.1582 | 219.0421 | 215.9664 | 215.0428 | 212.4039
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | Power Factor | 0.96406 | 0.9643 | 0.96442 | 0.96452 | 0.96426
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | 50 POE Load (A) | 662.8055 | 650.7875 | 641.2717 | 636.4462 | 629.4035
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Urban | 70
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | 10 POE Load (A) | 455.3029 | 448.1913 | 442.0946 | 438.9375 | 433.4505
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | Power Factor | 0.96668 | 0.96693 | 0.96705 | 0.96715 | 0.96694
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | 50 POE Load (A) | 633.1164 | 622.4977 | 614.0477 | 609.8375 | 603.5399
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | NCC Rating (A) | 792 | 792 | 792 | 792 | 792 | Urban | 70
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | 10 POE Load (A) | 455.4267 | 448.3328 | 442.237 | 439.0605 | 433.5913
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | Power Factor | 0.97096 | 0.97116 | 0.97126 | 0.97134 | 0.97117
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | ECC Rating (A) | 792 | 792 | 792 | 792 | 792
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | 50 POE Load (A) | 633.2405 | 622.6205 | 614.1695 | 609.9589 | 603.6606
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | 10 POE Load (A) | 0.10956 | 0.10966 | 0.10972 | 0.10977 | 0.10984
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | Power Factor | 2.0842e-06 | 2.0842e-06 | 2.0841e-06 | 2.0842e-06 | 2.0842e-06
Brendale Bulk | 333-1 | Brendale BS | Lawnton | NCC Rating (A) | 732 | 732 | 732 | 732 | 732 | Urban | 70
Brendale Bulk | 333-1 | Brendale BS | Lawnton | 10 POE Load (A) | 368.0409 | 365.9793 | 364.7207 | 364.9446 | 365.2362
Brendale Bulk | 333-1 | Brendale BS | Lawnton | Power Factor | 0.98326 | 0.98114 | 0.98109 | 0.98116 | 0.9809
Brendale Bulk | 333-1 | Brendale BS | Lawnton | ECC Rating (A) | 732 | 732 | 732 | 732 | 732
Brendale Bulk | 333-1 | Brendale BS | Lawnton | 50 POE Load (A) | 594.0418 | 595.1564 | 592.9326 | 592.5839 | 593.0017
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Urban | 70
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | 10 POE Load (A) | 170.1813 | 168.3913 | 166.6034 | 166.0079 | 165.2516
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | Power Factor | 0.98471 | 0.98543 | 0.98633 | 0.98691 | 0.98762
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | 50 POE Load (A) | 247.3109 | 244.6973 | 242.8075 | 241.8631 | 239.9756
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Rural | 170
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | 10 POE Load (A) | 39.8362 | 38.9324 | 38.7285 | 38.6505 | 38.457
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | Power Factor | 0.99346 | 0.99911 | 0.99946 | 0.99972 | 0.99991
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | 50 POE Load (A) | 227.7175 | 225.8365 | 221.963 | 219.8361 | 217.8647
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Rural | 170
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | 10 POE Load (A) | 81.6307 | 79.4457 | 78.5142 | 77.5024 | 76.4987
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | Power Factor | 0.93401 | 0.93437 | 0.9346 | 0.93494 | 0.93507
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | 50 POE Load (A) | 159.0726 | 157.1785 | 155.1469 | 153.0619 | 151.1067
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Rural | 170
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | 10 POE Load (A) | 84.7748 | 88.1484 | 87.9168 | 88.2556 | 88.5946
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | Power Factor | 0.99213 | 0.98952 | 0.98935 | 0.98928 | 0.98893
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | 50 POE Load (A) | 178.5375 | 182.6331 | 182.0057 | 183.1594 | 183.5915
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | NCC Rating (A) | 485 | 485 | 485 | 485 | 485 | Rural | 170
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | 10 POE Load (A) | 240.3807 | 241.123 | 239.5957 | 239.3916 | 238.0579
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | Power Factor | 0.94595 | 0.96058 | 0.96084 | 0.96103 | 0.96153
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | ECC Rating (A) | 485 | 485 | 485 | 485 | 485
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | 50 POE Load (A) | 333.7998 | 332.0576 | 330.2918 | 329.0159 | 328.5728
Brendale Bulk | 335-2 | 335 Tee | Whiteside | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Rural | 170
Brendale Bulk | 335-2 | 335 Tee | Whiteside | 10 POE Load (A) | 97.2872 | 95.7098 | 94.7171 | 93.8378 | 92.9227
Brendale Bulk | 335-2 | 335 Tee | Whiteside | Power Factor | 0.95041 | 0.95083 | 0.95109 | 0.9515 | 0.95161
Brendale Bulk | 335-2 | 335 Tee | Whiteside | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
Brendale Bulk | 335-2 | 335 Tee | Whiteside | 50 POE Load (A) | 156.3427 | 154.5183 | 152.5225 | 150.5764 | 148.6341
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | NCC Rating (A) | 485 | 485 | 485 | 485 | 485 | Rural | 170
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | 10 POE Load (A) | 151.0351 | 149.3642 | 149.1165 | 149.474 | 149.8316
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | Power Factor | 0.95647 | 0.98006 | 0.98006 | 0.98 | 0.97994
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | ECC Rating (A) | 485 | 485 | 485 | 485 | 485
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | 50 POE Load (A) | 246.0716 | 245.6569 | 245.0049 | 244.5228 | 244.9562
Brendale Bulk | 336-1 | Brendale BS | Strathpine | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | Urban | 70
Brendale Bulk | 336-1 | Brendale BS | Strathpine | 10 POE Load (A) | 194.4525 | 192.4046 | 190.3591 | 189.6778 | 188.8144
Brendale Bulk | 336-1 | Brendale BS | Strathpine | Power Factor | 0.9959 | 0.99626 | 0.9967 | 0.99698 | 0.99731
Brendale Bulk | 336-1 | Brendale BS | Strathpine | ECC Rating (A) | 455 | 455 | 455 | 455 | 455
Brendale Bulk | 336-1 | Brendale BS | Strathpine | 50 POE Load (A) | 263.1537 | 260.3697 | 258.3583 | 257.3532 | 255.3441
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | 10 POE Load (A) | 266.6723 | 262.1261 | 257.5864 | 254.8658 | 252.1475
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | Power Factor | 0.97842 | 0.97868 | 0.97877 | 0.97891 | 0.97884
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | ECC Rating (A) | 824 | 824 | 824 | 824 | 824
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | 50 POE Load (A) | 487.3507 | 479.5541 | 471.7874 | 465.9813 | 460.1913
Brendale Bulk | 337-1 | Brendale BS | Strathpine | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Urban | 70
Brendale Bulk | 337-1 | Brendale BS | Strathpine | 10 POE Load (A) | 159.4346 | 157.7554 | 156.0782 | 155.5196 | 154.8123
Brendale Bulk | 337-1 | Brendale BS | Strathpine | Power Factor | 0.99082 | 0.99133 | 0.99196 | 0.99234 | 0.99283
Brendale Bulk | 337-1 | Brendale BS | Strathpine | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
Brendale Bulk | 337-1 | Brendale BS | Strathpine | 50 POE Load (A) | 231.8581 | 229.4036 | 227.6304 | 226.7444 | 224.9733
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | 10 POE Load (A) | 70.758 | 69.9049 | 69.052 | 69.052 | 68.1992
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | Power Factor | 0.99971 | 0.99973 | 0.99973 | 0.99974 | 0.99973
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | 50 POE Load (A) | 128.5005 | 126.7719 | 125.0439 | 125.0439 | 123.3166
Brendale Bulk | 349-1 | Brendale BS | Lawnton | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Brendale Bulk | 349-1 | Brendale BS | Lawnton | 10 POE Load (A) | 397.5213 | 395.2512 | 393.9176 | 394.1829 | 394.4488
Brendale Bulk | 349-1 | Brendale BS | Lawnton | Power Factor | 0.98225 | 0.98001 | 0.97995 | 0.98002 | 0.97975
Brendale Bulk | 349-1 | Brendale BS | Lawnton | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Brendale Bulk | 349-1 | Brendale BS | Lawnton | 50 POE Load (A) | 606.7741 | 607.5908 | 605.3271 | 604.9414 | 605.3672
Brendale Bulk | 464-1 | Brendale BS | Samford | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Brendale Bulk | 464-1 | Brendale BS | Samford | 10 POE Load (A) | 221.8547 | 218.0302 | 215.1891 | 212.9836 | 210.2816
Brendale Bulk | 464-1 | Brendale BS | Samford | Power Factor | 0.97196 | 0.97215 | 0.97224 | 0.97232 | 0.97221
Brendale Bulk | 464-1 | Brendale BS | Samford | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Brendale Bulk | 464-1 | Brendale BS | Samford | 50 POE Load (A) | 337.9107 | 331.494 | 326.7283 | 323.3388 | 320.2228
Browns Plains Bulk | 406A-1 | Bethania | Kingston | NCC Rating (A) | 1000 | 1000 | 1000 | 1000 | 1000 | Urban | 70
Browns Plains Bulk | 406A-1 | Bethania | Kingston | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
Browns Plains Bulk | 406A-1 | Bethania | Kingston | Power Factor | 5.9382e-06 | 5.9385e-06 | 5.9381e-06 | 5.9382e-06 | 5.9384e-06
Browns Plains Bulk | 406A-1 | Bethania | Kingston | ECC Rating (A)
Browns Plains Bulk | 406A-1 | Bethania | Kingston | 50 POE Load (A)
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | NCC Rating (A) | 796 | 796 | 796 | 796 | 796 | Urban | 70
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | 10 POE Load (A) | 1.6998 | 1.6999 | 1.6997 | 1.6997 | 1.6997
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | Power Factor | 5.9382e-06 | 5.9385e-06 | 5.9381e-06 | 5.9382e-06 | 5.9384e-06
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | ECC Rating (A)
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | 50 POE Load (A)
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | NCC Rating (A) | 813 | 813 | 813 | 813 | 813 | Rural | 170
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | 10 POE Load (A) | 2.1805 | 2.1805 | 2.1805 | 2.1805 | 2.1805
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | Power Factor | 5.063e-05 | 5.063e-05 | 5.063e-05 | 5.063e-05 | 5.063e-05
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | 50 POE Load (A) | 539.1538 | 541.2956 | 543.4405 | 547.7396 | 566.4044
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | 10 POE Load (A) | 272.1502 | 269.4164 | 273.0621 | 272.1502 | 272.1502
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | Power Factor | 0.97882 | 0.97905 | 0.97899 | 0.97896 | 0.97867
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | 50 POE Load (A) | 611.1054 | 605.4902 | 607.8355 | 605.8363 | 605.888
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | Urban | 70
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | 10 POE Load (A) | 273.6663 | 270.9172 | 274.5834 | 273.6663 | 273.6663
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | Power Factor | 0.97858 | 0.97881 | 0.97875 | 0.97872 | 0.97843
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | 50 POE Load (A) | 614.5314 | 608.8844 | 611.2431 | 609.2327 | 609.2847
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | Urban | 70
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | 10 POE Load (A) | 593.1365 | 585.0566 | 579.0155 | 574.9969 | 568.9821
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | Power Factor | 0.96983 | 0.96984 | 0.96987 | 0.96994 | 0.96976
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | 50 POE Load (A)
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | 10 POE Load (A) | 589.1431 | 586.8727 | 584.8672 | 585.0691 | 583.065
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | Power Factor | 0.95589 | 0.9558 | 0.95613 | 0.95606 | 0.95589
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | 50 POE Load (A) | 932.2556 | 929.3325 | 925.0313 | 926.3136 | 923.2987
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | 10 POE Load (A) | 588.8235 | 586.5543 | 584.5499 | 584.7517 | 582.7487
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | Power Factor | 0.95589 | 0.95579 | 0.95612 | 0.95606 | 0.95588
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | 50 POE Load (A) | 932.0833 | 929.1607 | 924.8602 | 926.1423 | 923.128
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | 10 POE Load (A) | 184.4086 | 183.5348 | 182.5605 | 182.5605 | 181.784
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | Power Factor | 0.97208 | 0.97202 | 0.97253 | 0.97247 | 0.9723
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | 50 POE Load (A) | 271.0027 | 269.717 | 268.692 | 268.3088 | 267.5968
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | NCC Rating (A) | 532 | 532 | 532 | 532 | 532 | Urban | 70
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | 10 POE Load (A) | 164.9693 | 162.5441 | 160.1281 | 160.1281 | 157.5063
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | Power Factor | 0.97421 | 0.97431 | 0.97739 | 0.97729 | 0.97701
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | ECC Rating (A) | 532 | 532 | 532 | 532 | 532
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | 50 POE Load (A) | 349.6244 | 346.2014 | 344.3987 | 342.6112 | 340.8164
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | 10 POE Load (A) | 42.172 | 42.161 | 42.4935 | 43.9939 | 44.3267
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | Power Factor | -0.94562 | -0.94532 | -0.94374 | -0.94348 | -0.94265
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | 50 POE Load (A) | 246.2923 | 245.5972 | 246.1289 | 246.8229 | 248.0488
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | NCC Rating (A) | 717 | 715 | 717 | 717 | 715 | Urban | 70
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | 10 POE Load (A) | 42.3566 | 42.15 | 42.652 | 44.1504 | 44.316
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | Power Factor | 0.98095 | 0.97978 | 0.97983 | 0.97983 | 0.97985
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | 50 POE Load (A) | 246.388 | 245.6897 | 246.2213 | 246.9154 | 248.1413
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Urban | 70
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | 10 POE Load (A) | 317.2121 | 317.2139 | 317.195 | 319.1233 | 319.1042
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | Power Factor | 0.9575 | 0.95728 | 0.95711 | 0.95698 | 0.95666
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | 50 POE Load (A) | 298.9745 | 298.9779 | 298.9394 | 300.8788 | 302.7812
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | NCC Rating (A) | 654 | 654 | 654 | 654 | 654 | Urban | 70
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | 10 POE Load (A) | 473.8298 | 470.0557 | 468.1702 | 468.1702 | 468.1702
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | Power Factor | 0.976 | 0.9759 | 0.97573 | 0.97555 | 0.97523
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | NCC Rating (A) | 806 | 806 | 806 | 806 | 806 | Urban | 70
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | 10 POE Load (A) | 212.2747 | 211.214 | 210.0517 | 210.0517 | 209.1068
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | Power Factor | 0.97052 | 0.97046 | 0.97105 | 0.97098 | 0.9708
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | ECC Rating (A) | 806 | 806 | 806 | 806 | 806
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | 50 POE Load (A) | 351.4452 | 348.1248 | 346.2879 | 344.4519 | 342.617
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | NCC Rating (A) | 602 | 602 | 602 | 602 | 602 | Urban | 70
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | 10 POE Load (A) | 2.5602 | 2.5602 | 2.5602 | 2.5602 | 2.5602
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | Power Factor | 1.828e-05 | 1.828e-05 | 1.828e-05 | 1.828e-05 | 1.828e-05
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | 10 POE Load (A) | 1.2657 | 1.2657 | 1.2657 | 1.2657 | 1.2657
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | Power Factor | 3.1331e-05 | 3.1331e-05 | 3.1331e-05 | 3.1331e-05 | 3.1331e-05
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | 10 POE Load (A) | 0.47829 | 0.47829 | 0.47829 | 0.47829 | 0.47829
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | Power Factor | 2.8117e-05 | 2.8117e-05 | 2.8117e-05 | 2.8112e-05 | 2.8117e-05
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | 10 POE Load (A) | 0.3203 | 0.3203 | 0.3203 | 0.3203 | 0.3203
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | Power Factor | 4.0403e-06 | 4.0403e-06 | 4.0403e-06 | 4.0388e-06 | 4.0403e-06
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 509 | 509 | 509 | 509 | 509 | Urban | 70
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | 10 POE Load (A) | 290.3909 | 289.6651 | 288.2964 | 289.4935 | 292.2285
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | Power Factor | 0.97412 | 0.97384 | 0.9734 | 0.97302 | 0.97244
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | ECC Rating (A) | 509 | 509 | 509 | 509 | 509
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | 50 POE Load (A) | 423.0272 | 421.0295 | 419.8851 | 420.587 | 424.7635
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 509 | 509 | 509 | 509 | 509 | Urban | 70
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | 10 POE Load (A) | 305.3302 | 304.5671 | 303.1282 | 304.3868 | 307.2623
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | Power Factor | 0.96574 | 0.96542 | 0.96491 | 0.96448 | 0.96382
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | ECC Rating (A) | 509 | 509 | 509 | 509 | 509
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | 50 POE Load (A) | 432.4116 | 430.3724 | 429.204 | 429.9211 | 434.1853
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | NCC Rating (A) | 510 | 510 | 510 | 510 | 510 | Rural | 170
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | 10 POE Load (A) | 73.4228 | 71.6307 | 71.4251 | 69.8435 | 69.8558
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | Power Factor | 0.98843 | 0.9885 | 0.98851 | 0.9885 | 0.98842
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | ECC Rating (A) | 510 | 510 | 510 | 510 | 510
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | 50 POE Load (A) | 70.344 | 68.5377 | 68.3222 | 66.7406 | 66.7574
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | NCC Rating (A) | 457 | 457 | 457 | 457 | 457 | Rural | 170
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | 10 POE Load (A) | 73.7517 | 71.9568 | 71.6463 | 70.1667 | 70.179
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | Power Factor | 0.98627 | 0.98633 | 0.98633 | 0.98633 | 0.98626
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | ECC Rating (A) | 457 | 457 | 457 | 457 | 457
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | 50 POE Load (A) | 70.6666 | 68.8573 | 68.5375 | 67.0574 | 67.0741
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | NCC Rating (A) | 271 | 271 | 271 | 271 | 271 | Rural | 170
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | 10 POE Load (A) | 0.74865 | 0.74882 | 0.74885 | 0.74896 | 0.74885
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | Power Factor | 0.00012203 | 0.00012193 | 0.00012195 | 0.00012197 | 0.00012197
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | ECC Rating (A) | 271 | 271 | 271 | 271 | 271
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | 50 POE Load (A)
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | 10 POE Load (A) | 459.1389 | 474.4171 | 468.6293 | 466.114 | 461.4587
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | Power Factor | 0.98029 | 0.98035 | 0.98031 | 0.98024 | 0.9801
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | 50 POE Load (A) | 835.7702 | 856.0104 | 848.1566 | 839.6944 | 828.2935
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | NCC Rating (A) | 823 | 823 | 823 | 823 | 823 | Rural | 170
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | 10 POE Load (A) | 382.8032 | 388.0219 | 383.053 | 381.3261 | 377.4742
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | Power Factor | 0.96429 | 0.96439 | 0.96432 | 0.9642 | 0.9638
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | ECC Rating (A) | 823 | 823 | 823 | 823 | 823
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | 50 POE Load (A) | 892.3836 | 933.3542 | 920.6057 | 908.6436 | 893.1801
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | 10 POE Load (A) | 260.548 | 250.7432 | 247.1078 | 246.5893 | 244.0199
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | Power Factor | 0.98929 | 0.98936 | 0.98934 | 0.98929 | 0.98909
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | 50 POE Load (A) | 642.7911 | 635.8298 | 630.3691 | 624.3525 | 615.5317
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | NCC Rating (A) | 396 | 396 | 396 | 396 | 396 | Urban | 70
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | 10 POE Load (A) | 243.0109 | 241.4722 | 238.1896 | 237.0914 | 234.8801
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | Power Factor | 0.97911 | 0.97919 | 0.97914 | 0.97906 | 0.97879
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | ECC Rating (A) | 443 | 443 | 443 | 443 | 443
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | 50 POE Load (A) | 436.4056 | 431.1557 | 426.9607 | 424.7562 | 420.4875
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | NCC Rating (A) | 776 | 776 | 776 | 776 | 776 | Urban | 70
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | 10 POE Load (A) | 630.0467 | 629.5108 | 629.1456 | 633.7283 | 639.8903
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | Power Factor | 0.95742 | 0.9574 | 0.95743 | 0.95702 | 0.95692
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | ECC Rating (A) | 776 | 776 | 776 | 776 | 776
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | 50 POE Load (A) | 709.6169 | 707.8762 | 707.1642 | 710.5017 | 719.3062
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | NCC Rating (A) | 698 | 698 | 698 | 698 | 698 | Urban | 70
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | 10 POE Load (A) | 617.8698 | 617.8646 | 617.8469 | 623.9266 | 629.6213
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | Power Factor | 0.9881 | 0.98744 | 0.98656 | 0.98577 | 0.98461
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | ECC Rating (A) | 698 | 698 | 698 | 698 | 698
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | 50 POE Load (A) | 570.4287 | 570.3946 | 570.3855 | 574.4096 | 581.7335
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | NCC Rating (A) | 485 | 485 | 485 | 485 | 485 | Urban | 70
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | 10 POE Load (A) | 12.7586 | 12.4353 | 11.6591 | 10.9854 | 11.0242
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | Power Factor | 0.93705 | 0.80949 | 0.67847 | 0.60562 | 0.68576
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | ECC Rating (A) | 485 | 485 | 485 | 485 | 485
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | 50 POE Load (A) | 144.8967 | 143.1736 | 142.4811 | 141.8007 | 143.324
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | NCC Rating (A) | 402 | 402 | 402 | 402 | 402 | Urban | 70
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | 10 POE Load (A) | 241.724 | 240.1936 | 236.9287 | 235.8363 | 233.6369
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | Power Factor | 0.9818 | 0.98187 | 0.98182 | 0.98175 | 0.98149
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | 50 POE Load (A) | 436.8929 | 431.6379 | 427.4387 | 425.2338 | 420.959
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 260
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | 10 POE Load (A) | 587.85 | 586.7536 | 585.3763 | 588.983 | 594.0143
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | Power Factor | 0.95716 | 0.9572 | 0.95726 | 0.95699 | 0.95653
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | 50 POE Load (A) | 991.7802 | 990.7775 | 988.7878 | 993.3204 | 1002.4188
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 260
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | 10 POE Load (A) | 592.0714 | 590.9672 | 589.58 | 593.2126 | 598.2801
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | Power Factor | 0.9572 | 0.95724 | 0.95729 | 0.95702 | 0.95657
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | 50 POE Load (A) | 993.095 | 992.091 | 990.099 | 994.6368 | 1003.7458
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 746 | 746 | 746 | 746 | 746 | Urban | 70
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | 10 POE Load (A) | 498.1849 | 494.2979 | 489.2698 | 487.5169 | 483.6506
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | Power Factor | 0.97766 | 0.97768 | 0.97771 | 0.97766 | 0.97739
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | ECC Rating (A) | 746 | 746 | 746 | 746 | 746
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | 50 POE Load (A) | 645.5708 | 638.4715 | 633.1421 | 630.6937 | 625.292
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | 10 POE Load (A) | 113.2178 | 112.4618 | 110.8277 | 110.6407 | 109.0758
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | Power Factor | 1 | 1 | 1 | 0.99995 | 0.92775
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | 50 POE Load (A) | 310.9113 | 304.9332 | 300.8789 | 296.9104 | 293.2375
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | 10 POE Load (A) | 42.3796 | 42.3645 | 42.4872 | 43.1714 | 42.4721
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | Power Factor | 0.99363 | 0.99315 | 0.99231 | 0.99201 | 0.99153
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | 50 POE Load (A) | 331.8381 | 329.7507 | 327.6729 | 327.6729 | 325.5939
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | 10 POE Load (A) | 42.2894 | 42.2746 | 42.3972 | 43.0803 | 42.3824
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | Power Factor | 0.99539 | 0.9949 | 0.99411 | 0.9938 | 0.99332
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | 50 POE Load (A) | 331.6738 | 329.5869 | 327.5098 | 327.5098 | 325.4314
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | 10 POE Load (A) | 0.646 | 0.64613 | 0.64624 | 0.64632 | 0.64636
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | Power Factor | 1.4334e-05 | 1.4334e-05 | 1.4334e-05 | 1.4334e-05 | 1.4334e-05
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | 10 POE Load (A) | 467.1984 | 461.0816 | 453.5064 | 449.4588 | 442.9764
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | Power Factor | 0.9772 | 0.97754 | 0.97762 | 0.97789 | 0.96534
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | 50 POE Load (A) | 584.2768 | 575.2186 | 566.9379 | 560.7508 | 553.2808
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 611 | 611 | 611 | 611 | 611 | Urban | 308
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | 10 POE Load (A) | 448.4326 | 445.1747 | 441.356 | 440.7921 | 437.2357
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | Power Factor | 0.97123 | 0.97133 | 0.97118 | 0.97149 | 0.96837
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | ECC Rating (A) | 686 | 686 | 686 | 686 | 686
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | 50 POE Load (A) | 792.941 | 786.0791 | 781.5309 | 778.1681 | 772.7956
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | 10 POE Load (A) | 366.108 | 361.359 | 355.4786 | 352.5094 | 347.1618
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | Power Factor | 0.95712 | 0.95753 | 0.95801 | 0.95828 | 0.95868
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | 50 POE Load (A) | 573.2572 | 564.0535 | 555.899 | 549.8061 | 542.9569
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | 10 POE Load (A) | 421.8974 | 416.776 | 410.3339 | 407.3696 | 401.4367
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | Power Factor | 0.97683 | 0.97721 | 0.97728 | 0.97763 | 0.95838
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | 50 POE Load (A) | 607.2662 | 597.4874 | 588.9084 | 582.5733 | 574.9902
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | 10 POE Load (A) | 200.0299 | 198.3331 | 196.5127 | 195.4149 | 193.7384
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | Power Factor | 0.98901 | 0.98903 | 0.9891 | 0.98905 | 0.98888
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | 50 POE Load (A) | 468.4166 | 464.4481 | 460.4638 | 460.4215 | 456.467
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | 10 POE Load (A) | 200.0601 | 198.3975 | 196.5766 | 195.4786 | 193.8018
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | Power Factor | 0.99222 | 0.99222 | 0.99228 | 0.99223 | 0.99211
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | 50 POE Load (A) | 468.5023 | 464.5333 | 460.5487 | 460.5029 | 456.5481
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | 10 POE Load (A) | 0.00064707 | 0.0006471 | 0.00064713 | 0.00064715 | 0.00064717
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | Power Factor | 0.00030462 | 0.00030508 | 0.00030513 | 0.00030455 | 0.0003048
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 611 | 611 | 611 | 611 | 611 | Urban | 320
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | 10 POE Load (A) | 453.8673 | 450.5698 | 446.7048 | 446.134 | 442.5345
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | Power Factor | 0.97119 | 0.97129 | 0.97114 | 0.97145 | 0.96833
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | ECC Rating (A) | 611 | 611 | 611 | 611 | 611
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | 50 POE Load (A) | 793.5843 | 786.7175 | 782.1659 | 778.8009 | 773.4243
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | 10 POE Load (A) | 220.2914 | 218.57 | 216.3424 | 215.5659 | 213.8536
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | Power Factor | 0.99044 | 0.99045 | 0.99047 | 0.99043 | 0.99022
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | 50 POE Load (A) | 577.3764 | 571.0973 | 566.0251 | 563.8015 | 558.8816
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | NCC Rating (A) | 508 | 508 | 508 | 508 | 508 | Urban | 70
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | 10 POE Load (A) | 303.4479 | 301.6172 | 299.6581 | 298.9465 | 297.83
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | Power Factor | 0.98447 | 0.98448 | 0.98404 | 0.98395 | 0.98374
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | ECC Rating (A) | 508 | 508 | 508 | 508 | 508
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | 50 POE Load (A) | 453.627 | 449.8706 | 446.1447 | 445.0399 | 441.3363
Cleveland Bulk | 484-1 | Capalaba | Birkdale | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Cleveland Bulk | 484-1 | Capalaba | Birkdale | 10 POE Load (A) | 140.6348 | 138.0965 | 135.2038 | 133.6475 | 130.8407
Cleveland Bulk | 484-1 | Capalaba | Birkdale | Power Factor | 0.96756 | 0.9682 | 0.96837 | 0.96867 | 0.99954
Cleveland Bulk | 484-1 | Capalaba | Birkdale | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Cleveland Bulk | 484-1 | Capalaba | Birkdale | 50 POE Load (A) | 568.9616 | 558.2362 | 550.3763 | 543.9978 | 535.5101
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | 10 POE Load (A) | 326.415 | 324.6179 | 322.8221 | 322.8221 | 321.9247
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | Power Factor | 0.97702 | 0.97711 | 0.97692 | 0.9767 | 0.97651
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | 50 POE Load (A) | 607.3141 | 603.6317 | 599.9528 | 599.9528 | 599.9528
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 70
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | 10 POE Load (A) | 368.2728 | 379.972 | 433.9583 | 451.249 | 468.7522
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | Power Factor | 0.98004 | 0.97863 | 0.97754 | 0.97641 | 0.97604
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | 50 POE Load (A) | 717.3712 | 742.5806 | 856.3861 | 892.2723 | 931.2471
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 70
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | 10 POE Load (A) | 371.1695 | 382.9607 | 437.3714 | 454.798 | 472.4389
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | Power Factor | 0.97997 | 0.97856 | 0.97746 | 0.97634 | 0.97596
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | 50 POE Load (A) | 716.9185 | 742.0841 | 855.668 | 891.4648 | 930.3319
Coomera Bulk | 394-1 | Coomera BS | Hope Is | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
Coomera Bulk | 394-1 | Coomera BS | Hope Is | 10 POE Load (A) | 334.2877 | 332.4467 | 330.607 | 330.607 | 329.6877
Coomera Bulk | 394-1 | Coomera BS | Hope Is | Power Factor | 0.98131 | 0.98139 | 0.98122 | 0.98102 | 0.98085
Coomera Bulk | 394-1 | Coomera BS | Hope Is | ECC Rating (A) | 716 | 716 | 716 | 716 | 716
Coomera Bulk | 394-1 | Coomera BS | Hope Is | 50 POE Load (A) | 609.2296 | 605.5332 | 601.8402 | 601.8402 | 601.8402
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | 10 POE Load (A) | 217.7511 | 215.0268 | 212.305 | 211.3983 | 209.5856
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | Power Factor | 0.97397 | 0.97396 | 0.9739 | 0.97388 | 0.97368
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | 50 POE Load (A) | 417.3289 | 411.5118 | 405.711 | 403.7809 | 399.926
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | 10 POE Load (A) | 213.5793 | 210.9072 | 208.2375 | 207.3482 | 205.5703
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | Power Factor | 0.97393 | 0.97392 | 0.97386 | 0.97384 | 0.97364
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | 50 POE Load (A) | 417.9798 | 412.1383 | 406.3138 | 404.3759 | 400.5058
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | NCC Rating (A) | 721 | 721 | 721 | 721 | 721 | Urban | 70
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | 10 POE Load (A) | 2.2095 | 2.2095 | 2.2095 | 2.2095 | 2.2095
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | Power Factor | -6.6107e-07 | -6.6105e-07 | -6.6107e-07 | -6.6105e-07 | -6.6103e-07
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 766 | 766 | 766 | 766 | 766 | Urban | 70
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | 10 POE Load (A) | 325.0481 | 320.4561 | 316.788 | 313.859 | 310.0306
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | Power Factor | 0.97378 | 0.97428 | 0.97467 | 0.97545 | 0.9763
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | ECC Rating (A) | 766 | 766 | 766 | 766 | 766
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | 50 POE Load (A) | 611.1876 | 602.0225 | 594.7015 | 589.5301 | 582.5218
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 766 | 766 | 766 | 766 | 766 | Urban | 70
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | 10 POE Load (A) | 325.0481 | 320.4561 | 316.7879 | 313.859 | 310.0306
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | Power Factor | 0.97378 | 0.97428 | 0.97467 | 0.97545 | 0.9763
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | 50 POE Load (A) | 611.1876 | 602.0225 | 594.7015 | 589.5301 | 582.5218
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | 10 POE Load (A) | 0.59839 | 0.59843 | 0.59846 | 0.59849 | 0.59853
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | Power Factor | 1.126e-05 | 1.126e-05 | 1.126e-05 | 1.126e-05 | 1.126e-05
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | 10 POE Load (A) | 0.059429 | 0.059433 | 0.059435 | 0.059438 | 0.059442
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | Power Factor | 1.5497e-05 | 1.55e-05 | 1.5497e-05 | 1.5498e-05 | 1.5495e-05
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | NCC Rating (A) | 850 | 850 | 850 | 850 | 850 | Urban | 70
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | 10 POE Load (A) | 0.88309 | 0.88314 | 0.88318 | 0.88323 | 0.88328
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | Power Factor | 2.2116e-05 | 2.2116e-05 | 2.2116e-05 | 2.2116e-05 | 2.2116e-05
Doboy Bulk | 3426-1 | Queensport | Bulimba | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Doboy Bulk | 3426-1 | Queensport | Bulimba | 10 POE Load (A) | 297.1745 | 292.8786 | 289.6555 | 286.448 | 284.3042
Doboy Bulk | 3426-1 | Queensport | Bulimba | Power Factor | 0.96016 | 0.96035 | 0.96042 | 0.96053 | 0.96039
Doboy Bulk | 3426-1 | Queensport | Bulimba | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Doboy Bulk | 3426-1 | Queensport | Bulimba | 50 POE Load (A) | 422.013 | 414.7504 | 409.2983 | 405.678 | 403.8586
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | 10 POE Load (A) | 181.8301 | 180.6952 | 178.3479 | 176.896 | 174.554
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | Power Factor | 0.96696 | 0.96716 | 0.96724 | 0.96736 | 0.96727
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | 50 POE Load (A) | 406.5975 | 400.9304 | 395.275 | 391.8265 | 388.0599
Doboy Bulk | 416-1 | Doboy BS | Murarrie | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Urban | 70
Doboy Bulk | 416-1 | Doboy BS | Murarrie | 10 POE Load (A) | 202.525 | 200.7302 | 198.9363 | 198.9363 | 197.1431
Doboy Bulk | 416-1 | Doboy BS | Murarrie | Power Factor | 0.99777 | 0.99778 | 0.99782 | 0.9979 | 0.99783
Doboy Bulk | 416-1 | Doboy BS | Murarrie | ECC Rating (A) | 470 | 470 | 470 | 470 | 470
Doboy Bulk | 416-1 | Doboy BS | Murarrie | 50 POE Load (A) | 382.9039 | 379.2229 | 375.5469 | 375.5469 | 373.7108
Doboy Bulk | 443-1 | Queensport | Bulimba | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Doboy Bulk | 443-1 | Queensport | Bulimba | 10 POE Load (A) | 210.2526 | 207.2143 | 204.9348 | 202.6663 | 201.1501
Doboy Bulk | 443-1 | Queensport | Bulimba | Power Factor | 0.96867 | 0.96883 | 0.96888 | 0.96897 | 0.96885
Doboy Bulk | 443-1 | Queensport | Bulimba | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Doboy Bulk | 443-1 | Queensport | Bulimba | 50 POE Load (A) | 424.4588 | 417.1166 | 411.6111 | 407.9559 | 406.119
Doboy Bulk | 558-1 | Hemmant | Tingalpa | NCC Rating (A) | 680 | 680 | 680 | 680 | 680 | Urban | 70
Doboy Bulk | 558-1 | Hemmant | Tingalpa | 10 POE Load (A) | 241.571 | 237.6008 | 234.4572 | 232.2566 | 229.1204
Doboy Bulk | 558-1 | Hemmant | Tingalpa | Power Factor | 0.96191 | 0.96215 | 0.96224 | 0.96235 | 0.96225
Doboy Bulk | 558-1 | Hemmant | Tingalpa | ECC Rating (A) | 680 | 680 | 680 | 680 | 680
Doboy Bulk | 558-1 | Hemmant | Tingalpa | 50 POE Load (A) | 403.4473 | 397.9393 | 392.3845 | 388.989 | 385.2879
Doboy Bulk | 563-1 | Doboy BS | Hemmant | NCC Rating (A) | 371 | 371 | 371 | 371 | 371 | Urban | 70
Doboy Bulk | 563-1 | Doboy BS | Hemmant | 10 POE Load (A) | 203.2392 | 214.4399 | 211.9533 | 211.7146 | 209.2316
Doboy Bulk | 563-1 | Doboy BS | Hemmant | Power Factor | 0.97955 | 0.97975 | 0.97984 | 0.97997 | 0.9799
Doboy Bulk | 563-1 | Doboy BS | Hemmant | ECC Rating (A) | 429 | 429 | 429 | 429 | 429
Doboy Bulk | 563-1 | Doboy BS | Hemmant | 50 POE Load (A) | 363.7226 | 383.1524 | 380.0671 | 378.0125 | 375.9596
Doboy Bulk | 564-1 | Doboy BS | Hemmant | NCC Rating (A) | 371 | 371 | 371 | 371 | 371 | Urban | 70
Doboy Bulk | 564-1 | Doboy BS | Hemmant | 10 POE Load (A) | 195.1874 | 205.9445 | 203.5564 | 203.3271 | 200.9425
Doboy Bulk | 564-1 | Doboy BS | Hemmant | Power Factor | 0.97659 | 0.9768 | 0.9769 | 0.97704 | 0.97696
Doboy Bulk | 564-1 | Doboy BS | Hemmant | ECC Rating (A) | 429 | 429 | 429 | 429 | 429
Doboy Bulk | 564-1 | Doboy BS | Hemmant | 50 POE Load (A) | 362.5706 | 381.9435 | 378.8674 | 376.8189 | 374.7721
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Urban | 70
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | 10 POE Load (A) | 191.4241 | 189.7273 | 188.0314 | 188.0314 | 186.3362
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | Power Factor | 0.99726 | 0.99728 | 0.99732 | 0.99741 | 0.99733
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | ECC Rating (A) | 475 | 475 | 475 | 475 | 475
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | 50 POE Load (A) | 383.3439 | 379.6467 | 375.9547 | 375.9547 | 374.1109
Doboy Bulk | 581-1 | Doboy BS | Queensport | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 166 | 8
Doboy Bulk | 581-1 | Doboy BS | Queensport | 10 POE Load (A) | 537.6111 | 532.3374 | 527.0751 | 524.4406 | 520.9383
Doboy Bulk | 581-1 | Doboy BS | Queensport | Power Factor | 0.97414 | 0.97428 | 0.97439 | 0.97461 | 0.97445
Doboy Bulk | 581-1 | Doboy BS | Queensport | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
Doboy Bulk | 581-1 | Doboy BS | Queensport | 50 POE Load (A) | 927.9818 | 917.9105 | 907.8419 | 904.5014 | 899.4683
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | NCC Rating (A) | 433 | 433 | 433 | 433 | 433 | HighSec | 0
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | 10 POE Load (A) | 5.3007 | 5.3007 | 5.3007 | 5.3007 | 5.3007
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | Power Factor | 2.1138e-05 | 2.1138e-05 | 2.1138e-05 | 2.1138e-05 | 2.1138e-05
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | ECC Rating (A) | 433 | 433 | 433 | 433 | 433
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | 50 POE Load (A)
Doboy Bulk | 677-1 | Doboy BS | Queensport | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 166 | 8
Doboy Bulk | 677-1 | Doboy BS | Queensport | 10 POE Load (A) | 536.1156 | 530.8566 | 525.6089 | 522.9818 | 519.4892
Doboy Bulk | 677-1 | Doboy BS | Queensport | Power Factor | 0.97415 | 0.97429 | 0.9744 | 0.97462 | 0.97446
Doboy Bulk | 677-1 | Doboy BS | Queensport | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
Doboy Bulk | 677-1 | Doboy BS | Queensport | 50 POE Load (A) | 927.7812 | 917.7117 | 907.6449 | 904.305 | 899.2728
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | NCC Rating (A) | 821 | 821 | 821 | 821 | 821 | Rural | 170
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | 10 POE Load (A) | 266.8337 | 272.0098 | 269.3051 | 269.3207 | 266.665
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | Power Factor | 0.98448 | 0.98499 | 0.98524 | 0.98571 | 0.98585
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | ECC Rating (A) | 959 | 959 | 959 | 959 | 959
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | 50 POE Load (A) | 408.0347 | 402.2122 | 400.2602 | 398.3101 | 392.5358
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | 10 POE Load (A) | 0.0043955 | 0.0043954 | 0.0043954 | 0.0043954 | 0.0043955
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | Power Factor | 4.5101e-05 | 4.5101e-05 | 4.5115e-05 | 4.512e-05 | 4.5111e-05
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | 10 POE Load (A) | 266.9159 | 272.1006 | 269.4112 | 269.4112 | 266.7473
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | Power Factor | 0.9843 | 0.98481 | 0.98506 | 0.98553 | 0.98567
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | 50 POE Load (A) | 408.1187 | 402.2959 | 400.3437 | 398.3935 | 392.6187
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | 10 POE Load (A) | 267.1664 | 272.3916 | 269.6881 | 269.6881 | 267.0282
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | Power Factor | 0.99027 | 0.99062 | 0.99079 | 0.99111 | 0.99121
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | 50 POE Load (A) | 408.38 | 402.5565 | 400.604 | 398.6533 | 392.8773
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Rural | 170
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | 10 POE Load (A) | 0.58818 | 0.588 | 0.58809 | 0.58812 | 0.58818
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | Power Factor | 3.0304e-05 | 3.0304e-05 | 3.0304e-05 | 3.0304e-05 | 3.0304e-05
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | NCC Rating (A) | 764 | 764 | 764 | 764 | 764 | Rural | 170
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | 10 POE Load (A) | 35.6542 | 35.6542 | 34.7676 | 34.7676 | 34.7676
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | Power Factor | 0.96836 | 0.96871 | 0.96896 | 0.9694 | 0.96963
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | 50 POE Load (A) | 68.0736 | 68.0736 | 66.2879 | 66.2879 | 66.2879
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | NCC Rating (A) | 764 | 764 | 764 | 764 | 764 | Rural | 170
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | 10 POE Load (A) | 35.6427 | 35.6427 | 34.7567 | 34.7567 | 34.7567
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | Power Factor | 0.96822 | 0.96857 | 0.96882 | 0.96925 | 0.96949
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | 50 POE Load (A) | 68.0738 | 68.0738 | 66.288 | 66.288 | 66.288
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | NCC Rating (A) | 821 | 821 | 821 | 821 | 821 | Rural | 170
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | 10 POE Load (A) | 272.9634 | 290.6769 | 287.4967 | 287.4967 | 284.3459
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | Power Factor | 0.98047 | 0.98107 | 0.98139 | 0.98196 | 0.98218
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | ECC Rating (A) | 821 | 821 | 821 | 821 | 821
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | 50 POE Load (A) | 511.7144 | 536.831 | 530.6317 | 528.576 | 524.1071
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | 10 POE Load (A) | 0.0045542 | 0.0045541 | 0.0045541 | 0.0045541 | 0.0045541
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | Power Factor | 4.3524e-05 | 4.3536e-05 | 4.3524e-05 | 4.3525e-05 | 4.353e-05
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | 10 POE Load (A) | 274.1645 | 291.9051 | 288.7205 | 288.7205 | 285.5664
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | Power Factor | 0.98323 | 0.98375 | 0.98403 | 0.98453 | 0.98473
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | 50 POE Load (A) | 512.9637 | 538.0993 | 531.8965 | 529.8393 | 525.3626
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | 10 POE Load (A) | 0.0045542 | 0.0045541 | 0.0045541 | 0.0045541 | 0.0045541
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | Power Factor | -6.7679e-05 | -6.769e-05 | -6.7698e-05 | -6.7697e-05 | -6.7685e-05
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee1 | 10 POE Load (A) | 0.0045542 | 0.0045541 | 0.0045541 | 0.0045541 | 0.0045541
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee1 | Power Factor | 1 | 1 | 1 | 1 | 1
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | 10 POE Load (A) | 171.4835 | 163.0002 | 161.8142 | 160.9635 | 160.67
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | Power Factor | 0.99749 | 0.99765 | 0.99769 | 0.99781 | 0.99779
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | 50 POE Load (A) | 415.3891 | 410.2897 | 408.191 | 406.1737 | 400.1367
Gatton Bulk | 531-1 | Gatton | Tenthill | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
Gatton Bulk | 531-1 | Gatton | Tenthill | 10 POE Load (A) | 68.7504 | 68.7947 | 68.7726 | 66.9516 | 66.9378
Gatton Bulk | 531-1 | Gatton | Tenthill | Power Factor | 0.96943 | 0.96941 | 0.96942 | 0.96935 | 0.96936
Gatton Bulk | 531-1 | Gatton | Tenthill | ECC Rating (A) | 155 | 200 | 200 | 200 | 200
Gatton Bulk | 531-1 | Gatton | Tenthill | 50 POE Load (A) | 69.1954 | 67.4211 | 67.3867 | 67.3652 | 63.5996
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | 10 POE Load (A) | 0.0023146 | 0.0023131 | 0.0023139 | 0.0023147 | 0.0023151
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | Power Factor | 8.2581e-05 | 8.2584e-05 | 8.2592e-05 | 8.2616e-05 | 8.2577e-05
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | NCC Rating (A) | 78 | 78 | 78 | 78 | 78 | Rural | 170
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | 10 POE Load (A) | 21.6438 | 21.6625 | 21.655 | 21.655 | 21.6426
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | Power Factor | 0.91824 | 0.91846 | 0.9186 | 0.91878 | 0.91887
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | ECC Rating (A) | 78 | 78 | 78 | 78 | 78
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | 50 POE Load (A) | 22.3308 | 22.3538 | 22.3425 | 22.3355 | 20.5089
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | 10 POE Load (A) | 64.8974 | 75.3993 | 81.879 | 89.1848 | 94.8792
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | Power Factor | 0.98643 | 0.98835 | 0.98595 | 0.98408 | 0.98037
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | 50 POE Load (A) | 118.1897 | 137.2453 | 149.4197 | 163.383 | 173.8797
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | 10 POE Load (A) | 292.3862 | 290.2176 | 291.9069 | 292.0329 | 291.7127
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | Power Factor | 0.98985 | 0.98973 | 0.9897 | 0.98994 | 0.98955
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | ECC Rating (A) | 765 | 765 | 765 | 765 | 765
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | 50 POE Load (A) | 474.1785 | 470.2822 | 474.6281 | 474.436 | 473.6479
Goodna Bulk | 3802-1 | Goodna BS | Springfield | NCC Rating (A) | 592 | 592 | 592 | 592 | 592 | Urban | 70
Goodna Bulk | 3802-1 | Goodna BS | Springfield | 10 POE Load (A) | 376.6345 | 378.9473 | 396.9252 | 401.2186 | 408.8025
Goodna Bulk | 3802-1 | Goodna BS | Springfield | Power Factor | 0.97252 | 0.9726 | 0.97229 | 0.97214 | 0.9718
Goodna Bulk | 3802-1 | Goodna BS | Springfield | ECC Rating (A) | 675 | 675 | 675 | 675 | 675
Goodna Bulk | 3802-1 | Goodna BS | Springfield | 50 POE Load (A) | 689.3648 | 691.1981 | 726.6043 | 735.4249 | 748.969
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | NCC Rating (A) | 502 | 502 | 502 | 502 | 502 | Urban | 70
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | 10 POE Load (A) | 253.3107 | 253.936 | 265.3829 | 268.2451 | 272.1169
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | Power Factor | 0.99342 | 0.99319 | 0.99284 | 0.99275 | 0.99199
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | 50 POE Load (A) | 361.8865 | 362.4706 | 380.0294 | 383.9026 | 388.6221
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | NCC Rating (A) | 502 | 502 | 502 | 502 | 502 | Urban | 70
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | 10 POE Load (A) | 231.632 | 232.2037 | 242.671 | 245.2882 | 248.8286
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | Power Factor | 0.99178 | 0.99152 | 0.99114 | 0.99103 | 0.9902
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | 50 POE Load (A) | 347.865 | 348.426 | 365.3137 | 369.0393 | 373.5789
Goodna Bulk | 3806-1 | Goodna BS | Springfield | NCC Rating (A) | 592 | 592 | 592 | 592 | 592 | Urban | 70
Goodna Bulk | 3806-1 | Goodna BS | Springfield | 10 POE Load (A) | 372.4444 | 374.7504 | 392.6294 | 396.8957 | 404.4279
Goodna Bulk | 3806-1 | Goodna BS | Springfield | Power Factor | 0.99348 | 0.99304 | 0.99231 | 0.99163 | 0.99066
Goodna Bulk | 3806-1 | Goodna BS | Springfield | ECC Rating (A) | 675 | 675 | 675 | 675 | 675
Goodna Bulk | 3806-1 | Goodna BS | Springfield | 50 POE Load (A) | 686.6407 | 688.4835 | 723.8683 | 732.7025 | 746.2027
Goodna Bulk | 3807-1 | Goodna BS | Redbank | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70
Goodna Bulk | 3807-1 | Goodna BS | Redbank | 10 POE Load (A) | 342.551 | 338.9775 | 371.2287 | 369.4317 | 365.8394
Goodna Bulk | 3807-1 | Goodna BS | Redbank | Power Factor | 0.9745 | 0.9746 | 0.97468 | 0.97478 | 0.97479
Goodna Bulk | 3807-1 | Goodna BS | Redbank | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
Goodna Bulk | 3807-1 | Goodna BS | Redbank | 50 POE Load (A)
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | 10 POE Load (A) | 292.9094 | 290.7368 | 292.4292 | 292.5555 | 292.2347
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | Power Factor | 0.98996 | 0.98983 | 0.9898 | 0.99004 | 0.98966
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | 50 POE Load (A) | 474.3489 | 470.4511 | 474.7987 | 474.6065 | 473.8181
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | 10 POE Load (A) | 73.3367 | 85.2063 | 92.5299 | 100.7871 | 107.2232
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | Power Factor | 0.98729 | 0.98915 | 0.98682 | 0.98499 | 0.98138
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | 50 POE Load (A) | 118.0704 | 137.0954 | 149.2423 | 163.153 | 173.6251
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | NCC Rating (A) | 742 | 742 | 742 | 742 | 742 | Urban | 70
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | 10 POE Load (A) | 171.1958 | 177.1576 | 211.0264 | 218.6876 | 230.7292
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | Power Factor | 1 | 0.99986 | 0.99947 | 0.9989 | 0.99831
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | 50 POE Load (A) | 348.0226 | 359.3452 | 436.8077 | 451.8561 | 475.8641
Goodna Bulk | 3881-1 | Springfield | Springfield Central | NCC Rating (A) | 742 | 742 | 742 | 742 | 742 | Urban | 70
Goodna Bulk | 3881-1 | Springfield | Springfield Central | 10 POE Load (A) | 199.1065 | 205.4917 | 242.7262 | 251.1777 | 264.2856
Goodna Bulk | 3881-1 | Springfield | Springfield Central | Power Factor | 0.9925 | 0.99143 | 0.99021 | 0.98897 | 0.98799
Goodna Bulk | 3881-1 | Springfield | Springfield Central | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
Goodna Bulk | 3881-1 | Springfield | Springfield Central | 50 POE Load (A) | 344.6584 | 355.3492 | 429.8482 | 445.1371 | 468.2743
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | NCC Rating (A) | 899 | 899 | 899 | 899 | 899 | Urban | 70
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | 10 POE Load (A) | 105.864 | 107.1017 | 115.706 | 117.9255 | 120.832
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | Power Factor | 0.99829 | 0.99804 | 0.99763 | 0.99724 | 0.99676
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | 10 POE Load (A) | 105.8608 | 107.0985 | 115.7019 | 117.9212 | 120.8275
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | Power Factor | 0.99828 | 0.99814 | 0.99713 | 0.99683 | 0.9964
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | 50 POE Load (A) | 200.9329 | 201.8962 | 215.0746 | 218.1331 | 222.0713
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | 10 POE Load (A) | 105.9299 | 107.1702 | 115.7894 | 118.0129 | 120.9248
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | Power Factor | 0.99818 | 0.99793 | 0.99751 | 0.99713 | 0.99665
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | 50 POE Load (A) | 201.0236 | 201.9873 | 215.1756 | 218.2366 | 222.1783
Griffin Bulk | 312-1 | Kallangur | Narangba | NCC Rating (A) | 422 | 422 | 422 | 422 | 422 | Urban | 70
Griffin Bulk | 312-1 | Kallangur | Narangba | 10 POE Load (A) | 0.64204 | 0.64242 | 0.64247 | 0.64226 | 0.64183
Griffin Bulk | 312-1 | Kallangur | Narangba | Power Factor | -1.3713e-06 | -1.371e-06 | -1.3714e-06 | -1.3711e-06 | -1.3713e-06
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | 10 POE Load (A) | 409.8904 | 442.2539 | 444.338 | 452.7363 | 463.5988
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | Power Factor | 0.99111 | 0.99116 | 0.99079 | 0.99073 | 0.98995
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | 50 POE Load (A) | 570.4215 | 628.6737 | 631.9262 | 644.3925 | 657.308
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70 | 15
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | 10 POE Load (A) | 303.9662 | 359.5838 | 365.5934 | 372.289 | 374.2028
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | Power Factor | 0.9996 | 0.99967 | 0.99973 | 0.99989 | 0.99984
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | 50 POE Load (A) | 604.0276 | 703.0005 | 710.9635 | 724.1202 | 730.3726
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | 10 POE Load (A) | 124.4518 | 112.1435 | 108.7357 | 110.6817 | 120.7353
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | Power Factor | 0.935 | 0.93593 | 0.93868 | 0.93966 | 0.94191
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | 50 POE Load (A) | 345.3434 | 334.9153 | 330.6006 | 338.6102 | 357.8122
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | 10 POE Load (A) | 446.942 | 458.4478 | 457.4168 | 466.2626 | 482.7038
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | Power Factor | 0.97517 | 0.97483 | 0.97313 | 0.97164 | 0.96968
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | 50 POE Load (A) | 527.4584 | 544.0026 | 541.9948 | 553.469 | 573.1939
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | 10 POE Load (A) | 0.029115 | 0.029122 | 0.029123 | 0.02912 | 0.029114
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | Power Factor | 6.7994e-06 | 6.7996e-06 | 6.7993e-06 | 6.7992e-06 | 6.7996e-06
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | 10 POE Load (A) | 447.9138 | 459.3532 | 458.3181 | 467.1755 | 483.6421
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | Power Factor | 0.97595 | 0.97565 | 0.97416 | 0.97287 | 0.97115
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | 50 POE Load (A) | 528.4033 | 544.8844 | 542.8684 | 554.3541 | 574.1039
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | 10 POE Load (A) | 227.6739 | 233.3071 | 232.7919 | 237.2009 | 245.3974
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | Power Factor | 0.98414 | 0.98389 | 0.98259 | 0.98144 | 0.9799
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | 50 POE Load (A) | 378.5162 | 390.0397 | 388.7895 | 396.9029 | 411.1093
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | 10 POE Load (A) | 0.0016882 | 0.0016887 | 0.0016888 | 0.0016885 | 0.0016879
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | Power Factor | 1.9246e-05 | 1.9244e-05 | 1.9245e-05 | 1.9244e-05 | 1.9245e-05
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | 10 POE Load (A) | 227.8238 | 233.4454 | 232.9294 | 237.3405 | 245.5416
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | Power Factor | 0.9849 | 0.98467 | 0.98354 | 0.98256 | 0.98121
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | 50 POE Load (A) | 378.6948 | 390.2059 | 388.9549 | 397.0704 | 411.2813
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | 10 POE Load (A) | 191.0021 | 197.1659 | 196.6569 | 201.0431 | 209.1931
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | Power Factor | 0.98809 | 0.98783 | 0.98663 | 0.98544 | 0.98415
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | 50 POE Load (A) | 343.2236 | 353.4102 | 352.1672 | 361.9601 | 376.1155
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | 10 POE Load (A) | 227.8373 | 233.4578 | 232.9418 | 237.353 | 245.5545
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | Power Factor | 0.98665 | 0.98643 | 0.98532 | 0.98434 | 0.98305
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | 50 POE Load (A) | 378.7105 | 390.2204 | 388.9694 | 397.0851 | 411.2964
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | 10 POE Load (A) | 0.38711 | 0.3875 | 0.38745 | 0.38734 | 0.38727
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | Power Factor | -1.0508e-06 | -1.0503e-06 | -1.0517e-06 | -1.0512e-06 | -1.051e-06
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | 10 POE Load (A) | 326.1726 | 365.0861 | 368.673 | 375.533 | 381.4847
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | Power Factor | 0.96494 | 0.9654 | 0.96562 | 0.96677 | 0.96584
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | 50 POE Load (A) | 598.9783 | 697.2786 | 705.2394 | 719.2308 | 725.2505
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | 10 POE Load (A) | 326.2954 | 365.233 | 368.8211 | 375.6824 | 381.6347
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | Power Factor | 0.96488 | 0.96534 | 0.96557 | 0.96672 | 0.9658
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | 50 POE Load (A) | 599.0505 | 697.3792 | 705.341 | 719.334 | 725.3544
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 70
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | 10 POE Load (A) | 326.8035 | 365.8401 | 369.4327 | 376.2993 | 382.2537
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | Power Factor | 0.96628 | 0.96673 | 0.96697 | 0.96811 | 0.96723
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | ECC Rating (A) | 762 | 762 | 762 | 762 | 762
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | 50 POE Load (A) | 599.329 | 697.772 | 705.7373 | 719.7365 | 725.7595
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | 10 POE Load (A) | 0.43645 | 0.43691 | 0.43685 | 0.43671 | 0.43662
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | Power Factor | 8.5354e-06 | 8.5353e-06 | 8.5353e-06 | 8.5353e-06 | 8.5354e-06
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | NCC Rating (A) | 850 | 850 | 850 | 850 | 850 | Urban | 70
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | 10 POE Load (A) | 0.26218 | 0.26245 | 0.26242 | 0.26233 | 0.26228
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | Power Factor | 3.3927e-06 | 3.3927e-06 | 3.3928e-06 | 3.3927e-06 | 3.3928e-06
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | 10 POE Load (A) | 326.066 | 364.9584 | 368.5444 | 375.4031 | 381.3543
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | Power Factor | 0.95995 | 0.96046 | 0.96066 | 0.96185 | 0.9608
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | 50 POE Load (A) | 598.9147 | 697.1902 | 705.1502 | 719.1401 | 725.1592
Griffin Bulk | 338-1 | Griffin BS | Strathpine | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
Griffin Bulk | 338-1 | Griffin BS | Strathpine | 10 POE Load (A) | 2.1432 | 2.1432 | 2.1432 | 2.1432 | 2.1432
Griffin Bulk | 338-1 | Griffin BS | Strathpine | Power Factor | 0.00011973 | 0.00011973 | 0.00011973 | 0.00011973 | 0.00011973
Griffin Bulk | 338-1 | Griffin BS | Strathpine | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
Griffin Bulk | 338-1 | Griffin BS | Strathpine | 50 POE Load (A)
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 127 | 127 | 127 | 127 | 127 | Rural | 170
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | 10 POE Load (A) | 81.3091 | 80.0138 | 78.7964 | 78.4487 | 77.5338
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | Power Factor | 0.00028204 | 0.00028204 | 0.00028204 | 0.00028204 | 0.00028204
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | ECC Rating (A) | 127 | 127 | 127 | 127 | 127
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | 50 POE Load (A)
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | 10 POE Load (A) | 77.6113 | 76.431 | 75.3338 | 75.0323 | 74.2185
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | Power Factor | 0.99708 | 0.9971 | 0.99706 | 0.99703 | 0.9969
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | 50 POE Load (A)
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | 10 POE Load (A) | 148.6394 | 146.8828 | 145.1271 | 144.2497 | 143.3725
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | Power Factor | 0.99053 | 0.99073 | 0.99086 | 0.99107 | 0.99105
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | 50 POE Load (A) | 266.6889 | 263.175 | 259.6632 | 257.9082 | 256.1537
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | 10 POE Load (A) | 148.6839 | 146.9268 | 145.1706 | 144.293 | 143.4155
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | Power Factor | 0.99052 | 0.99072 | 0.99085 | 0.99107 | 0.99104
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | 50 POE Load (A) | 266.6921 | 263.1781 | 259.6664 | 257.9113 | 256.1569
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | 10 POE Load (A) | 65.3518 | 63.2413 | 63.1132 | 61.098 | 60.9945
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | Power Factor | 0.9799 | 0.98314 | 0.98407 | 0.9841 | 0.98406
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | 50 POE Load (A)
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | 10 POE Load (A) | 50.8521 | 48.7904 | 48.7012 | 46.7179 | 46.6449
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | Power Factor | 0.99151 | 0.99444 | 0.99521 | 0.99523 | 0.9952
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | 50 POE Load (A)
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | 10 POE Load (A) | 0.13189 | 0.13205 | 0.13236 | 0.13236 | 0.13254
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | Power Factor | 3.5781e-06 | 3.5781e-06 | 3.5781e-06 | 3.5781e-06 | 3.5781e-06
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | NCC Rating (A) | 742 | 742 | 742 | 742 | 742 | Rural | 170
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | 10 POE Load (A) | 158.4927 | 154.2568 | 152.1756 | 150.0505 | 147.9478
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | Power Factor | 0.94975 | 0.95184 | 0.95245 | 0.95258 | 0.9525
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | 50 POE Load (A)
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | NCC Rating (A) | 210 | 210 | 210 | 210 | 210 | Rural | 170
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | 10 POE Load (A) | 158.7691 | 154.5303 | 152.446 | 150.3188 | 148.2136
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | Power Factor | 0.95864 | 0.96043 | 0.96095 | 0.96104 | 0.96098
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | ECC Rating (A) | 210 | 210 | 210 | 210 | 210
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | 50 POE Load (A)
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | NCC Rating (A) | 210 | 210 | 210 | 210 | 210 | Rural | 170
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | 10 POE Load (A) | 0.00033654 | 0.00033654 | 0.00033654 | 0.00033654 | 0.00033654
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | Power Factor | 0.00059245 | 0.00059346 | 0.00059366 | 0.00059309 | 0.0005932
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | Rural | 170
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | 10 POE Load (A) | 67.3328 | 66.502 | 65.672 | 64.8426 | 64.014
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | Power Factor | 0.96578 | 0.96428 | 0.96442 | 0.96465 | 0.96467
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | 50 POE Load (A) | 138.4493 | 136.65 | 134.8525 | 133.0567 | 131.2627
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | Rural | 170
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | 10 POE Load (A) | 0.0018835 | 0.0018835 | 0.0018835 | 0.0018835 | 0.0018835
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | Power Factor | 0.00010576 | 0.00010575 | 0.00010583 | 0.00010583 | 0.00010586
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | Rural | 170
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | 10 POE Load (A) | 67.4117 | 66.5807 | 65.7503 | 64.9315 | 64.1025
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | Power Factor | 0.96528 | 0.96385 | 0.96398 | 0.9642 | 0.96422
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | 50 POE Load (A) | 138.5417 | 136.742 | 134.9441 | 133.148 | 131.3536
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | NCC Rating (A) | 328 | 328 | 328 | 328 | 328 | Rural | 170
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | 10 POE Load (A) | 3.3765 | 3.3767 | 3.3769 | 3.3769 | 3.3771
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | Power Factor | 0.00076215 | 0.00076215 | 0.00076215 | 0.00076215 | 0.00076215
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | ECC Rating (A) | 328 | 328 | 328 | 328 | 328
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | 50 POE Load (A)
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | 10 POE Load (A) | 1.5385 | 1.5385 | 1.5386 | 1.5386 | 1.5387
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | Power Factor | 0.00014067 | 0.00014067 | 0.00014067 | 0.00014067 | 0.00014067
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | 50 POE Load (A)
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | 10 POE Load (A) | 1.5325 | 1.5326 | 1.5327 | 1.5327 | 1.5327
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | Power Factor | 0.0001403 | 0.0001403 | 0.0001403 | 0.0001403 | 0.0001403
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | 50 POE Load (A)
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | NCC Rating (A) | 328 | 328 | 328 | 328 | 328 | Rural | 170
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | 10 POE Load (A) | 0.59954 | 0.59958 | 0.59961 | 0.59961 | 0.59964
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | Power Factor | 4.3695e-05 | 4.3695e-05 | 4.3695e-05 | 4.3695e-05 | 4.3695e-05
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | 10 POE Load (A) | 68.4737 | 67.64 | 66.8071 | 65.9749 | 65.1433
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | Power Factor | 0.9508 | 0.95003 | 0.9501 | 0.95023 | 0.95024
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | 50 POE Load (A) | 139.5665 | 137.7639 | 135.963 | 134.1638 | 132.3663
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | NCC Rating (A) | 211 | 211 | 211 | 211 | 211 | Rural | 170
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | 10 POE Load (A) | 209.8595 | 205.8429 | 202.9279 | 201.4926 | 198.4878
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | Power Factor | 0.99951 | 0.99951 | 0.9995 | 0.9995 | 0.99949
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | ECC Rating (A) | 211 | 211 | 211 | 211 | 211
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | 50 POE Load (A)
Gympie Bulk | 341-2 | 341 Tee1 | Customer | NCC Rating (A) | 410 | 704 | 410 | 410 | 410 | Rural | 170
Gympie Bulk | 341-2 | 341 Tee1 | Customer | 10 POE Load (A) | 48.207 | 79.79 | 45.7772 | 44.4623 | 43.7216
Gympie Bulk | 341-2 | 341 Tee1 | Customer | Power Factor | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 1
Gympie Bulk | 341-2 | 341 Tee1 | Customer | ECC Rating (A) | 463 | 463 | 463 | 463 | 463
Gympie Bulk | 341-2 | 341 Tee1 | Customer | 50 POE Load (A)
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | NCC Rating (A) | 210 | 210 | 210 | 210 | 210 | Rural | 170
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | 10 POE Load (A) | 166.6695 | 164.0708 | 161.6424 | 161.0415 | 159.1458
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | Power Factor | 0.99836 | 0.99838 | 0.99835 | 0.99832 | 0.99821
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | ECC Rating (A) | 210 | 210 | 210 | 210 | 210
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | 50 POE Load (A)
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Rural | 170
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | 10 POE Load (A) | 158.7339 | 156.259 | 153.9462 | 153.3735 | 151.5684
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | Power Factor | 0.99838 | 0.9984 | 0.99836 | 0.99834 | 0.99823
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | 50 POE Load (A)
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Rural | 170
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | 10 POE Load (A) | 77.4828 | 76.5281 | 75.5742 | 74.6211 | 73.6687
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | Power Factor | 0.96146 | 0.9599 | 0.96004 | 0.96028 | 0.9603
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | ECC Rating (A) | 355 | 355 | 355 | 355 | 355
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | 50 POE Load (A) | 139.3673 | 137.5694 | 135.7732 | 133.9786 | 132.1857
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | 10 POE Load (A) | 291.0251 | 285.9104 | 282.2184 | 279.5251 | 275.7135
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | Power Factor | 0.95731 | 0.95731 | 0.95726 | 0.95721 | 0.95708
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | 50 POE Load (A) | 336.9329 | 331.1432 | 326.1153 | 321.233 | 318.1316
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | NCC Rating (A) | 461 | 461 | 461 | 461 | 461 | Rural | 170
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | 10 POE Load (A) | 54.1859 | 54.1076 | 54.0525 | 52.209 | 52.1557
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | Power Factor | 0.99431 | 0.99434 | 0.99436 | 0.99438 | 0.99437
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | ECC Rating (A) | 461 | 461 | 461 | 461 | 461
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | 50 POE Load (A) | 49.3547 | 47.4491 | 47.3755 | 47.3101 | 47.2677
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | NCC Rating (A) | 410 | 410 | 410 | 410 | 410 | Rural | 170
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | 10 POE Load (A) | 240.8184 | 235.6649 | 231.9522 | 230.9686 | 227.7756
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | Power Factor | 0.96019 | 0.96025 | 0.96025 | 0.96027 | 0.96018
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | ECC Rating (A) | 463 | 463 | 463 | 463 | 463
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | 50 POE Load (A) | 291.9106 | 287.8956 | 282.8124 | 277.9103 | 274.7269
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 266 | 0.5
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | 10 POE Load (A) | 818.038 | 812.2308 | 806.2109 | 805.4433 | 804.9889
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | Power Factor | 0.96666 | 0.96656 | 0.96643 | 0.96622 | 0.96573
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | 50 POE Load (A) | 1157.9164 | 1152.0557 | 1148.0192 | 1148.7122 | 1151.2599
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 623 | 623 | 623 | 623 | 623 | Urban | 154 | 0.5
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | 10 POE Load (A) | 270.7379 | 268.8168 | 266.8252 | 266.5714 | 266.4213
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | Power Factor | 0.97733 | 0.97758 | 0.97785 | 0.97785 | 0.97784
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | 50 POE Load (A) | 821.4575 | 813.9793 | 808.0352 | 806.0326 | 804.7261
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 256 | 0.5
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | 10 POE Load (A) | 522.932 | 520.5754 | 520.1434 | 521.6345 | 524.7826
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | Power Factor | 0.98158 | 0.98151 | 0.98154 | 0.98136 | 0.98101
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | 50 POE Load (A) | 1025.4447 | 1023.2515 | 1023.4766 | 1028.3845 | 1035.7541
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | 10 POE Load (A) | 332.2974 | 330.2903 | 329.3296 | 329.6253 | 329.4875
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | Power Factor | 0.98796 | 0.98803 | 0.98797 | 0.98799 | 0.98794
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | 50 POE Load (A) | 437.5187 | 434.5897 | 433.8889 | 433.5387 | 434.2379
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | NCC Rating (A) | 464 | 464 | 464 | 464 | 464 | Urban | 170
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | 10 POE Load (A) | 0.84206 | 0.84219 | 0.84248 | 0.84231 | 0.8421
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | Power Factor | 4.3774e-07 | 4.3775e-07 | 4.3774e-07 | 4.3774e-07 | 4.3786e-07
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | ECC Rating (A) | 464 | 464 | 464 | 464 | 464
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | 50 POE Load (A) | 610.0129 | 609.8212 | 609.6459 | 614.2432 | 623.4842
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | NCC Rating (A) | 322 | 322 | 322 | 322 | 322 | Urban | 70
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | 10 POE Load (A) | 55.167 | 55.3318 | 56.2212 | 56.4306 | 57.5981
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | Power Factor | 0.99911 | 0.99866 | 0.99825 | 0.99774 | 0.99711
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | ECC Rating (A) | 322 | 322 | 322 | 322 | 322
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | 50 POE Load (A) | 351.0988 | 349.2079 | 349.182 | 349.169 | 350.979
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | 10 POE Load (A) | 459.16 | 381.4749 | 389.0066 | 396.5643 | 400.3531
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | Power Factor | 0.96589 | 0.97394 | 0.97309 | 0.97223 | 0.97179
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | 50 POE Load (A)
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Urban | 70
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | 10 POE Load (A) | 105.7979 | 106.099 | 106.4065 | 107.5288 | 108.3223
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | Power Factor | 0.97543 | 0.97533 | 0.97223 | 0.97542 | 0.97222
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | 50 POE Load (A) | 265.0475 | 264.2073 | 264.859 | 265.1848 | 266.286
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 543 | 543 | 543 | 543 | 543 | Urban | 70
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | 10 POE Load (A) | 294.9046 | 292.2735 | 290.5774 | 290.2321 | 288.786
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | Power Factor | 0.97353 | 0.97376 | 0.97393 | 0.97397 | 0.97413
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | 50 POE Load (A) | 434.4094 | 430.2204 | 428.0494 | 426.9648 | 426.2745
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 543 | 430 | 430 | 430 | 430 | Urban | 70
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | 10 POE Load (A) | 296.4404 | 293.8052 | 292.1002 | 291.7531 | 290.2994
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | Power Factor | 0.96964 | 0.96939 | 0.96957 | 0.96961 | 0.96979
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | ECC Rating (A) | 573 | 573 | 573 | 573 | 573
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | 50 POE Load (A) | 435.1568 | 430.9687 | 428.7951 | 427.7091 | 427.0182
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | NCC Rating (A) | 524 | 524 | 524 | 524 | 524 | Urban | 70
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | 10 POE Load (A) | 308.5614 | 306.5497 | 305.3179 | 305.6963 | 304.9577
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | Power Factor | 0.96384 | 0.96396 | 0.96377 | 0.96376 | 0.96356
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | ECC Rating (A) | 524 | 524 | 524 | 524 | 524
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | 50 POE Load (A) | 446.1229 | 443.0535 | 442.2548 | 441.8557 | 442.3852
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | NCC Rating (A) | 422 | 422 | 422 | 422 | 422 | Urban | 305
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | 10 POE Load (A) | 56.4589 | 52.9209 | 49.5248 | 46.9837 | 42.1625
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | Power Factor | 0.96679 | 0.96712 | 0.96509 | 0.96535 | 0.96534
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | ECC Rating (A) | 422 | 422 | 422 | 422 | 422
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | 50 POE Load (A) | 528.7089 | 530.6125 | 534.7902 | 541.4176 | 550.3672
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 300
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | 10 POE Load (A) | 589.0696 | 587.3323 | 587.7356 | 590.2802 | 595.2483
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | Power Factor | 0.95637 | 0.95652 | 0.95647 | 0.95622 | 0.95574
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | 50 POE Load (A) | 1014.8856 | 1013.158 | 1012.9583 | 1017.3583 | 1023.3381
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | 10 POE Load (A) | 362.7948 | 372.6357 | 384.5514 | 398.5303 | 406.6154
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | Power Factor | 0.97944 | 0.9786 | 0.97758 | 0.97658 | 0.9765
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | 10 POE Load (A) | 601.3759 | 603.616 | 605.8598 | 612.6122 | 633.071
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | Power Factor | 0.96567 | 0.96566 | 0.96556 | 0.96431 | 0.96269
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | 50 POE Load (A)
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | 10 POE Load (A) | 172.7689 | 171.6151 | 170.6528 | 193.4985 | 192.5007
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | Power Factor | 0.9722 | 0.97489 | 0.97514 | 0.96449 | 0.96479
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | 50 POE Load (A) | 282.8388 | 278.177 | 276.0742 | 329.2254 | 326.9676
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | NCC Rating (A) | 442 | 442 | 442 | 442 | 442 | Rural | 170
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | 10 POE Load (A) | 41.6328 | 41.6181 | 41.6126 | 41.7616 | 41.7556
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | Power Factor | 0.99733 | 0.99733 | 0.99733 | 0.99731 | 0.99731
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | ECC Rating (A) | 442 | 442 | 442 | 442 | 442
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | 50 POE Load (A) | 39.0558 | 39.0204 | 39.009 | 39.3292 | 39.316
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | 10 POE Load (A) | 132.0234 | 130.7768 | 129.8124 | 152.885 | 151.8837
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | Power Factor | 0.93452 | 0.93451 | 0.93065 | 0.92639 | 0.91854
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | 50 POE Load (A) | 244.3689 | 239.6527 | 237.5534 | 290.7605 | 288.5044
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | 10 POE Load (A) | 0.87447 | 0.87472 | 0.87006 | 0.85354 | 0.85388
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | Power Factor | -5.6276e-06 | -5.6276e-06 | -5.6276e-06 | -5.6276e-06 | -5.6276e-06
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | 10 POE Load (A) | 132.2539 | 130.9936 | 130.0287 | 153.1357 | 152.1338
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | Power Factor | 0.94023 | 0.94022 | 0.93793 | 0.93535 | 0.93076
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | 50 POE Load (A) | 244.5136 | 239.7852 | 237.6853 | 290.9265 | 288.6698
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | 10 POE Load (A) | 44.4442 | 43.4575 | 43.342 | 43.3254 | 43.3254
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | Power Factor | 0.98679 | 0.98693 | 0.98682 | 0.98674 | 0.98633
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | 50 POE Load (A) | 152.4589 | 149.7174 | 149.7174 | 149.5437 | 144.8636
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | NCC Rating (A) | 160 | 160 | 160 | 160 | 160 | Rural | 170
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | 10 POE Load (A) | 7.2201 | 7.2101 | 7.1975 | 7.195 | 7.195
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | Power Factor | 0.99394 | 0.99388 | 0.99383 | 0.99375 | 0.99365
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | ECC Rating (A) | 160 | 160 | 160 | 160 | 160
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | 50 POE Load (A) | 8.1997 | 8.1858 | 8.1858 | 8.1461 | 6.0963
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | 10 POE Load (A) | 38.0844 | 37.8972 | 37.9694 | 37.9694 | 37.7785
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | Power Factor | 0.98516 | 0.98531 | 0.98518 | 0.98512 | 0.98469
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | 50 POE Load (A) | 145.4627 | 142.7329 | 142.7329 | 142.566 | 139.7167
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | 10 POE Load (A) | 171.0341 | 168.6629 | 166.7516 | 165.3983 | 165.3983
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | Power Factor | 0.97437 | 0.97441 | 0.97438 | 0.97242 | 0.96978
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | 50 POE Load (A) | 328.711 | 323.553 | 323.553 | 320.7516 | 313.0469
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | 10 POE Load (A) | 0.0058743 | 0.0058745 | 0.0058747 | 0.0058748 | 0.0058748
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | Power Factor | 1 | 1 | 1 | 1 | 1
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | 10 POE Load (A) | 171.1585 | 168.7867 | 166.875 | 165.5214 | 165.5214
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | Power Factor | 0.97887 | 0.97891 | 0.97889 | 0.97735 | 0.97525
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | 50 POE Load (A) | 328.8573 | 323.6983 | 323.6983 | 320.8962 | 313.1904
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | 10 POE Load (A) | 0.0058743 | 0.0058745 | 0.0058747 | 0.0058748 | 0.0058748
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | Power Factor | 3.3851e-05 | 3.3859e-05 | 3.3857e-05 | 3.3854e-05 | 3.3854e-05
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | 10 POE Load (A) | 171.1591 | 168.7872 | 166.8755 | 165.522 | 165.522
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | Power Factor | 0.97899 | 0.97903 | 0.97901 | 0.97749 | 0.97541
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | 50 POE Load (A) | 328.8641 | 323.705 | 323.705 | 320.9029 | 313.197
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | 10 POE Load (A) | 54.1204 | 54.1004 | 53.1428 | 53.1428 | 53.1228
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | Power Factor | 0.99899 | 0.99893 | 0.9989 | 0.99754 | 0.99586
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | 50 POE Load (A) | 53.4741 | 52.3688 | 52.3688 | 51.2356 | 51.2356
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | 10 POE Load (A) | 118.9788 | 117.5806 | 115.6916 | 115.2898 | 115.2898
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | Power Factor | 0.9724 | 0.97254 | 0.97256 | 0.97237 | 0.97181
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | 50 POE Load (A) | 278.3218 | 274.2557 | 274.2557 | 271.5131 | 264.9529
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | 10 POE Load (A) | 54.1557 | 54.1358 | 53.1428 | 53.1428 | 53.1454
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | Power Factor | 0.999 | 0.99894 | 0.9989 | 0.9976 | 0.99588
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | 50 POE Load (A) | 53.5303 | 52.4369 | 52.4369 | 51.2807 | 51.2807
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | 10 POE Load (A) | 66.7524 | 66.314 | 64.4604 | 65.0084 | 65.0084
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | Power Factor | 0.92686 | 0.92678 | 0.92668 | 0.92376 | 0.92025
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | 50 POE Load (A) | 227.6834 | 224.709 | 224.709 | 222.0256 | 216.6002
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | 10 POE Load (A) | 150.9306 | 149.096 | 146.8258 | 146.1986 | 146.1986
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | Power Factor | 0.97147 | 0.97159 | 0.97159 | 0.97058 | 0.96898
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | 50 POE Load (A) | 209.616 | 207.2779 | 207.2779 | 204.9706 | 200.4659
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | 10 POE Load (A) | 0.010138 | 0.010138 | 0.010139 | 0.010139 | 0.010139
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | Power Factor | 1.9416e-05 | 1.9415e-05 | 1.9415e-05 | 1.9415e-05 | 1.9413e-05
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | 10 POE Load (A) | 151.3026 | 149.4658 | 147.194 | 146.5662 | 146.5662
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | Power Factor | 0.98468 | 0.98477 | 0.98477 | 0.98442 | 0.98384
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | 50 POE Load (A) | 210.0288 | 207.689 | 207.689 | 205.3799 | 200.874
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | 10 POE Load (A) | 102.1641 | 101.0655 | 99.1644 | 99.127 | 99.127
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | Power Factor | 0.98137 | 0.98155 | 0.98159 | 0.98156 | 0.98141
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | ECC Rating (A) | 155 | 400 | 400 | 400 | 400
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | 50 POE Load (A) | 209.6953 | 207.5284 | 207.5284 | 204.7199 | 200.0456
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | 10 POE Load (A) | 105.2672 | 104.2056 | 102.1903 | 102.1519 | 102.1519
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | Power Factor | 0.96252 | 0.96259 | 0.96256 | 0.96251 | 0.96213
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | 50 POE Load (A) | 208.4047 | 205.5736 | 205.5736 | 203.5332 | 198.7177
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Rural | 170
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | 10 POE Load (A) | 150.7517 | 148.8672 | 148.8672 | 146.9854 | 145.1063
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | Power Factor | 0.95491 | 0.95493 | 0.95485 | 0.95482 | 0.95468
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | ECC Rating (A) | 355 | 355 | 355 | 355 | 355
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | 50 POE Load (A)
Lockrose Bulk | 3832-1 | Tarampa | 383 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Lockrose Bulk | 3832-1 | Tarampa | 383 Tee1 | 10 POE Load (A) | 0.0050935 | 0.005096 | 0.0050985 | 0.0050985 | 0.0050985
Lockrose Bulk | 3832-1 | Tarampa | 383 Tee1 | Power Factor | 1 | 1 | 1 | 1 | 1
Lockrose Bulk | 3832-2 | 3832 Tee1 | 381 Tee1 | NCC Rating (A) | 155 | 700 | 700 | 700 | 700 | Rural | 170
Lockrose Bulk | 3832-2 | 3832 Tee1 | 381 Tee1 | 10 POE Load (A)
Lockrose Bulk | 3832-2 | 3832 Tee1 | 381 Tee1 | Power Factor | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | NCC Rating (A) | 802 | 802 | 802 | 802 | 802 | Rural | 170
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | 10 POE Load (A) | 0.7203 | 0.72065 | 0.721 | 0.721 | 0.721
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | Power Factor | -8.0548e-06 | -8.0547e-06 | -8.0546e-06 | -8.0547e-06 | -8.0548e-06
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | ECC Rating (A) | 434 | 434 | 434 | 434 | 434
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | 50 POE Load (A) | 0.74244 | 0.74244 | 0.74277 | 0.74277 | 0.74277
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | 10 POE Load (A) | 38.2251 | 37.9212 | 37.7604 | 37.7604 | 37.8924
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | Power Factor | 0.98948 | 0.9896 | 0.98957 | 0.98953 | 0.98918
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | 50 POE Load (A) | 150.5842 | 150.3252 | 150.3252 | 147.5876 | 144.8772
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | NCC Rating (A) | 451 | 451 | 451 | 451 | 451 | Rural | 170
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | 10 POE Load (A) | 180.0176 | 178.7493 | 177.7477 | 201.6406 | 200.602
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | Power Factor | 0.99213 | 0.9935 | 0.99361 | 0.98838 | 0.98853
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | ECC Rating (A) | 451 | 451 | 451 | 451 | 451
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | 50 POE Load (A) | 285.798 | 280.8793 | 278.7294 | 333.1128 | 330.7944
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | 10 POE Load (A) | 41.4817 | 41.4684 | 41.464 | 41.5858 | 41.581
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | Power Factor | 0.99192 | 0.99203 | 0.99204 | 0.99208 | 0.99001
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | 50 POE Load (A) | 38.8882 | 38.8541 | 38.8444 | 39.1157 | 39.1045
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | 10 POE Load (A) | 138.6769 | 137.3883 | 136.3893 | 160.2853 | 159.248
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | Power Factor | 0.98273 | 0.98273 | 0.98139 | 0.97993 | 0.97715
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | 50 POE Load (A) | 247.4441 | 242.4686 | 240.3216 | 294.7666 | 292.4494
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Rural | 170
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | 10 POE Load (A) | 189.8668 | 187.8652 | 185.955 | 185.955 | 185.955
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | Power Factor | 0.96801 | 0.96811 | 0.96809 | 0.96814 | 0.96806
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | 50 POE Load (A) | 174.3685 | 172.476 | 172.476 | 172.476 | 172.476
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | 10 POE Load (A) | 132.6012 | 130.6294 | 130.562 | 130.562 | 130.562
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | Power Factor | 0.9719 | 0.97202 | 0.972 | 0.97205 | 0.97197
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | 50 POE Load (A) | 120.7919 | 120.7315 | 120.7315 | 120.7315 | 120.7315
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | NCC Rating (A) | 777 | 777 | 777 | 777 | 777 | Urban | 70
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | 10 POE Load (A) | 331.1865 | 327.4062 | 323.6297 | 322.6862 | 319.857
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | Power Factor | 0.98696 | 0.98767 | 0.98821 | 0.98886 | 0.98912
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | ECC Rating (A) | 777 | 777 | 777 | 777 | 777
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | 50 POE Load (A) | 589.3112 | 591.1413 | 585.6529 | 581.9973 | 578.3445
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 280
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | 10 POE Load (A) | 394.8781 | 393.8231 | 387.0007 | 388.0552 | 390.166
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | Power Factor | 0.9578 | 0.9586 | 0.95793 | 0.95732 | 0.95611
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | 50 POE Load (A) | 608.3381 | 607.5397 | 593.1393 | 596.933 | 598.8314
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | 10 POE Load (A) | 295.8001 | 292.4236 | 289.0505 | 288.2078 | 285.6809
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | Power Factor | 0.98865 | 0.98931 | 0.98982 | 0.99042 | 0.99065
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | 50 POE Load (A) | 591.3566 | 593.2014 | 587.6693 | 583.985 | 580.3038
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | 10 POE Load (A) | 394.518 | 389.0269 | 383.5437 | 379.8928 | 374.4229
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | Power Factor | 0.00013354 | 0.00013355 | 0.00013341 | 0.00013344 | 0.00013351
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | 50 POE Load (A)
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | NCC Rating (A) | 510 | 510 | 510 | 510 | 510 | Urban | 280
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | 10 POE Load (A) | 320.6487 | 319.7921 | 314.2529 | 315.1092 | 316.8231
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | Power Factor | 0.98687 | 0.98732 | 0.98694 | 0.9866 | 0.98591
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | ECC Rating (A) | 510 | 510 | 510 | 510 | 510
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | 50 POE Load (A) | 611.3575 | 610.5217 | 596.0153 | 599.8443 | 601.7605
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | 10 POE Load (A) | 218.6522 | 214.0162 | 292.0047 | 317.7176 | 328.3917
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | 50 POE Load (A) | 425.5159 | 417.9118 | 579.4848 | 633.4491 | 656.0061
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | 10 POE Load (A) | 218.1793 | 213.5534 | 291.3701 | 317.0264 | 327.677
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | 50 POE Load (A) | 425.5432 | 417.9378 | 579.5433 | 633.5219 | 656.0856
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | NCC Rating (A) | 628 | 628 | 628 | 628 | 628 | HighSec | 0
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | 10 POE Load (A) | 168.2573 | 166.328 | 163.6148 | 162.7109 | 160.9036
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | ECC Rating (A) | 628 | 628 | 628 | 628 | 628
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | 50 POE Load (A) | 325.9464 | 322.1437 | 318.5985 | 315.0552 | 311.5135
Lytton Bulk | 491-1 | Lytton BS | Lytton | NCC Rating (A) | 450 | 450 | 450 | 450 | 450 | HighSec | 314
Lytton Bulk | 491-1 | Lytton BS | Lytton | 10 POE Load (A) | 241.9851 | 237.6354 | 250.8549 | 248.1924 | 246.4181
Lytton Bulk | 491-1 | Lytton BS | Lytton | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 491-1 | Lytton BS | Lytton | ECC Rating (A) | 450 | 450 | 450 | 450 | 450
Lytton Bulk | 491-1 | Lytton BS | Lytton | 50 POE Load (A) | 477.6907 | 470.5311 | 497.27 | 491.9262 | 488.3653
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | NCC Rating (A) | 463 | 463 | 463 | 463 | 463 | HighSec | 0
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | 10 POE Load (A) | 161.45 | 159.5794 | 156.9748 | 156.1071 | 154.3721
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | ECC Rating (A) | 463 | 463 | 463 | 463 | 463
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | 50 POE Load (A) | 326.1927 | 322.3845 | 318.8339 | 315.2851 | 311.7381
Lytton Bulk | 493-1 | Lytton BS | Lytton | NCC Rating (A) | 536 | 536 | 536 | 536 | 536 | HighSec | 0
Lytton Bulk | 493-1 | Lytton BS | Lytton | 10 POE Load (A) | 242.956 | 238.5522 | 251.8444 | 249.1764 | 247.3984
Lytton Bulk | 493-1 | Lytton BS | Lytton | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 493-1 | Lytton BS | Lytton | ECC Rating (A) | 536 | 536 | 536 | 536 | 536
Lytton Bulk | 493-1 | Lytton BS | Lytton | 50 POE Load (A) | 477.0982 | 469.9462 | 496.6275 | 491.2975 | 487.7457
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | NCC Rating (A) | 488 | 488 | 488 | 488 | 488 | Urban | 70
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | 10 POE Load (A) | 89.4836 | 87.6701 | 165.3002 | 191.4631 | 202.8471
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | ECC Rating (A) | 488 | 488 | 488 | 488 | 488
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | 50 POE Load (A) | 175.0998 | 171.4654 | 327.7387 | 380.4764 | 403.4331
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | 10 POE Load (A) | 90.8131 | 88.9602 | 168.1812 | 194.8843 | 206.5024
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | 50 POE Load (A) | 174.0332 | 170.4055 | 326.3501 | 378.9599 | 401.854
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | 10 POE Load (A) | 161.8764 | 159.4264 | 156.982 | 155.1522 | 153.3256
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | Power Factor | 0.98888 | 0.98903 | 0.98906 | 0.98912 | 0.98902
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | 50 POE Load (A) | 467.2484 | 460.9672 | 452.633 | 448.4829 | 442.2789
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 367 | 367 | 367 | 367 | 367 | Urban | 70
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | 10 POE Load (A) | 66.7497 | 65.7391 | 64.7307 | 63.9759 | 63.2223
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | Power Factor | 0.98928 | 0.98956 | 0.98984 | 0.99005 | 0.99026
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | ECC Rating (A) | 367 | 367 | 367 | 367 | 367
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | 50 POE Load (A) | 192.4575 | 189.8712 | 186.4396 | 184.7309 | 182.1763
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Urban | 70
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | 10 POE Load (A) | 95.4234 | 93.9796 | 92.539 | 91.4606 | 90.3841
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | Power Factor | 0.9889 | 0.98903 | 0.98907 | 0.98912 | 0.98903
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | 50 POE Load (A) | 275.2323 | 271.5335 | 266.6258 | 264.182 | 260.5286
Lytton Bulk | 560-16 | Lota | 560 Tee1 | NCC Rating (A) | 983 | 983 | 983 | 983 | 983 | Urban | 70
Lytton Bulk | 560-16 | Lota | 560 Tee1 | 10 POE Load (A) | 163.7224 | 161.2538 | 158.7909 | 156.9473 | 155.1069
Lytton Bulk | 560-16 | Lota | 560 Tee1 | Power Factor | 0.98101 | 0.98123 | 0.98144 | 0.9816 | 0.98175
Lytton Bulk | 560-16 | Lota | 560 Tee1 | ECC Rating (A) | 983 | 983 | 983 | 983 | 983
Lytton Bulk | 560-16 | Lota | 560 Tee1 | 50 POE Load (A) | 469.5503 | 463.2524 | 454.8959 | 450.7347 | 444.514
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | 10 POE Load (A) | 0.10103 | 0.10107 | 0.1011 | 0.10112 | 0.10115
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | Power Factor | 1.9415e-06 | 1.9404e-06 | 1.9415e-06 | 1.9412e-06 | 1.9414e-06
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | 10 POE Load (A) | 161.9864 | 159.5346 | 157.1147 | 155.2572 | 153.4549
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | Power Factor | 0.99061 | 0.99092 | 0.99107 | 0.99144 | 0.99151
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | 50 POE Load (A) | 467.4613 | 461.1782 | 452.8414 | 448.6901 | 442.4842
Lytton Bulk | 560-5 | Lota | 560 Tee2 | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | Urban | 70
Lytton Bulk | 560-5 | Lota | 560 Tee2 | 10 POE Load (A) | 95.3736 | 93.9305 | 92.4907 | 91.4129 | 90.337
Lytton Bulk | 560-5 | Lota | 560 Tee2 | Power Factor | 0.99067 | 0.99097 | 0.99127 | 0.9915 | 0.99172
Lytton Bulk | 560-5 | Lota | 560 Tee2 | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
Lytton Bulk | 560-5 | Lota | 560 Tee2 | 50 POE Load (A) | 275.1591 | 271.461 | 266.5541 | 264.1107 | 260.458
Lytton Bulk | 569-1 | Lytton BS | Lota | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Urban | 70
Lytton Bulk | 569-1 | Lytton BS | Lota | 10 POE Load (A) | 334.1515 | 329.0944 | 324.0488 | 320.2719 | 316.5014
Lytton Bulk | 569-1 | Lytton BS | Lota | Power Factor | 0.96659 | 0.96682 | 0.96688 | 0.96697 | 0.96681
Lytton Bulk | 569-1 | Lytton BS | Lota | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Lytton Bulk | 569-1 | Lytton BS | Lota | 50 POE Load (A) | 449.8125 | 444.1335 | 436.2197 | 432.4581 | 427.1633
Lytton Bulk | 599-1 | Hemmant | Lindum | NCC Rating (A) | 443 | 443 | 443 | 443 | 443 | Urban | 70
Lytton Bulk | 599-1 | Hemmant | Lindum | 10 POE Load (A) | 1.7521 | 1.7522 | 1.7522 | 1.7522 | 1.7522
Lytton Bulk | 599-1 | Hemmant | Lindum | Power Factor | -1.1634e-06 | -1.1627e-06 | -1.1625e-06 | -1.1632e-06 | -1.163e-06
Lytton Bulk | 599-1 | Hemmant | Lindum | ECC Rating (A) | 443 | 443 | 443 | 443 | 443
Lytton Bulk | 599-1 | Hemmant | Lindum | 50 POE Load (A)
Lytton Bulk | 681-1 | Lindum | Wynnum | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 70
Lytton Bulk | 681-1 | Lindum | Wynnum | 10 POE Load (A) | 208.3891 | 206.5602 | 204.7325 | 204.7325 | 202.906
Lytton Bulk | 681-1 | Lindum | Wynnum | Power Factor | 0.97042 | 0.97033 | 0.97012 | 0.9699 | 0.96946
Lytton Bulk | 681-1 | Lindum | Wynnum | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
Lytton Bulk | 681-1 | Lindum | Wynnum | 50 POE Load (A) | 398.3427 | 394.4995 | 390.6633 | 390.6633 | 386.8342
Lytton Bulk | 682-1 | Lindum | Wynnum | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 70
Lytton Bulk | 682-1 | Lindum | Wynnum | 10 POE Load (A) | 199.7146 | 197.962 | 196.2104 | 196.2104 | 194.46
Lytton Bulk | 682-1 | Lindum | Wynnum | Power Factor | 0.96776 | 0.96797 | 0.96817 | 0.96817 | 0.96837
Lytton Bulk | 682-1 | Lindum | Wynnum | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
Lytton Bulk | 682-1 | Lindum | Wynnum | 50 POE Load (A) | 399.5802 | 395.7048 | 391.8371 | 391.8371 | 387.9771
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | 10 POE Load (A) | 147.8178 | 146.5153 | 145.2137 | 145.2137 | 143.9129
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | Power Factor | 0.98934 | 0.98927 | 0.98911 | 0.98895 | 0.98862
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | 50 POE Load (A) | 384.3943 | 380.8178 | 377.2439 | 377.2439 | 373.6727
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | 10 POE Load (A) | 2.2523 | 2.2524 | 2.2524 | 2.2524 | 2.2524
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | Power Factor | 1.8338e-05 | 1.8338e-05 | 1.8338e-05 | 1.8338e-05 | 1.8338e-05
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | 50 POE Load (A)
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | 10 POE Load (A) | 148.1636 | 146.8584 | 145.5541 | 145.5541 | 144.2506
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | Power Factor | 0.9863 | 0.98624 | 0.98609 | 0.98593 | 0.98562
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | 50 POE Load (A) | 384.9114 | 381.3321 | 377.7555 | 377.7555 | 374.1815
Lytton Bulk | 688-1 | Lytton BS | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
Lytton Bulk | 688-1 | Lytton BS | Lindum | 10 POE Load (A) | 257.6322 | 255.3616 | 253.0925 | 253.0925 | 250.8249
Lytton Bulk | 688-1 | Lytton BS | Lindum | Power Factor | 0.96154 | 0.96143 | 0.96116 | 0.96088 | 0.96032
Lytton Bulk | 688-1 | Lytton BS | Lindum | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Lytton Bulk | 688-1 | Lytton BS | Lindum | 50 POE Load (A) | 384.0463 | 380.4847 | 376.9254 | 376.9254 | 373.3686
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | NCC Rating (A) | 700 | 704 | 704 | 704 | 704 | Urban | 70
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | 10 POE Load (A) | 38.8817 | 44.3763 | 41.2212 | 38.603 | 35.9255
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | Power Factor | 0.92563 | 0.92599 | 0.92638 | 0.92686 | 0.92726
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | 50 POE Load (A) | 162.6885 | 160.8149 | 159.056 | 157.318 | 155.5729
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | 10 POE Load (A) | 191.1312 | 183.9018 | 191.5139 | 196.7859 | 201.1393
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | Power Factor | 0.97975 | 0.97879 | 0.9781 | 0.97736 | 0.97632
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | ECC Rating (A) | 787 | 787 | 787 | 787 | 787
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | 50 POE Load (A) | 316.7049 | 315.9877 | 317.7363 | 324.7615 | 332.1422
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | 10 POE Load (A) | 189.6181 | 182.437 | 189.9879 | 195.219 | 199.538
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | Power Factor | 0.9798 | 0.97884 | 0.97815 | 0.97741 | 0.97637
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | ECC Rating (A) | 787 | 787 | 787 | 787 | 787
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | 50 POE Load (A) | 316.0438 | 315.3238 | 317.0688 | 324.0798 | 331.4453
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | 10 POE Load (A) | 131.3904 | 127.6172 | 129.6853 | 131.6964 | 132.6734
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | Power Factor | 0.94936 | 0.94906 | 0.94894 | 0.94881 | 0.94843
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | 50 POE Load (A) | 173.8067 | 172.2486 | 172.2269 | 174.273 | 176.3391
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 847 | 847 | 847 | 847 | 847 | Urban | 70
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | 10 POE Load (A) | 0.8432 | 0.8432 | 0.8432 | 0.8432 | 0.8432
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | Power Factor | 5.6184e-06 | 5.6184e-06 | 5.6182e-06 | 5.6187e-06 | 5.6184e-06
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | 10 POE Load (A) | 0.56996 | 0.56996 | 0.56996 | 0.56996 | 0.56996
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | Power Factor | 9.0967e-06 | 9.097e-06 | 9.0967e-06 | 9.097e-06 | 9.0967e-06
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | NCC Rating (A) | 710 | 710 | 710 | 710 | 710 | Urban | 70
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | 10 POE Load (A) | 355.0044 | 362.1216 | 373.0336 | 372.2627 | 370.8007
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | Power Factor | 0.97232 | 0.97167 | 0.97158 | 0.97095 | 0.97061
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | ECC Rating (A) | 710 | 710 | 710 | 710 | 710
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | 50 POE Load (A) | 570.3568 | 577.771 | 590.6877 | 589.4752 | 586.5723
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Urban | 70
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | 10 POE Load (A) | 282.2154 | 287.875 | 296.552 | 295.939 | 294.7765
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | Power Factor | 0.98055 | 0.98 | 0.97993 | 0.97939 | 0.9791
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | 50 POE Load (A) | 463.0636 | 473.0092 | 489.222 | 487.653 | 485.1898
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | 10 POE Load (A) | 321.7167 | 314.9899 | 306.0991 | 306.4993 | 307.4402
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | Power Factor | 0.97827 | 0.97865 | 0.97842 | 0.97882 | 0.9781
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | 50 POE Load (A) | 718.752 | 712.4021 | 705.0684 | 706.4863 | 704.8799
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | 10 POE Load (A) | 214.3072 | 213.8178 | 214.4478 | 216.1898 | 221.2653
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | Power Factor | 0.93552 | 0.93504 | 0.9349 | 0.93439 | 0.93409
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | 50 POE Load (A) | 390.9671 | 390.9926 | 391.0614 | 394.7261 | 398.364
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | 10 POE Load (A) | 109.584 | 103.3799 | 93.9301 | 92.6113 | 88.5527
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | Power Factor | 0.98395 | 0.97714 | 0.97602 | 0.96811 | 0.96894
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | 50 POE Load (A) | 639.1993 | 633.4822 | 627.8944 | 625.9775 | 620.1222
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | 10 POE Load (A) | 143.5878 | 141.0778 | 139.4078 | 138.5738 | 136.9078
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | Power Factor | 0.9997 | 0.9949 | 0.99516 | 0.99555 | 0.99561
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | ECC Rating (A) | 637 | 637 | 637 | 637 | 637
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | 50 POE Load (A) | 338.3039 | 333.6216 | 326.6565 | 324.35 | 322.0508
Molendinar Bulk | 390-2 | F390 Tee | Bundall | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Urban | 70
Molendinar Bulk | 390-2 | F390 Tee | Bundall | 10 POE Load (A) | 143.7445 | 141.2338 | 139.5633 | 138.7291 | 137.0626
Molendinar Bulk | 390-2 | F390 Tee | Bundall | Power Factor | 0.99944 | 0.9951 | 0.99532 | 0.99565 | 0.99571
Molendinar Bulk | 390-2 | F390 Tee | Bundall | ECC Rating (A) | 653 | 653 | 653 | 653 | 653
Molendinar Bulk | 390-2 | F390 Tee | Bundall | 50 POE Load (A) | 338.5113 | 333.8281 | 326.8616 | 324.5546 | 322.255
Molendinar Bulk | 390-3 | F390 Tee | Miami | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
Molendinar Bulk | 390-3 | F390 Tee | Miami | 10 POE Load (A) | 0.18332 | 0.1834 | 0.18345 | 0.18347 | 0.18349
Molendinar Bulk | 390-3 | F390 Tee | Miami | Power Factor | 1 | 1 | 1 | 1 | 1
Molendinar Bulk | 390-3 | F390 Tee | Miami | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
Molendinar Bulk | 390-3 | F390 Tee | Miami | 50 POE Load (A)
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | NCC Rating (A) | 623 | 623 | 623 | 623 | 623 | Urban | 70
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | 10 POE Load (A) | 180.8507 | 177.7065 | 175.6145 | 174.5698 | 172.4827
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | Power Factor | 0.99463 | 0.98528 | 0.98567 | 0.98627 | 0.98637
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | 50 POE Load (A) | 324.2178 | 320.0545 | 313.8384 | 311.7739 | 309.7132
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Urban | 70
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | 10 POE Load (A) | 268.6911 | 265.9437 | 264.114 | 264.114 | 262.2859
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | Power Factor | 0.96802 | 0.96879 | 0.96893 | 0.96898 | 0.96882
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | 50 POE Load (A) | 493.8857 | 488.3171 | 484.6095 | 484.6095 | 480.9055
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | NCC Rating (A) | 673 | 673 | 673 | 673 | 673 | Urban | 553
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | 10 POE Load (A) | 481.3774 | 478.919 | 478.2101 | 477.2342 | 474.9164
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | Power Factor | 0.98031 | 0.98041 | 0.98053 | 0.98034 | 0.97982
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | 50 POE Load (A) | 776.7805 | 773.1018 | 773.2514 | 770.8812 | 767.3648
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | 10 POE Load (A) | 189.4112 | 189.9303 | 191.1857 | 191.2638 | 191.661
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | Power Factor | 0.97893 | 0.97883 | 0.97866 | 0.97856 | 0.97813
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | 50 POE Load (A) | 400.5804 | 400.5804 | 400.5804 | 404.5593 | 408.5471
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | 10 POE Load (A) | 269.5886 | 266.8335 | 264.9986 | 264.9986 | 263.1653
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | Power Factor | 0.96797 | 0.96874 | 0.96887 | 0.96893 | 0.96877
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | 50 POE Load (A) | 494.1368 | 488.5673 | 484.859 | 484.859 | 481.1544
Molendinar Bulk | 474A-1 | Arundel | Hollywell | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 517
Molendinar Bulk | 474A-1 | Arundel | Hollywell | 10 POE Load (A) | 567.9303 | 568.5317 | 570.5738 | 570.0168 | 568.4748
Molendinar Bulk | 474A-1 | Arundel | Hollywell | Power Factor | 0.96391 | 0.96414 | 0.96437 | 0.96441 | 0.96455
Molendinar Bulk | 474A-1 | Arundel | Hollywell | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
Molendinar Bulk | 474A-1 | Arundel | Hollywell | 50 POE Load (A) | 642.0327 | 645.0038 | 651.6318 | 651.0849 | 648.0786
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Urban | 70
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | 10 POE Load (A) | 3.686 | 3.6861 | 3.6862 | 3.6863 | 3.6867
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | Power Factor | 5.1781e-05 | 5.1781e-05 | 5.1781e-05 | 5.1781e-05 | 5.1781e-05
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | ECC Rating (A) | 786 | 786 | 786 | 786 | 786
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | 50 POE Load (A)
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | NCC Rating (A) | 673 | 673 | 673 | 673 | 673 | Urban | 70
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | 10 POE Load (A) | 481.7258 | 479.2656 | 478.5563 | 477.5796 | 475.2601
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | Power Factor | 0.98029 | 0.98038 | 0.9805 | 0.98031 | 0.9798
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | 50 POE Load (A) | 776.8928 | 773.2135 | 773.3632 | 770.9927 | 767.4758
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | 10 POE Load (A) | 220.3082 | 217.6751 | 215.9216 | 214.956 | 213.2067
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | Power Factor | 0.97233 | 0.97232 | 0.97214 | 0.97202 | 0.97165
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | 50 POE Load (A) | 405.8594 | 402.149 | 398.4429 | 398.4429 | 394.7409
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | 10 POE Load (A) | 0.004302 | 0.0043021 | 0.0043021 | 0.0043021 | 0.0043021
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | Power Factor | 6.6143e-05 | 6.6145e-05 | 6.6104e-05 | 6.6116e-05 | 6.6126e-05
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | 10 POE Load (A) | 220.3294 | 217.7181 | 215.9216 | 214.956 | 213.2274
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | Power Factor | 0.97344 | 0.97344 | 0.97327 | 0.97317 | 0.97283
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | 50 POE Load (A) | 405.9056 | 402.1951 | 398.4887 | 398.4887 | 394.7866
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | 10 POE Load (A) | 0.12343 | 0.12344 | 0.12345 | 0.12346 | 0.12347
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | Power Factor | 8.6872e-06 | 8.6885e-06 | 8.6866e-06 | 8.6862e-06 | 8.6875e-06
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | 10 POE Load (A) | 220.3294 | 217.7181 | 216.0117 | 215.0453 | 213.2956
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | Power Factor | 0.97562 | 0.97561 | 0.97547 | 0.97538 | 0.97509
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | 50 POE Load (A) | 405.9553 | 402.2445 | 398.538 | 398.538 | 394.8356
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Rural | 170
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | 10 POE Load (A) | 238.356 | 235.5068 | 233.6093 | 232.5639 | 230.6711
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | Power Factor | 0.9697 | 0.9697 | 0.96953 | 0.96943 | 0.9691
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | 50 POE Load (A) | 404.4738 | 400.7869 | 397.1039 | 397.1039 | 393.4249
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | 10 POE Load (A) | 106.961 | 106.0001 | 106.0001 | 106.0001 | 105.0401
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | Power Factor | 0.94107 | 0.94096 | 0.94073 | 0.94059 | 0.94096
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | 50 POE Load (A) | 699.8914 | 750.7145 | 737.5451 | 727.6594 | 713.6734
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | NCC Rating (A) | 755 | 755 | 755 | 755 | 755 | Rural | 170
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | 10 POE Load (A) | 107.8601 | 106.8968 | 106.8968 | 106.8968 | 105.9344
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | Power Factor | 0.93805 | 0.93796 | 0.93776 | 0.93764 | 0.93808
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | ECC Rating (A) | 755 | 755 | 755 | 755 | 755
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | 50 POE Load (A) | 170.2978 | 170.2978 | 168.5736 | 168.5736 | 168.5736
Nambour Bulk | 344-1 | Nambour BS | Maleny | NCC Rating (A) | 155 | 155 | 200 | 200 | 200 | Rural | 170
Nambour Bulk | 344-1 | Nambour BS | Maleny | 10 POE Load (A) | 148.7194 | 146.6933 | 138.323 | 138.323 | 136.491
Nambour Bulk | 344-1 | Nambour BS | Maleny | Power Factor | 0.94586 | 0.94559 | 0.94553 | 0.9453 | 0.94573
Nambour Bulk | 344-1 | Nambour BS | Maleny | ECC Rating (A) | 155 | 155 | 155 | 200 | 200
Nambour Bulk | 344-1 | Nambour BS | Maleny | 50 POE Load (A)
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | 10 POE Load (A) | 94.4666 | 94.3017 | 92.4098 | 92.4098 | 90.4781
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | Power Factor | 0.98999 | 0.99003 | 0.99004 | 0.99008 | 0.99003
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | 50 POE Load (A)
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | 10 POE Load (A) | 207.9813 | 206.2126 | 204.4475 | 203.5663 | 202.6859
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | Power Factor | 0.95896 | 0.95882 | 0.95849 | 0.95816 | 0.95745
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | 50 POE Load (A) | 455.1706 | 450.4958 | 445.8435 | 444.1208 | 441.799
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | NCC Rating (A) | 357 | 357 | 357 | 357 | 357 | Rural | 170
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | 10 POE Load (A) | 208.4629 | 206.6925 | 204.9257 | 204.0436 | 203.1624
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | Power Factor | 0.96153 | 0.96142 | 0.96116 | 0.96091 | 0.96035
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | ECC Rating (A) | 357 | 357 | 357 | 357 | 357
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | 50 POE Load (A) | 455.6525 | 450.9759 | 446.3218 | 444.6029 | 442.2801
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | 10 POE Load (A) | 1.6608 | 1.6614 | 1.662 | 1.6623 | 1.6626
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | Power Factor | 0.00019082 | 0.00019082 | 0.00019082 | 0.00019082 | 0.00019082
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | 50 POE Load (A) | 235.251 | 257.1592 | 254.8064 | 254.7463 | 254.6863
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | 10 POE Load (A) | 265.5757 | 263.3177 | 261.0644 | 259.9395 | 258.8156
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | Power Factor | 0.95467 | 0.95455 | 0.95424 | 0.95395 | 0.95331
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | 50 POE Load (A) | 441.4407 | 437.6535 | 433.3339 | 431.1794 | 429.0286
Nambour Bulk | 489-1 | Nambour BS | Yandina | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Nambour Bulk | 489-1 | Nambour BS | Yandina | 10 POE Load (A) | 97.7737 | 96.8969 | 96.8969 | 96.8969 | 96.0209
Nambour Bulk | 489-1 | Nambour BS | Yandina | Power Factor | 0.99979 | 0.99979 | 0.99981 | 0.99981 | 0.99983
Nambour Bulk | 489-1 | Nambour BS | Yandina | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Nambour Bulk | 489-1 | Nambour BS | Yandina | 50 POE Load (A) | 306.5235 | 324.88 | 319.5602 | 316.0087 | 310.9308
Nudgee Bulk | 3280-1 | Hendra | Clayfield | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
Nudgee Bulk | 3280-1 | Hendra | Clayfield | 10 POE Load (A) | 168.6023 | 167.724 | 166.811 | 167.7045 | 167.6955
Nudgee Bulk | 3280-1 | Hendra | Clayfield | Power Factor | 0.98018 | 0.98009 | 0.97996 | 0.97984 | 0.97956
Nudgee Bulk | 3280-1 | Hendra | Clayfield | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
Nudgee Bulk | 3280-1 | Hendra | Clayfield | 50 POE Load (A) | 310.6842 | 310.7193 | 308.8085 | 308.7978 | 308.7808
Nudgee Bulk | 540-1 | Hendra | Nundah | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | Urban | 70
Nudgee Bulk | 540-1 | Hendra | Nundah | 10 POE Load (A) | 221.1429 | 227.3001 | 224.9546 | 224.8495 | 224.1119
Nudgee Bulk | 540-1 | Hendra | Nundah | Power Factor | 0.98823 | 0.98734 | 0.98755 | 0.98754 | 0.98756
Nudgee Bulk | 540-1 | Hendra | Nundah | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
Nudgee Bulk | 540-1 | Hendra | Nundah | 50 POE Load (A) | 412.9717 | 407.4642 | 403.7137 | 401.8396 | 398.1025
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | NCC Rating (A) | 696 | 696 | 696 | 696 | 696 | Urban | 192
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | 10 POE Load (A) | 657.1785 | 657.9589 | 651.9447 | 650.0179 | 645.6354
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | Power Factor | 0.97561 | 0.97557 | 0.97584 | 0.97594 | 0.97614
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | ECC Rating (A) | 696 | 696 | 696 | 696 | 696
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | 50 POE Load (A) | 793.5488 | 796.6996 | 790.3883 | 787.2291 | 781.7569
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Urban | 70
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | 10 POE Load (A) | 231.6833 | 229.2221 | 227.3778 | 227.3778 | 225.535
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | Power Factor | 0.97304 | 0.97333 | 0.97354 | 0.97354 | 0.97375
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | ECC Rating (A) | 491 | 491 | 491 | 491 | 491
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | 50 POE Load (A) | 317.0575 | 314.2894 | 311.5234 | 311.5234 | 308.7597
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Urban | 70
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | 10 POE Load (A) | 231.9475 | 229.4835 | 227.6371 | 227.6371 | 225.7921
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | Power Factor | 0.99989 | 0.99995 | 0.99999 | 1 | 1
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | ECC Rating (A) | 491 | 491 | 491 | 491 | 491
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | 50 POE Load (A) | 317.2373 | 314.4676 | 311.7001 | 311.7001 | 308.9347
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | NCC Rating (A) | 738 | 738 | 738 | 738 | 738 | Urban | 70
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | 10 POE Load (A) | 444.8764 | 450.0425 | 445.7212 | 444.8432 | 442.4571
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | Power Factor | 0.971 | 0.97068 | 0.97064 | 0.97034 | 0.96997
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | ECC Rating (A) | 738 | 738 | 738 | 738 | 738
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | 50 POE Load (A) | 714.6061 | 720.1169 | 714.5644 | 711.7841 | 707.1511
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | NCC Rating (A) | 738 | 738 | 738 | 738 | 738 | Urban | 70
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | 10 POE Load (A) | 444.8764 | 450.0425 | 445.7212 | 444.8432 | 442.4571
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | Power Factor | 0.971 | 0.97068 | 0.97064 | 0.97034 | 0.96997
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | ECC Rating (A) | 738 | 738 | 738 | 738 | 738
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | 50 POE Load (A) | 714.6061 | 720.1169 | 714.5644 | 711.7841 | 707.1511
Nudgee Bulk | 636-1 | Hendra | Clayfield | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
Nudgee Bulk | 636-1 | Hendra | Clayfield | 10 POE Load (A) | 169.4953 | 168.6124 | 167.6946 | 168.5928 | 168.5838
Nudgee Bulk | 636-1 | Hendra | Clayfield | Power Factor | 0.97342 | 0.97351 | 0.9736 | 0.97351 | 0.97351
Nudgee Bulk | 636-1 | Hendra | Clayfield | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
Nudgee Bulk | 636-1 | Hendra | Clayfield | 50 POE Load (A) | 310.6397 | 310.6747 | 308.7648 | 308.754 | 308.737
Nudgee Bulk | 643-1 | Hendra | Hamilton | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70
Nudgee Bulk | 643-1 | Hendra | Hamilton | 10 POE Load (A) | 201.0927 | 212.075 | 210.2252 | 209.3065 | 208.3813
Nudgee Bulk | 643-1 | Hendra | Hamilton | Power Factor | 0.97185 | 0.97168 | 0.97145 | 0.97064 | 0.97023
Nudgee Bulk | 643-1 | Hendra | Hamilton | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
Nudgee Bulk | 643-1 | Hendra | Hamilton | 50 POE Load (A) | 373.7475 | 397.2013 | 395.2122 | 393.239 | 391.2597
Nudgee Bulk | 674-1 | Hendra | Hamilton | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70
Nudgee Bulk | 674-1 | Hendra | Hamilton | 10 POE Load (A) | 200.6538 | 211.6122 | 209.7664 | 208.8497 | 207.9265
Nudgee Bulk | 674-1 | Hendra | Hamilton | Power Factor | 0.97183 | 0.97166 | 0.97144 | 0.97062 | 0.97021
Nudgee Bulk | 674-1 | Hendra | Hamilton | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
Nudgee Bulk | 674-1 | Hendra | Hamilton | 50 POE Load (A) | 373.7981 | 397.261 | 395.2711 | 393.2971 | 391.317
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | NCC Rating (A) | 478 | 478 | 478 | 478 | 478 | Urban | 70
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | 10 POE Load (A) | 226.7558 | 224.3403 | 222.5303 | 222.5303 | 220.7217
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | Power Factor | 0.96534 | 0.96573 | 0.96602 | 0.96602 | 0.96631
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | ECC Rating (A) | 478 | 478 | 478 | 478 | 478
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | 50 POE Load (A) | 310.8452 | 308.1259 | 305.4088 | 305.4088 | 302.6939
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | 10 POE Load (A) | 57.5616 | 55.8293 | 55.7735 | 55.7735 | 55.7735
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | Power Factor | 0.96291 | 0.96308 | 0.96321 | 0.96335 | 0.9633
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | 50 POE Load (A) | 52.3277 | 52.3277 | 50.6031 | 50.6031 | 50.6031
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | 10 POE Load (A) | 32.7715 | 32.7715 | 32.7715 | 32.7715 | 32.7715
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | Power Factor | 0.99474 | 0.99473 | 0.99475 | 0.99478 | 0.99474
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | 50 POE Load (A)
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Rural | 170
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | 10 POE Load (A) | 0.49343 | 0.49343 | 0.49343 | 0.49343 | 0.49343
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | Power Factor | 0.0001188 | 0.00011877 | 0.00011878 | 0.00011876 | 0.00011886
Raceview Bulk | 354-1 | Raceview BS | Roderick St | NCC Rating (A) | 497 | 497 | 497 | 497 | 497 | Urban | 70
Raceview Bulk | 354-1 | Raceview BS | Roderick St | 10 POE Load (A) | 314.3974 | 315.2947 | 316.0133 | 318.0818 | 319.9722
Raceview Bulk | 354-1 | Raceview BS | Roderick St | Power Factor | 0.99532 | 0.99544 | 0.99547 | 0.99556 | 0.99545
Raceview Bulk | 354-1 | Raceview BS | Roderick St | ECC Rating (A) | 517 | 517 | 517 | 517 | 517
Raceview Bulk | 354-1 | Raceview BS | Roderick St | 50 POE Load (A) | 453.8546 | 453.8546 | 453.8546 | 455.6557 | 455.6557
Raceview Bulk | 355-1 | Roderick St | Booval | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Raceview Bulk | 355-1 | Roderick St | Booval | 10 POE Load (A) | 161.8762 | 161.0057 | 160.3088 | 160.0524 | 159.9699
Raceview Bulk | 355-1 | Roderick St | Booval | Power Factor | 0.99544 | 0.99553 | 0.9956 | 0.99565 | 0.99569
Raceview Bulk | 355-1 | Roderick St | Booval | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Raceview Bulk | 355-1 | Roderick St | Booval | 50 POE Load (A) | 458.6871 | 458.7236 | 458.7602 | 460.6512 | 460.6884
Raceview Bulk | 361-1 | Raceview BS | Booval | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70
Raceview Bulk | 361-1 | Raceview BS | Booval | 10 POE Load (A) | 361.053 | 365.4211 | 368.9196 | 374.6071 | 379.4253
Raceview Bulk | 361-1 | Raceview BS | Booval | Power Factor | 0.98994 | 0.99009 | 0.99005 | 0.99013 | 0.98987
Raceview Bulk | 361-1 | Raceview BS | Booval | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
Raceview Bulk | 361-1 | Raceview BS | Booval | 50 POE Load (A) | 581.6418 | 587.6184 | 593.6016 | 603.3276 | 609.328
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | NCC Rating (A) | 357 | 357 | 357 | 357 | 357 | Rural | 170
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | 10 POE Load (A) | 139.7617 | 138.131 | 136.5092 | 141.3027 | 140.2925
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | Power Factor | 0.98839 | 0.98848 | 0.98848 | 0.98855 | 0.98765
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | ECC Rating (A) | 357 | 357 | 357 | 357 | 357
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | 50 POE Load (A) | 364.809 | 368.9712 | 373.013 | 393.9643 | 399.1607
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Rural | 170
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | 10 POE Load (A) | 39.6513 | 38.8607 | 38.0561 | 34.6784 | 33.5002
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | Power Factor | 0.677 | 0.67297 | 0.6675 | 0.66278 | 0.61403
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | 50 POE Load (A) | 197.0227 | 203.3558 | 209.5739 | 228.8713 | 236.2092
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Rural | 170
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | 10 POE Load (A) | 170.0791 | 167.6932 | 165.3196 | 165.5339 | 163.1891
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | Power Factor | 0.96951 | 0.96972 | 0.96978 | 0.96998 | 0.96961
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | 50 POE Load (A) | 298.1099 | 293.296 | 288.6243 | 289.6167 | 284.8444
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Rural | 170
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | 10 POE Load (A) | 137.2622 | 135.643 | 134.0324 | 138.4804 | 137.4374
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | Power Factor | 0.99242 | 0.99249 | 0.99249 | 0.99254 | 0.9918
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | 50 POE Load (A) | 345.6216 | 349.3644 | 352.9981 | 372.4718 | 377.1723
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | 10 POE Load (A) | 7.4556 | 7.265 | 7.1334 | 8.0165 | 8.0683
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | Power Factor | 0.45853 | 0.42575 | 0.31686 | 1 | 0.22865
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | 50 POE Load (A) | 197.8614 | 203.2916 | 208.5693 | 225.9487 | 232.2873
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | NCC Rating (A) | 374 | 374 | 374 | 374 | 374 | Rural | 170
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | 10 POE Load (A) | 139.8192 | 137.8753 | 135.9415 | 136.389 | 134.5134
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | Power Factor | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 0.99998
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | ECC Rating (A) | 374 | 374 | 374 | 374 | 374
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | 50 POE Load (A) | 317.5935 | 311.9178 | 306.4457 | 307.6645 | 302.09
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | 10 POE Load (A) | 394.7397 | 400.6866 | 406.9619 | 424.6183 | 431.3353
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | Power Factor | 0.94493 | 0.94439 | 0.94357 | 0.94293 | 0.94134
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | 50 POE Load (A) | 442.7374 | 447.3207 | 451.3662 | 470.0498 | 474.4571
Raceview Bulk | 3972-1 | Yamanto | Flinders | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Raceview Bulk | 3972-1 | Yamanto | Flinders | 10 POE Load (A) | 140.1752 | 137.2278 | 134.2755 | 138.7628 | 136.5777
Raceview Bulk | 3972-1 | Yamanto | Flinders | Power Factor | 0.90555 | 0.90527 | 0.90466 | 0.90435 | 0.90145
Raceview Bulk | 3972-1 | Yamanto | Flinders | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Raceview Bulk | 3972-1 | Yamanto | Flinders | 50 POE Load (A) | 288.2002 | 301.7809 | 313.0786 | 334.1902 | 349.6156
Raceview Bulk | 3980-1 | Kalbar | Boonah | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170
Raceview Bulk | 3980-1 | Kalbar | Boonah | 10 POE Load (A) | 80.2445 | 79.1488 | 78.0865 | 78.2179 | 77.1223
Raceview Bulk | 3980-1 | Kalbar | Boonah | Power Factor | 0.98184 | 0.98193 | 0.98195 | 0.98203 | 0.98185
Raceview Bulk | 3980-1 | Kalbar | Boonah | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Raceview Bulk | 3980-1 | Kalbar | Boonah | 50 POE Load (A) | 146.384 | 144.2604 | 142.2208 | 142.3635 | 140.4047
Raceview Bulk | 401-1 | Kalbar | Boonah | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Raceview Bulk | 401-1 | Kalbar | Boonah | 10 POE Load (A) | 77.3573 | 76.3012 | 75.2773 | 75.4028 | 74.3467
Raceview Bulk | 401-1 | Kalbar | Boonah | Power Factor | 0.98195 | 0.98204 | 0.98206 | 0.98214 | 0.98196
Raceview Bulk | 401-1 | Kalbar | Boonah | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Raceview Bulk | 401-1 | Kalbar | Boonah | 50 POE Load (A) | 147.4522 | 145.3137 | 143.1949 | 143.4064 | 141.3698
Raceview Bulk | 411-1 | Raceview BS | Booval | NCC Rating (A) | 558 | 558 | 558 | 558 | 558 | Urban | 70
Raceview Bulk | 411-1 | Raceview BS | Booval | 10 POE Load (A) | 305.5504 | 309.2474 | 312.2289 | 317.0427 | 321.1209
Raceview Bulk | 411-1 | Raceview BS | Booval | Power Factor | 0.99533 | 0.99544 | 0.99541 | 0.99546 | 0.99528
Raceview Bulk | 411-1 | Raceview BS | Booval | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
Raceview Bulk | 411-1 | Raceview BS | Booval | 50 POE Load (A) | 565.1583 | 570.9798 | 576.8082 | 586.2821 | 592.1282
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 721 | 721 | 721 | 721 | 721 | Urban | 70
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | 10 POE Load (A) | 397.8197 | 404.3981 | 410.219 | 423.3922 | 430.3605
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | Power Factor | 0.96453 | 0.96385 | 0.96319 | 0.96243 | 0.96129
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | 50 POE Load (A) | 715.6717 | 728.8294 | 739.2964 | 763.1557 | 774.4602
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | Rural | 170
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | 10 POE Load (A) | 0.48565 | 0.48565 | 0.48565 | 0.48565 | 0.48565
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | Power Factor | 8.7908e-06 | 8.7907e-06 | 8.7913e-06 | 8.791e-06 | 8.7909e-06
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 721 | 721 | 721 | 721 | 721 | Urban | 70
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | 10 POE Load (A) | 393.8237 | 400.3358 | 406.0981 | 419.1388 | 426.0369
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | Power Factor | 0.96456 | 0.96388 | 0.96322 | 0.96246 | 0.96132
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | 50 POE Load (A) | 715.5285 | 728.6846 | 739.1504 | 763.0073 | 774.3105
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | NCC Rating (A) | 426 | 426 | 426 | 426 | 426 | Rural | 170
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | 10 POE Load (A) | 0.62897 | 0.62897 | 0.62897 | 0.62897 | 0.62897
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | Power Factor | 1.6632e-05 | 1.6632e-05 | 1.6632e-05 | 1.6632e-05 | 1.6632e-05
Richlands Bulk | 3818-1 | Richlands BS | Wacol | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Urban | 70
Richlands Bulk | 3818-1 | Richlands BS | Wacol | 10 POE Load (A) | 103.594 | 102.6556 | 126.2053 | 125.772 | 124.9056
Richlands Bulk | 3818-1 | Richlands BS | Wacol | Power Factor | 0.99807 | 0.99861 | 0.99845 | 0.99823 | 0.99816
Richlands Bulk | 3818-1 | Richlands BS | Wacol | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
Richlands Bulk | 3818-1 | Richlands BS | Wacol | 50 POE Load (A) | 198.2686 | 196.2266 | 244.583 | 244.583 | 242.7786
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 430 | 430 | 430 | 430 | 430 | Urban | 70
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | 10 POE Load (A) | 212.9736 | 211.3052 | 208.5666 | 207.6545 | 206.7428
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | Power Factor | 0.97309 | 0.97315 | 0.97322 | 0.97335 | 0.97323
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | ECC Rating (A) | 460 | 460 | 460 | 460 | 460
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | 50 POE Load (A) | 393.4649 | 389.7436 | 386.0264 | 384.1694 | 382.3134
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 430 | 430 | 430 | 430 | 430 | Urban | 70
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | 10 POE Load (A) | 214.3381 | 212.659 | 209.9028 | 208.9849 | 208.0674
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | Power Factor | 0.97313 | 0.9732 | 0.97326 | 0.9734 | 0.97328
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | ECC Rating (A) | 460 | 460 | 460 | 460 | 460
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | 50 POE Load (A) | 393.4105 | 389.6904 | 385.9744 | 384.1179 | 382.2625
Richlands Bulk | 543-1 | Inala | 543 Tee1 | NCC Rating (A) | 836 | 836 | 836 | 836 | 836 | Urban | 70
Richlands Bulk | 543-1 | Inala | 543 Tee1 | 10 POE Load (A) | 2.9538 | 2.9542 | 2.9544 | 2.9545 | 2.9545
Richlands Bulk | 543-1 | Inala | 543 Tee1 | Power Factor | -8.3786e-05 | -8.3786e-05 | -8.3786e-05 | -8.3786e-05 | -8.3786e-05
Richlands Bulk | 543-1 | Inala | 543 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Richlands Bulk | 543-1 | Inala | 543 Tee1 | 50 POE Load (A) | 589.1735 | 579.6228 | 572.498 | 567.7839 | 560.7948
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | 10 POE Load (A) | 0.20546 | 0.20549 | 0.2055 | 0.20551 | 0.20551
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | Power Factor | -7.5154e-06 | -7.5156e-06 | -7.5151e-06 | -7.5144e-06 | -7.5148e-06
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | 50 POE Load (A)
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | 10 POE Load (A) | 2.1928 | 2.193 | 2.1932 | 2.1933 | 2.1933
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | Power Factor | 9.1011e-05 | 9.1011e-05 | 9.1011e-05 | 9.1011e-05 | 9.1011e-05
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | ECC Rating (A) | 807 | 807 | 807 | 807 | 807
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | 50 POE Load (A) | 589.7653 | 580.2099 | 573.0817 | 568.3654 | 561.3729
Richlands Bulk | 616-1 | Richlands BS | Darra | NCC Rating (A) | 407 | 407 | 407 | 407 | 407 | Urban | 70
Richlands Bulk | 616-1 | Richlands BS | Darra | 10 POE Load (A) | 245.8425 | 244.4355 | 243.5224 | 244.0443 | 244.0764
Richlands Bulk | 616-1 | Richlands BS | Darra | Power Factor | 0.93306 | 0.93026 | 0.92784 | 0.92446 | 0.92294
Richlands Bulk | 616-1 | Richlands BS | Darra | ECC Rating (A) | 440 | 440 | 440 | 440 | 440
Richlands Bulk | 616-1 | Richlands BS | Darra | 50 POE Load (A) | 369.0338 | 368.3266 | 366.9147 | 366.8745 | 367.6879
Richlands Bulk | 617-1 | Richlands BS | Darra | NCC Rating (A) | 407 | 407 | 407 | 407 | 407 | Urban | 70
Richlands Bulk | 617-1 | Richlands BS | Darra | 10 POE Load (A) | 254.0025 | 252.5474 | 251.603 | 252.1426 | 252.1757
Richlands Bulk | 617-1 | Richlands BS | Darra | Power Factor | 0.93334 | 0.93055 | 0.92813 | 0.92476 | 0.92324
Richlands Bulk | 617-1 | Richlands BS | Darra | ECC Rating (A) | 440 | 440 | 440 | 440 | 440
Richlands Bulk | 617-1 | Richlands BS | Darra | 50 POE Load (A) | 374.3035 | 373.5857 | 372.1527 | 372.1119 | 372.9374
Richlands Bulk | 618-1 | Richlands BS | Inala | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Richlands Bulk | 618-1 | Richlands BS | Inala | 10 POE Load (A) | 353.88 | 350.4938 | 348.2386 | 347.1117 | 347.1117
Richlands Bulk | 618-1 | Richlands BS | Inala | Power Factor | 0.96028 | 0.96 | 0.95969 | 0.95942 | 0.95995
Richlands Bulk | 618-1 | Richlands BS | Inala | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Richlands Bulk | 618-1 | Richlands BS | Inala | 50 POE Load (A) | 680.9637 | 672.8776 | 666.2665 | 662.2616 | 658.0131
Richlands Bulk | 619-1 | Richlands BS | Inala | NCC Rating (A) | 550 | 550 | 550 | 550 | 550 | Urban | 70
Richlands Bulk | 619-1 | Richlands BS | Inala | 10 POE Load (A) | 228.573 | 226.3864 | 224.9301 | 224.2025 | 224.2025
Richlands Bulk | 619-1 | Richlands BS | Inala | Power Factor | 0.96084 | 0.96056 | 0.96026 | 0.95999 | 0.96052
Richlands Bulk | 619-1 | Richlands BS | Inala | ECC Rating (A) | 550 | 550 | 550 | 550 | 550
Richlands Bulk | 619-1 | Richlands BS | Inala | 50 POE Load (A) | 544.3994 | 538.684 | 534.8792 | 534.8792 | 532.9785
Richlands Bulk | 620-1 | Richlands BS | Oxley | NCC Rating (A) | 324 | 324 | 324 | 324 | 324 | Urban | 70
Richlands Bulk | 620-1 | Richlands BS | Oxley | 10 POE Load (A) | 214.6327 | 211.8461 | 209.9899 | 209.9899 | 208.135
Richlands Bulk | 620-1 | Richlands BS | Oxley | Power Factor | 0.96045 | 0.96077 | 0.96099 | 0.96099 | 0.96121
Richlands Bulk | 620-1 | Richlands BS | Oxley | ECC Rating (A) | 359 | 359 | 359 | 359 | 359
Richlands Bulk | 620-1 | Richlands BS | Oxley | 50 POE Load (A) | 363.4618 | 361.5303 | 357.6727 | 355.7466 | 353.8222
Richlands Bulk | 621-1 | Richlands BS | Oxley | NCC Rating (A) | 324 | 324 | 324 | 324 | 324 | Urban | 70
Richlands Bulk | 621-1 | Richlands BS | Oxley | 10 POE Load (A) | 204.2795 | 201.6274 | 199.8608 | 199.8608 | 198.0954
Richlands Bulk | 621-1 | Richlands BS | Oxley | Power Factor | 0.9551 | 0.95545 | 0.95568 | 0.95568 | 0.95591
Richlands Bulk | 621-1 | Richlands BS | Oxley | ECC Rating (A) | 359 | 359 | 359 | 359 | 359
Richlands Bulk | 621-1 | Richlands BS | Oxley | 50 POE Load (A) | 363.6706 | 361.7336 | 357.8654 | 355.9341 | 354.0047
Richlands Bulk | 641-1 | Darra | Jindalee | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70
Richlands Bulk | 641-1 | Darra | Jindalee | 10 POE Load (A) | 133.8254 | 132.0445 | 130.2651 | 129.3765 | 128.4878
Richlands Bulk | 641-1 | Darra | Jindalee | Power Factor | 0.98105 | 0.98121 | 0.98138 | 0.98146 | 0.98154
Richlands Bulk | 641-1 | Darra | Jindalee | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Richlands Bulk | 641-1 | Darra | Jindalee | 50 POE Load (A) | 250.5066 | 248.6649 | 244.9861 | 243.1497 | 241.3154
Richlands Bulk | 642-1 | Darra | Jindalee | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70
Richlands Bulk | 642-1 | Darra | Jindalee | 10 POE Load (A) | 131.1571 | 129.4122 | 127.6687 | 126.7981 | 125.9273
Richlands Bulk | 642-1 | Darra | Jindalee | Power Factor | 0.98003 | 0.9802 | 0.98036 | 0.98045 | 0.98053
Richlands Bulk | 642-1 | Darra | Jindalee | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Richlands Bulk | 642-1 | Darra | Jindalee | 50 POE Load (A) | 250.6045 | 248.7606 | 245.0774 | 243.2388 | 241.4024
Richlands Bulk | 679-1 | Richlands BS | Wacol | NCC Rating (A) | 605 | 605 | 605 | 605 | 605 | Urban | 70
Richlands Bulk | 679-1 | Richlands BS | Wacol | 10 POE Load (A) | 104.9572 | 104.0079 | 127.9026 | 127.4635 | 126.5854
Richlands Bulk | 679-1 | Richlands BS | Wacol | Power Factor | 0.99196 | 0.9937 | 0.98587 | 0.9859 | 0.98597
Richlands Bulk | 679-1 | Richlands BS | Wacol | ECC Rating (A) | 605 | 605 | 605 | 605 | 605
Richlands Bulk | 679-1 | Richlands BS | Wacol | 50 POE Load (A) | 198.2895 | 196.2513 | 244.5877 | 244.5877 | 242.7838
Richlands Bulk | 680-1 | Richlands BS | Wacol | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Urban | 70
Richlands Bulk | 680-1 | Richlands BS | Wacol | 10 POE Load (A) | 210.5078 | 208.4212 | 258.028 | 257.1209 | 255.3075
Richlands Bulk | 680-1 | Richlands BS | Wacol | Power Factor | 0.99919 | 0.99877 | 0.99891 | 0.99908 | 0.99913
Richlands Bulk | 680-1 | Richlands BS | Wacol | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
Richlands Bulk | 680-1 | Richlands BS | Wacol | 50 POE Load (A)
Richlands Bulk | 700-1 | Richlands BS | Darra | NCC Rating (A) | 517 | 517 | 517 | 517 | 517 | Urban | 70
Richlands Bulk | 700-1 | Richlands BS | Darra | 10 POE Load (A) | 194.4673 | 193.3555 | 192.6339 | 193.0465 | 193.072
Richlands Bulk | 700-1 | Richlands BS | Darra | Power Factor | 0.95873 | 0.95651 | 0.95457 | 0.95186 | 0.95063
Richlands Bulk | 700-1 | Richlands BS | Darra | ECC Rating (A) | 517 | 517 | 517 | 517 | 517
Richlands Bulk | 700-1 | Richlands BS | Darra | 50 POE Load (A) | 291.9684 | 291.4093 | 290.2932 | 290.2612 | 290.9045
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | NCC Rating (A) | 544 | 544 | 544 | 544 | 544 | Urban | 70
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | 10 POE Load (A) | 445.5772 | 441.1185 | 438.1476 | 436.6626 | 433.6937
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | Power Factor | 0.98802 | 0.98832 | 0.98859 | 0.98903 | 0.98905
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | ECC Rating (A) | 544 | 544 | 544 | 544 | 544
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | 50 POE Load (A) | 509.6707 | 506.0863 | 500.7128 | 498.9225 | 495.3429
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | NCC Rating (A) | 406 | 406 | 406 | 406 | 406 | Urban | 70
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | 10 POE Load (A) | 2.354 | 2.354 | 2.354 | 2.354 | 2.354
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | Power Factor | 4.0608e-05 | 4.0608e-05 | 4.0608e-05 | 4.0608e-05 | 4.0608e-05
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | ECC Rating (A) | 406 | 406 | 406 | 406 | 406
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | 50 POE Load (A)
Runcorn Bulk | 434-1 | Runcorn | Calamvale | NCC Rating (A) | 406 | 406 | 406 | 406 | 406 | Urban | 70
Runcorn Bulk | 434-1 | Runcorn | Calamvale | 10 POE Load (A) | 1.6773 | 1.6774 | 1.6775 | 1.6776 | 1.6776
Runcorn Bulk | 434-1 | Runcorn | Calamvale | Power Factor | 6.272e-05 | 6.272e-05 | 6.272e-05 | 6.272e-05 | 6.272e-05
Runcorn Bulk | 434-1 | Runcorn | Calamvale | ECC Rating (A) | 406 | 406 | 406 | 406 | 406
Runcorn Bulk | 434-1 | Runcorn | Calamvale | 50 POE Load (A)
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | 10 POE Load (A)
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | Power Factor | 0.93 | 0.926 | 0.926 | 0.926 | 0.926
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | 50 POE Load (A)
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | NCC Rating (A) | 801 | 801 | 801 | 801 | 801 | Urban | 70
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | 10 POE Load (A)
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | Power Factor | 0.942 | 0.937 | 0.937 | 0.937 | 0.937
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | ECC Rating (A) | 801 | 801 | 801 | 801 | 801
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | 50 POE Load (A)
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 426 | 426 | 426 | 426 | 426 | Urban | 70
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | 10 POE Load (A) | 27.7124 | 27.7124 | 27.7124 | 27.7124 | 27.7124
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | Power Factor | 9.2863e-05 | 9.2863e-05 | 9.2863e-05 | 9.2863e-05 | 9.2863e-05
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | ECC Rating (A) | 426 | 426 | 426 | 426 | 426
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | 50 POE Load (A)
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 426 | 426 | 426 | 426 | 426 | Urban | 70
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | 10 POE Load (A) | 27.8479 | 27.8479 | 27.8479 | 27.8479 | 27.8479
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | Power Factor | 1 | 1 | 1 | 1 | 1
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | ECC Rating (A) | 426 | 426 | 426 | 426 | 426
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | 50 POE Load (A)
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | 10 POE Load (A) | 224.7746 | 222.773 | 219.7729 | 218.7735 | 216.7756
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | Power Factor | 0.9763 | 0.97634 | 0.97628 | 0.97619 | 0.9759
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | 50 POE Load (A) | 377.2423 | 371.8453 | 368.2504 | 366.4539 | 362.8627
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | 10 POE Load (A) | 177.8614 | 176.2775 | 173.9036 | 173.1128 | 171.5319
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | Power Factor | 0.97683 | 0.97687 | 0.97682 | 0.97673 | 0.97644
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | 50 POE Load (A) | 378.0593 | 372.6352 | 369.0227 | 367.2174 | 363.6089
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | NCC Rating (A) | 531 | 531 | 531 | 531 | 531 | Urban | 260
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | 10 POE Load (A) | 278.9604 | 368.5351 | 366.629 | 366.629 | 366.629
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | Power Factor | 0.97956 | 0.98 | 0.97996 | 0.97991 | 0.97955
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | ECC Rating (A) | 531 | 531 | 531 | 531 | 531
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | 50 POE Load (A) | 509.9571 | 731.071 | 724.3229 | 724.3229 | 726.5689
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | NCC Rating (A) | 853 | 853 | 853 | 853 | 853 | Urban | 70
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | 10 POE Load (A) | 70.4313 | 69.5911 | 68.7511 | 68.7511 | 67.9114
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | Power Factor | 1 | 0.99999 | 0.99999 | 0.99999 | 0.99999
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | ECC Rating (A) | 853 | 853 | 853 | 853 | 853
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | 50 POE Load (A) | 127.6092 | 125.8931 | 124.1775 | 124.1775 | 122.4626
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | 10 POE Load (A) | 294.5663 | 290.49 | 286.1907 | 283.7617 | 280.528
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | Power Factor | 0.97927 | 0.97996 | 0.98143 | 0.98182 | 0.98234
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | 50 POE Load (A) | 398.9431 | 393.0714 | 388.3841 | 385.213 | 381.699
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | NCC Rating (A) | 453 | 453 | 453 | 453 | 453 | Urban | 70
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | 10 POE Load (A) | 198.272 | 195.5374 | 192.6614 | 191.0318 | 188.8625
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | Power Factor | 0.99043 | 0.99091 | 0.99191 | 0.99217 | 0.99253
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | ECC Rating (A) | 453 | 453 | 453 | 453 | 453
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | 50 POE Load (A) | 337.7626 | 332.7557 | 328.7606 | 325.7703 | 322.7852
Sandgate Bulk | 524-2 | Geebung | Zillmere | NCC Rating (A) | 410 | 410 | 410 | 410 | 410 | Urban | 70
Sandgate Bulk | 524-2 | Geebung | Zillmere | 10 POE Load (A) | 202.8533 | 200.0453 | 197.0263 | 195.3485 | 193.1326
Sandgate Bulk | 524-2 | Geebung | Zillmere | Power Factor | 0.99391 | 0.99413 | 0.99422 | 0.99431 | 0.99406
Sandgate Bulk | 524-2 | Geebung | Zillmere | ECC Rating (A) | 410 | 410 | 410 | 410 | 410
Sandgate Bulk | 524-2 | Geebung | Zillmere | 50 POE Load (A) | 342.2893 | 337.2131 | 333.1622 | 330.13 | 327.1029
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Urban | 70
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | 10 POE Load (A) | 95.7146 | 94.8348 | 93.0758 | 92.1967 | 91.3177
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | Power Factor | 0.98929 | 0.98936 | 0.98939 | 0.98943 | 0.98937
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | ECC Rating (A) | 786 | 786 | 786 | 786 | 786
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | 50 POE Load (A) | 173.3832 | 171.6299 | 168.126 | 166.3756 | 164.6261
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | NCC Rating (A) | 270 | 270 | 270 | 270 | 270 | Urban | 70
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | 10 POE Load (A) | 91.8844 | 91.0401 | 89.3521 | 88.5085 | 87.665
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | Power Factor | 0.99799 | 0.99803 | 0.99804 | 0.99806 | 0.99803
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | ECC Rating (A) | 270 | 270 | 270 | 270 | 270
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | 50 POE Load (A) | 174.8826 | 173.0995 | 169.5372 | 167.758 | 165.9802
Sandgate Bulk | 664-1 | Geebung | Zillmere | NCC Rating (A) | 410 | 410 | 410 | 410 | 410 | Urban | 70
Sandgate Bulk | 664-1 | Geebung | Zillmere | 10 POE Load (A) | 24.8963 | 24.9022 | 24.908 | 24.9103 | 24.9149
Sandgate Bulk | 664-1 | Geebung | Zillmere | Power Factor | 1 | 1 | 1 | 1 | 1
Sandgate Bulk | 664-1 | Geebung | Zillmere | ECC Rating (A) | 410 | 410 | 410 | 410 | 410
Sandgate Bulk | 664-1 | Geebung | Zillmere | 50 POE Load (A)
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | NCC Rating (A) | 507 | 507 | 507 | 507 | 507 | Urban | 70
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | 10 POE Load (A) | 173.684 | 171.282 | 168.7446 | 167.3133 | 165.4078
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | Power Factor | 0.99908 | 0.99918 | 0.99922 | 0.99925 | 0.99915
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | ECC Rating (A) | 507 | 507 | 507 | 507 | 507
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | 50 POE Load (A) | 295.7955 | 291.405 | 287.9016 | 285.2794 | 282.6617
Stafford Bulk | 548-1 | Stafford BS | Enoggera | NCC Rating (A) | 836 | 836 | 836 | 836 | 836 | Urban | 170
Stafford Bulk | 548-1 | Stafford BS | Enoggera | 10 POE Load (A) | 555.1677 | 550.7936 | 545.3426 | 542.6194 | 539.8978
Stafford Bulk | 548-1 | Stafford BS | Enoggera | Power Factor | 0.97513 | 0.97526 | 0.97531 | 0.97538 | 0.97529
Stafford Bulk | 548-1 | Stafford BS | Enoggera | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
Stafford Bulk | 548-1 | Stafford BS | Enoggera | 50 POE Load (A) | 1040.1568 | 1029.1689 | 1020.0306 | 1014.5283 | 1007.2377
Stafford Bulk | 550-1 | Stafford BS | Chermside | NCC Rating (A) | 668 | 668 | 668 | 668 | 668 | Urban | 70
Stafford Bulk | 550-1 | Stafford BS | Chermside | 10 POE Load (A) | 391.0519 | 386.5779 | 383.0165 | 381.2369 | 377.6797
Stafford Bulk | 550-1 | Stafford BS | Chermside | Power Factor | 0.99731 | 0.99744 | 0.99758 | 0.99777 | 0.99775
Stafford Bulk | 550-1 | Stafford BS | Chermside | ECC Rating (A) | 789 | 789 | 789 | 789 | 789
Stafford Bulk | 550-1 | Stafford BS | Chermside | 50 POE Load (A) | 736.5411 | 727.5565 | 720.4054 | 716.8323 | 711.4755
Stafford Bulk | 551-1 | Stafford BS | Chermside | NCC Rating (A) | 668 | 668 | 668 | 668 | 668 | Urban | 70
Stafford Bulk | 551-1 | Stafford BS | Chermside | 10 POE Load (A) | 390.3053 | 385.8398 | 382.2852 | 380.509 | 376.9586
Stafford Bulk | 551-1 | Stafford BS | Chermside | Power Factor | 0.99731 | 0.99745 | 0.99758 | 0.99778 | 0.99775
Stafford Bulk | 551-1 | Stafford BS | Chermside | ECC Rating (A) | 789 | 789 | 789 | 789 | 789
Stafford Bulk | 551-1 | Stafford BS | Chermside | 50 POE Load (A) | 736.5531 | 727.5682 | 720.4169 | 716.8436 | 711.4866
Stafford Bulk | 567-1 | Stafford BS | Kedron | NCC Rating (A) | 576 | 576 | 576 | 576 | 576 | Urban | 70
Stafford Bulk | 567-1 | Stafford BS | Kedron | 10 POE Load (A) | 270.554 | 280.5119 | 277.7926 | 276.8868 | 275.076
Stafford Bulk | 567-1 | Stafford BS | Kedron | Power Factor | 0.9837 | 0.98375 | 0.98146 | 0.98142 | 0.99693
Stafford Bulk | 567-1 | Stafford BS | Kedron | ECC Rating (A) | 643 | 643 | 643 | 643 | 643
Stafford Bulk | 567-1 | Stafford BS | Kedron | 50 POE Load (A) | 503.5358 | 525.3714 | 519.904 | 518.0828 | 514.4424
Stafford Bulk | 568-1 | Stafford BS | Kedron | NCC Rating (A) | 576 | 576 | 576 | 576 | 576 | Urban | 70
Stafford Bulk | 568-1 | Stafford BS | Kedron | 10 POE Load (A) | 272.606 | 282.6396 | 279.8996 | 278.9869 | 277.1623
Stafford Bulk | 568-1 | Stafford BS | Kedron | Power Factor | 0.97421 | 0.97317 | 0.97345 | 0.97355 | 0.97374
Stafford Bulk | 568-1 | Stafford BS | Kedron | ECC Rating (A) | 643 | 643 | 643 | 643 | 643
Stafford Bulk | 568-1 | Stafford BS | Kedron | 50 POE Load (A) | 503.4987 | 525.3309 | 519.8644 | 518.0435 | 514.4036
Stafford Bulk | 594-1 | Stafford BS | Enoggera | NCC Rating (A) | 836 | 836 | 836 | 836 | 836 | Urban | 70
Stafford Bulk | 594-1 | Stafford BS | Enoggera | 10 POE Load (A) | 551.666 | 547.3195 | 541.9028 | 539.1968 | 536.4923
Stafford Bulk | 594-1 | Stafford BS | Enoggera | Power Factor | 0.97515 | 0.97528 | 0.97533 | 0.9754 | 0.97531
Stafford Bulk | 594-1 | Stafford BS | Enoggera | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
Stafford Bulk | 594-1 | Stafford BS | Enoggera | 50 POE Load (A) | 1040.2412 | 1029.251 | 1020.1108 | 1014.6074 | 1007.3153
Stafford Bulk | 595-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
Stafford Bulk | 595-1 | Enoggera | Grovely | 10 POE Load (A) | 236.199 | 232.7523 | 229.1452 | 227.3405 | 225.5307
Stafford Bulk | 595-1 | Enoggera | Grovely | Power Factor | 0.97619 | 0.97648 | 0.97662 | 0.97681 | 0.97674
Stafford Bulk | 595-1 | Enoggera | Grovely | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
Stafford Bulk | 595-1 | Enoggera | Grovely | 50 POE Load (A) | 452.5845 | 445.636 | 439.723 | 433.8423 | 429.9189
Stafford Bulk | 596-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
Stafford Bulk | 596-1 | Enoggera | Grovely | 10 POE Load (A) | 237.7804 | 234.3177 | 230.68 | 228.8632 | 227.0475
Stafford Bulk | 596-1 | Enoggera | Grovely | Power Factor | 0.97616 | 0.97645 | 0.97659 | 0.97678 | 0.97671
Stafford Bulk | 596-1 | Enoggera | Grovely | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
Stafford Bulk | 596-1 | Enoggera | Grovely | 50 POE Load (A) | 453.2955 | 445.3986 | 439.4947 | 433.6229 | 429.7052
Stafford Bulk | 607-1 | Chermside | Zillmere | NCC Rating (A) | 311 |  |  |  |  | Urban | 70
Stafford Bulk | 607-1 | Chermside | Zillmere | 10 POE Load (A) | 0.2108
Stafford Bulk | 607-1 | Chermside | Zillmere | Power Factor | 1.3215e-05 | 1.3215e-05 | 1.3215e-05 | 1.3215e-05 | 1.3215e-05
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | 10 POE Load (A) | 593.3107 | 642.9398 | 631.4076 | 627.2963 | 615.8124
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | Power Factor | 0.9539 | 0.94204 | 0.94178 | 0.94149 | 0.94013
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | 50 POE Load (A)
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | 10 POE Load (A) | 593.3107 | 643.0036 | 631.4711 | 627.359 | 615.8747
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | Power Factor | 0.96104 | 0.95123 | 0.95101 | 0.95077 | 0.94964
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | 50 POE Load (A)
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | 10 POE Load (A) | 0.0015674 | 0.0015535 | 0.0015572 | 0.0015593 | 0.0015634
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | Power Factor | 1 | 0.99999 | 1 | 1 | 1
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | NCC Rating (A) | 793 | 793 | 793 | 793 | 793 | Urban | 70
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | 10 POE Load (A) | 854.6278 | 901.3972 | 887.5116 | 881.4146 | 865.58
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | Power Factor | -0.00040931 | -0.00040954 | -0.00040842 | -0.00040902 | -0.00040831
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | ECC Rating (A) | 793 | 793 | 793 | 793 | 793
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | 50 POE Load (A)
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | 10 POE Load (A) | 854.8038 | 901.5834 | 887.6959 | 881.5968 | 865.7638
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | Power Factor | 0.91771 | 0.90747 | 0.90964 | 0.91161 | 0.95139
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | 50 POE Load (A)
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | 10 POE Load (A) | 454.825 | 447.023 | 440.1498 | 434.3927 | 429.9431
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | Power Factor | 0.97189 | 0.97255 | 0.97282 | 0.97318 | 0.97307
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | 50 POE Load (A) | 708.2284 | 697.1888 | 687.7403 | 679.0227 | 669.5351
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | 10 POE Load (A) | 189.8668 | 187.5122 | 183.6012 | 181.8125 | 178.3473
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | Power Factor | 0.94712 | 0.9475 | 0.94819 | 0.94862 | 0.94915
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | 50 POE Load (A) | 484.0697 | 476.4431 | 466.9848 | 463.1623 | 455.6047
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | 10 POE Load (A) | 278.7226 | 273.3871 | 271.389 | 266.3867 | 264.3939
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | Power Factor | 0.99299 | 0.99303 | 0.99301 | 0.99301 | 0.99294
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | 50 POE Load (A) | 235.7624 | 232.4198 | 229.4644 | 227.4718 | 224.525
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | NCC Rating (A) | 976 | 976 | 976 | 976 | 976 | Urban | 70
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | 10 POE Load (A) | 326.828 | 321.6603 | 316.2035 | 312.371 | 308.3749
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | Power Factor | 0.96126 | 0.96193 | 0.96258 | 0.96299 | 0.96349
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | 50 POE Load (A) | 481.9866 | 474.4406 | 465.0304 | 461.81 | 454.2851
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | 10 POE Load (A) | 326.8526 | 321.6847 | 316.2277 | 312.3951 | 308.3988
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | Power Factor | 0.9664 | 0.96716 | 0.96749 | 0.96793 | 0.96783
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | 50 POE Load (A) | 482.0125 | 474.4663 | 465.0559 | 461.8358 | 454.3107
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | 10 POE Load (A) | 0.00064374 | 0.00064374 | 0.00064375 | 0.00064375 | 0.00064375
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | Power Factor | 0.00030686 | 0.00030706 | 0.0003069 | 0.00030679 | 0.00030684
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | 10 POE Load (A) | 132.2676 | 128.9519 | 128.8765 | 125.8996 | 125.8298
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | Power Factor | 0.99618 | 0.99616 | 0.9961 | 0.99605 | 0.99595
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | 50 POE Load (A) | 115.7293 | 114.3476 | 113.324 | 111.4007 | 110.3788
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | 10 POE Load (A) | 132.2803 | 128.9641 | 128.8888 | 125.9117 | 125.8418
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | Power Factor | 0.9957 | 0.99568 | 0.99562 | 0.99558 | 0.99547
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | 50 POE Load (A) | 115.7413 | 114.3591 | 113.3354 | 111.412 | 110.3901
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | 10 POE Load (A) | 53.1149 | 51.777 | 51.7468 | 50.7387 | 50.7106
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | Power Factor | 1.5722e-05 | 1.5722e-05 | 1.5722e-05 | 1.5722e-05 | 1.5722e-05
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | 50 POE Load (A) | 48.1891 | 46.8336 | 45.8702 | 45.8397 | 44.8766
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | 10 POE Load (A) | 79.3002 | 77.2796 | 77.2653 | 75.2662 | 75.2245
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | Power Factor | 0.99527 | 0.99525 | 0.99519 | 0.99515 | 0.99505
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | 50 POE Load (A) | 67.702 | 67.6471 | 67.5983 | 65.6939 | 65.6343
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | NCC Rating (A) | 293 | 293 | 293 | 438 | 438 | Rural | 170
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | 10 POE Load (A) | 53.1149 | 51.777 | 51.7468 | 75.3915 | 75.3499
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | Power Factor | 0.99382 | 0.99381 | 0.99377 | 0.99374 | 0.99367
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | ECC Rating (A) | 438 | 438 | 438 | 438 | 438
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | 50 POE Load (A) | 67.7937 | 67.7375 | 67.7088 | 65.7827 | 65.7246
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | 10 POE Load (A) | 1.0179 | 1.0196 | 1.0201 | 1.0217 | 1.0222
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | Power Factor | 1.4326e-06 | 1.4325e-06 | 1.4325e-06 | 1.4326e-06 | 1.4325e-06
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | 50 POE Load (A)
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | NCC Rating (A) | 728 | 728 | 728 | 728 | 728 | Urban | 70
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | 10 POE Load (A) | 144.2724 | 141.6744 | 139.5597 | 138.2017 | 136.2965
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | Power Factor | 0.95522 | 0.95526 | 0.95602 | 0.95652 | 0.95656
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | ECC Rating (A) | 728 | 728 | 728 | 728 | 728
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | 50 POE Load (A) | 184.3576 | 181.069 | 178.5518 | 176.54 | 174.6056
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | NCC Rating (A) | 610 | 610 | 610 | 610 | 610 | Urban | 70
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | 10 POE Load (A) | 112.9672 | 111.6259 | 110.1246 | 109.2506 | 108.3629
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | Power Factor | 0.99728 | 0.99755 | 0.99774 | 0.99796 | 0.99806
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | ECC Rating (A) | 610 | 610 | 610 | 610 | 610
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | 50 POE Load (A) | 212.4845 | 209.8199 | 206.6979 | 204.9324 | 203.168
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | NCC Rating (A) | 610 | 610 | 610 | 610 | 610 | Urban | 70
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | 10 POE Load (A) | 224.5495 | 221.8793 | 218.8549 | 217.083 | 215.3119
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | Power Factor | 0.98884 | 0.9896 | 0.99002 | 0.99058 | 0.99088
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | ECC Rating (A) | 610 | 610 | 610 | 610 | 610
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | 50 POE Load (A)
Tennyson Bulk | 3460-1 | Annerley | Buranda | NCC Rating (A) | 802 | 802 | 802 | 802 | 802 | Urban | 70
Tennyson Bulk | 3460-1 | Annerley | Buranda | 10 POE Load (A) | 220.0931 | 236.3743 | 235.464 | 236.3743 | 236.3713
Tennyson Bulk | 3460-1 | Annerley | Buranda | Power Factor | 0.97516 | 0.97187 | 0.97074 | 0.97081 | 0.97121
Tennyson Bulk | 3460-1 | Annerley | Buranda | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 3460-1 | Annerley | Buranda | 50 POE Load (A) | 419.425 | 451.9818 | 450.1618 | 451.9818 | 450.1618
Tennyson Bulk | 3461-1 | Annerley | Buranda | NCC Rating (A) | 802 | 802 | 802 | 802 | 802 | Urban | 70
Tennyson Bulk | 3461-1 | Annerley | Buranda | 10 POE Load (A) | 220.4314 | 236.7376 | 235.8259 | 236.7376 | 236.7346
Tennyson Bulk | 3461-1 | Annerley | Buranda | Power Factor | 0.97517 | 0.97188 | 0.97075 | 0.97082 | 0.97123
Tennyson Bulk | 3461-1 | Annerley | Buranda | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 3461-1 | Annerley | Buranda | 50 POE Load (A) | 419.4232 | 451.9797 | 450.1597 | 451.9797 | 450.1597
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | NCC Rating (A) | 400 | 400 | 400 | 400 | 400 | Urban | 70
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | 10 POE Load (A) | 257.2236 | 252.9019 | 249.0441 | 247.2623 | 244.6003
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | Power Factor | 0.98108 | 0.98145 | 0.982 | 0.98237 | 0.98247
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | ECC Rating (A) | 451 | 451 | 451 | 451 | 451
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | 50 POE Load (A) | 385.4071 | 379.2853 | 374.7173 | 371.3619 | 368.4551
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | NCC Rating (A) | 763 | 763 | 763 | 763 | 763 | Urban | 70
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | 10 POE Load (A) | 432.5303 | 425.9119 | 419.7774 | 415.9099 | 411.2213
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | Power Factor | 0.96798 | 0.96831 | 0.96875 | 0.96906 | 0.96903
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | ECC Rating (A) | 763 | 763 | 763 | 763 | 763
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | 50 POE Load (A) | 537.3546 | 528.7877 | 522.0702 | 516.7284 | 511.3065
Tennyson Bulk | 480-1 | Taringa | St Lucia | NCC Rating (A) | 610 | 610 | 610 | 610 | 610 | Urban | 70
Tennyson Bulk | 480-1 | Taringa | St Lucia | 10 POE Load (A) | 109.1913 | 107.9333 | 106.5992 | 105.7472 | 104.9077
Tennyson Bulk | 480-1 | Taringa | St Lucia | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
Tennyson Bulk | 480-1 | Taringa | St Lucia | ECC Rating (A) | 610 | 610 | 610 | 610 | 610
Tennyson Bulk | 480-1 | Taringa | St Lucia | 50 POE Load (A) | 212.3223 | 209.6583 | 206.5913 | 204.8271 | 203.0641
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | NCC Rating (A) | 601 | 601 | 601 | 601 | 601 | Urban | 70
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | 10 POE Load (A) | 339.0028 | 334.0867 | 329.4324 | 326.806 | 323.6476
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | Power Factor | 0.98061 | 0.98108 | 0.98186 | 0.9821 | 0.98242
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | 50 POE Load (A) | 461.6651 | 454.6318 | 449.4468 | 445.3809 | 441.3945
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | 10 POE Load (A) | 147.4029 | 144.744 | 142.5792 | 141.1894 | 139.2395
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | Power Factor | 0.94929 | 0.94893 | 0.94957 | 0.94998 | 0.94999
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | ECC Rating (A) | 858 | 858 | 858 | 858 | 858
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | 50 POE Load (A) | 186.0628 | 182.7361 | 180.1865 | 178.1511 | 176.194
Tennyson Bulk | 507B-1 | Toowong | Taringa | NCC Rating (A) | 727 | 727 | 727 | 727 | 727 | Urban | 70
Tennyson Bulk | 507B-1 | Toowong | Taringa | 10 POE Load (A) | 145.3056 | 142.6981 | 140.4974 | 139.1169 | 137.1794
Tennyson Bulk | 507B-1 | Toowong | Taringa | Power Factor | 0.95976 | 0.9598 | 0.96053 | 0.961 | 0.96104
Tennyson Bulk | 507B-1 | Toowong | Taringa | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 507B-1 | Toowong | Taringa | 50 POE Load (A) | 184.0511 | 180.7412 | 178.1897 | 176.1633 | 174.2149
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | NCC Rating (A) | 739 | 739 | 739 | 739 | 739 | Urban | 70
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | 10 POE Load (A) | 167.8174 | 174.8276 | 174.8276 | 174.8276 | 173.1164
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | Power Factor | 0.96298 | 0.96239 | 0.96239 | 0.96239 | 0.96232
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | ECC Rating (A) | 753 | 753 | 753 | 753 | 753
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | 50 POE Load (A) | 298.0469 | 313.9197 | 313.9197 | 313.9197 | 312.1538
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | NCC Rating (A) | 739 | 739 | 739 | 739 | 739 | Urban | 70
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | 10 POE Load (A) | 168.79 | 175.841 | 175.841 | 175.841 | 174.1198
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | Power Factor | 0.96502 | 0.96487 | 0.96467 | 0.96449 | 0.96418
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | ECC Rating (A) | 753 | 753 | 753 | 753 | 753
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | 50 POE Load (A) | 298.0441 | 313.9166 | 313.9166 | 313.9166 | 312.1508
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | NCC Rating (A) | 740 | 740 | 740 | 740 | 740 | Urban | 70
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | 10 POE Load (A)
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | Power Factor | 0.97251 | 0.97281 | 0.97322 | 0.97351 | 0.97348
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | 50 POE Load (A) | 568.8137 | 559.7363 | 552.6259 | 546.9696 | 541.2289
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | 10 POE Load (A) | 7.7883 | 7.7883 | 7.7883 | 7.7883 | 7.7883
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | Power Factor | 1.0729e-05 | 1.0729e-05 | 1.0729e-05 | 1.0729e-05 | 1.0729e-05
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | 50 POE Load (A)
Tennyson Bulk | 539-1 | Sherwood | Kenmore | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 340
Tennyson Bulk | 539-1 | Sherwood | Kenmore | 10 POE Load (A) | 295.7568 | 290.6327 | 285.5757 | 282.2864 | 278.146
Tennyson Bulk | 539-1 | Sherwood | Kenmore | Power Factor | 0.97318 | 0.97334 | 0.97393 | 0.97426 | 0.97436
Tennyson Bulk | 539-1 | Sherwood | Kenmore | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Tennyson Bulk | 539-1 | Sherwood | Kenmore | 50 POE Load (A) | 604.2883 | 591.844 | 581.5336 | 575.365 | 567.1809
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | 10 POE Load (A) | 486.7302 | 479.284 | 472.3839 | 468.0323 | 462.7569
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | Power Factor | 0.96957 | 0.96988 | 0.97032 | 0.97062 | 0.97059
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | ECC Rating (A) | 716 | 716 | 716 | 716 | 716
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | 50 POE Load (A) | 590.3215 | 580.9158 | 573.5375 | 567.6711 | 561.7167
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | 10 POE Load (A) | 381.7949 | 375.1524 | 368.5186 | 364.0308 | 358.4602
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | Power Factor | 0.95692 | 0.95768 | 0.95843 | 0.95884 | 0.95896
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | 50 POE Load (A) | 593.6927 | 581.7988 | 571.9311 | 566.0189 | 558.1778
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | NCC Rating (A) | 601 | 601 | 601 | 601 | 601 | Urban | 70
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | 10 POE Load (A) | 340.5999 | 335.6606 | 330.9844 | 328.3456 | 325.1724
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | Power Factor | 0.98219 | 0.98234 | 0.9827 | 0.98298 | 0.98299
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | 50 POE Load (A) | 462.6745 | 455.6259 | 450.4298 | 446.355 | 442.3599
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | 10 POE Load (A) | 382.2049 | 398.4332 | 396.6456 | 398.4332 | 397.5497
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | Power Factor | 0.97776 | 0.97567 | 0.97486 | 0.97484 | 0.97489
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | 50 POE Load (A) | 682.03 | 714.7091 | 711.1194 | 714.7091 | 711.1194
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | 10 POE Load (A) | 383.5022 | 399.7857 | 397.992 | 399.7857 | 398.8992
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | Power Factor | 0.97775 | 0.97565 | 0.97485 | 0.97483 | 0.97488
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | 50 POE Load (A) | 682.0099 | 714.6867 | 711.0972 | 714.6867 | 711.0972
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | NCC Rating (A) | 400 | 400 | 400 | 400 | 400 | Urban | 70
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | 10 POE Load (A) | 259.9079 | 255.5411 | 251.6432 | 249.8428 | 247.153
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | Power Factor | 0.98116 | 0.98153 | 0.98208 | 0.98245 | 0.98255
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | ECC Rating (A) | 451 | 451 | 451 | 451 | 451
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | 50 POE Load (A) | 386.8454 | 380.7009 | 376.1162 | 372.7484 | 369.8309
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 415 | 415 | 415 | 415 | 415 | Urban | 70
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 0.15378 | 0.15378 | 0.15378 | 0.15378 | 0.15378
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | Power Factor | 0.96802 | 0.96802 | 0.96802 | 0.96802 | 0.96802
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A) | 0.16198 | 0.16198 | 0.16198 | 0.16198 | 0.16198
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 415 | 415 | 415 | 415 | 415 | Urban | 70
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 213.0374 | 211.3143 | 209.5918 | 208.7308 | 207.8699
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | Power Factor | 0.99213 | 0.99204 | 0.99204 | 0.99212 | 0.99196
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A) | 417.262 | 413.6126 | 409.9678 | 409.9678 | 408.1471
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 503 | 503 | 503 | 503 | 503 | Urban | 70
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | 10 POE Load (A) | 212.2026 | 209.5277 | 206.8553 | 205.075 | 202.4064
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | Power Factor | 0.98515 | 0.98524 | 0.98522 | 0.98521 | 0.98498
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | ECC Rating (A) | 585 | 585 | 585 | 585 | 585
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | 50 POE Load (A) | 389.6319 | 384.2901 | 380.7316 | 377.1752 | 373.8446
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 415 | 415 | 415 | 415 | 415 | Urban | 70
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 215.5901 | 213.8466 | 212.1038 | 211.2326 | 210.3615
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | Power Factor | 0.99227 | 0.99219 | 0.99218 | 0.99226 | 0.9921
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A) | 417.1019 | 413.4574 | 409.8175 | 409.8175 | 407.9991
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 503 | 503 | 503 | 503 | 503 | Urban | 70
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | 10 POE Load (A) | 212.2026 | 209.5277 | 206.8553 | 205.075 | 202.4065
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | Power Factor | 0.97161 | 0.9719 | 0.97219 | 0.97239 | 0.97267
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | ECC Rating (A) | 585 | 585 | 585 | 585 | 585
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | 50 POE Load (A) | 389.6319 | 384.2901 | 380.7316 | 377.1752 | 373.8446
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 538 | 538 | 538 | 538 | 538 | Urban | 70
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 9.2967 | 9.2967 | 9.2967 | 9.2967 | 9.2967
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | Power Factor | 1 | 1 | 1 | 1 | 1
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 538 | 538 | 538 | 538 | 538
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A)