## Notes
Sub-Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2022-23 to 2026-27)
This workbook provides 5 year forecast capacity and loading information for sub-transmission feeders in the Energex network.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation due to COVID 19 impacts. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
The following sections list the 33kV feeders, their forecast loads, power factor, customer category and available load transfers. The feeder loads are calculated from load flow results using forecast substation demands. For the transmission and sub-transmission feeders, load flow studies are conducted for system normal and single contingency situations.
The forecast and capacity cut-off date for the winter season is 1 June of each year, and for the summer season is 1 December of each year. For example, 2023 winter forecast includes all committed projects with a proposed commissioning date up to 1 June 2023, and the 2022/23 summer forecast includes all committed projects with a proposed commissioning date up to 1 December 2022.
Assessment of 33kV feeders is performed under four possible risk periods: winter day, winter night, summer day and summer night. For the winter table, the worst case (highest) load between winter day and winter night has been represented in the table.
Peak, reconciled, compensated load forecasts have been used in the 33kV feeder analyses, with 50 PoE forecast load used for single contingency studies, and 10 PoE forecast load used for system normal studies.
Feeder capacities are shown for ECC and NCC. These ratings have also been adjusted for known committed projects. All load transfers associated with contingent condition include acceptable feeder voltage profiles.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
Interconnected feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
Power Factor (System Normal) | Lowest power factor along the feeder at 10 PoE Peak Load. Where the Power Factor is either 0 the feeder is a normally open feeder that does not have load under System Normal conditions.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween winter day and winter night.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites. It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders to meet this criteria and 10MVA (170A) is available for Rural feeders. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.

## 33kV Feeders - Winter
Bulk Supply Name | Feeder | From Substation | To Substation | Attributes | 2023 | 2024 | 2025 | 2026 | 2027 | Security Standard | Transfers | Hours above 95%
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | NCC Rating (A) | 554 | 554 | 554 | 554 | 554 | Urban | 70
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | 10 POE Load (A) | 105.4483 | 104.7004 | 102.4687 | 102.4687 | 100.9751
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | Power Factor | 0.9989 | 0.99871 | 0.99884 | 0.99896 | 0.99899
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | ECC Rating (A) | 554 | 554 | 554 | 554 | 554
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | 50 POE Load (A) | 232.2736 | 230.4272 | 226.6342 | 227.8982 | 227.1338
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | 10 POE Load (A) | 0.19845 | 0.19846 | 0.19849 | 0.19849 | 0.1985
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | Power Factor | 1.4767e-05 | 1.4765e-05 | 1.4766e-05 | 1.4766e-05 | 1.4766e-05
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | 50 POE Load (A) | 166.2878 | 166.2752 | 189.5485 | 191.1812 | 191.1675
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | NCC Rating (A) | 840 | 840 | 840 | 840 | 840 | Urban | 70
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | 10 POE Load (A) | 105.6205 | 104.8695 | 102.6356 | 102.6356 | 101.1356
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | Power Factor | 0.9992 | 0.99907 | 0.99916 | 0.99925 | 0.99927
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | ECC Rating (A) | 917 | 917 | 917 | 917 | 917
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | 50 POE Load (A) | 232.5115 | 230.6612 | 225.1211 | 225.1211 | 223.2779
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | NCC Rating (A) | 525 | 525 | 525 | 525 | 525 | Rural | 170
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | 10 POE Load (A) | 0.82851 | 0.82851 | 0.82851 | 0.82851 | 0.82851
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | Power Factor | -6.9809e-06 | -6.981e-06 | -6.981e-06 | -6.981e-06 | -6.9806e-06
Abermain Bulk | 364-1 | Marburg | Rosewood | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Abermain Bulk | 364-1 | Marburg | Rosewood | 10 POE Load (A) | 51.1653 | 57.3139 | 69.0272 | 74.2215 | 74.4294
Abermain Bulk | 364-1 | Marburg | Rosewood | Power Factor | 0.99994 | 0.99995 | 0.99999 | 0.99888 | 0.99867
Abermain Bulk | 364-1 | Marburg | Rosewood | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Abermain Bulk | 364-1 | Marburg | Rosewood | 50 POE Load (A) | 93.27 | 103.1898 | 124.0735 | 135.7169 | 136.1098
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | 10 POE Load (A) | 236.9893 | 265.2451 | 311.2369 | 336.3307 | 341.0582
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | Power Factor | 0.97062 | 0.96928 | 0.96641 | 0.95762 | 0.95665
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | ECC Rating (A) | 944 | 944 | 944 | 944 | 944
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | 50 POE Load (A) | 451.8279 | 510.209 | 605.2652 | 660.0276 | 668.7384
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | 10 POE Load (A) | 0.0095971 | 0.0095615 | 0.0095024 | 0.0094678 | 0.0094619
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | Power Factor | 2.018e-05 | 2.018e-05 | 2.0181e-05 | 2.0181e-05 | 2.0182e-05
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | 10 POE Load (A) | 236.9893 | 265.2451 | 311.2369 | 336.3307 | 341.0674
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | Power Factor | 0.97101 | 0.96975 | 0.96695 | 0.95839 | 0.95749
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | 50 POE Load (A) | 451.8335 | 510.2149 | 605.2714 | 660.0339 | 668.7447
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | 10 POE Load (A) | 258.7187 | 289.5663 | 339.7773 | 367.1735 | 372.3347
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | Power Factor | 0.96129 | 0.95836 | 0.95376 | 0.93967 | 0.93708
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | 50 POE Load (A) | 455.6082 | 513.88 | 608.8536 | 663.1477 | 671.7833
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | 10 POE Load (A) | 258.7187 | 289.5663 | 339.7773 | 367.1735 | 372.3347
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | Power Factor | 0.97038 | 0.96934 | 0.96658 | 0.95766 | 0.95698
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | ECC Rating (A) | 845 | 845 | 845 | 845 | 845
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | 50 POE Load (A) | 455.6258 | 513.8984 | 608.873 | 663.1673 | 671.8029
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | 10 POE Load (A) | 0.021518 | 0.021443 | 0.021319 | 0.021246 | 0.021234
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | Power Factor | 9.0278e-06 | 9.0272e-06 | 9.0276e-06 | 9.0275e-06 | 9.0277e-06
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | NCC Rating (A) | 581 | 581 | 581 | 581 | 581 | Rural | 170
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | 10 POE Load (A) | 222.0032 | 222.0032 | 218.0079 | 116.7704 | 218.4714
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | Power Factor | 0.94995 | 0.95234 | 0.95234 | 0.95231 | 0.95233
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | ECC Rating (A) | 581 | 581 | 581 | 581 | 581
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | 50 POE Load (A) | 390.4747 | 388.5882 | 384.9012 | 183.724 | 382.271
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | NCC Rating (A) | 552 | 552 | 552 | 552 | 552 | HighSec | 0
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | 10 POE Load (A) | 177.4154 | 177.4154 | 174.2253 | 78.432 | 173.024
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | Power Factor | 0.94088 | 0.94231 | 0.9423 | 0.94224 | 0.94228
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | 50 POE Load (A) | 393.0976 | 391.2315 | 387.4874 | 184.7251 | 384.8256
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 548 | 548 | 548 | 548 | 548 | Urban | 70
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | 10 POE Load (A) | 146.0955 | 147.8337 | 147.8337 | 150.4427 | 152.1832
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | Power Factor | 0.98793 | 0.98794 | 0.98783 | 0.98779 | 0.98771
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | ECC Rating (A) | 548 | 548 | 548 | 548 | 548
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | 50 POE Load (A) | 275.4559 | 279.1186 | 279.1186 | 284.6232 | 286.4608
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | 10 POE Load (A) | 148.672 | 150.4408 | 150.4408 | 153.0959 | 154.8671
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | Power Factor | 0.98864 | 0.98864 | 0.98854 | 0.9885 | 0.98843
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | 50 POE Load (A) | 275.4011 | 279.0609 | 279.0609 | 284.5609 | 286.3969
Abermain Bulk | 387-1 | Abermain BS | Marburg | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170
Abermain Bulk | 387-1 | Abermain BS | Marburg | 10 POE Load (A) | 116.6839 | 130.3568 | 148.0322 | 160.8871 | 166.7666
Abermain Bulk | 387-1 | Abermain BS | Marburg | Power Factor | 0.99759 | 0.99753 | 0.99716 | 0.99577 | 0.99558
Abermain Bulk | 387-1 | Abermain BS | Marburg | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
Abermain Bulk | 387-1 | Abermain BS | Marburg | 50 POE Load (A) | 154.5274 | 172.0055 | 199.2256 | 217.0265 | 223.2324
Abermain Bulk | 3901-1 | Karrabin | Amberley | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 3901-1 | Karrabin | Amberley | 10 POE Load (A) | 117.997 | 144.6386 | 191.4181 | 214.7135 | 217.7988
Abermain Bulk | 3901-1 | Karrabin | Amberley | Power Factor | 0.95707 | 0.95522 | 0.952 | 0.94276 | 0.94389
Abermain Bulk | 3901-1 | Karrabin | Amberley | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Abermain Bulk | 3901-1 | Karrabin | Amberley | 50 POE Load (A) | 218.4865 | 270.0115 | 359.4516 | 405.8968 | 410.5464
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | HighSec | 0
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | 10 POE Load (A) | 34.103 | 33.2605 | 33.0294 | 77.3876 | 33.0302
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | Power Factor | 0.91432 | 0.88088 | 0.87675 | 0.85763 | 0.87045
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | 50 POE Load (A) | 205.1775 | 203.3076 | 201.4518 | 183.6351 | 198.8182
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | 10 POE Load (A) | 46.1037 | 46.6041 | 41.1604 | 42.9363 | 48.3388
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | Power Factor | 0.86833 | 0.85326 | 0.79073 | 0.77671 | 0.80228
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | 50 POE Load (A) | 155.9502 | 171.2876 | 183.8527 | 197.8367 | 208.8255
Abermain Bulk | 436-2 | 436 Tee1 | Ebeneezer | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Abermain Bulk | 436-2 | 436 Tee1 | Ebeneezer | 10 POE Load (A) | 0.17694 | 0.17594 | 0.17435 | 0.17336 | 0.17311
Abermain Bulk | 436-2 | 436 Tee1 | Ebeneezer | Power Factor | 5.5136e-06 | 5.5136e-06 | 5.5133e-06 | 5.5131e-06 | 5.5133e-06
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | 10 POE Load (A) | 46.461 | 46.9771 | 41.5939 | 43.3794 | 48.7578
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | Power Factor | 0.86399 | 0.84883 | 0.78434 | 0.77064 | 0.79765
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | 50 POE Load (A) | 156.0804 | 171.4199 | 183.9855 | 197.9714 | 208.9623
Abermain Bulk | 445-1 | Abermain BS | Moggill | NCC Rating (A) | 776 | 776 | 776 | 776 | 776 | Urban | 70
Abermain Bulk | 445-1 | Abermain BS | Moggill | 10 POE Load (A) | 143.0459 | 142.0301 | 139.0022 | 139.0022 | 136.9734
Abermain Bulk | 445-1 | Abermain BS | Moggill | Power Factor | 0.99803 | 0.99783 | 0.99797 | 0.9981 | 0.99813
Abermain Bulk | 445-1 | Abermain BS | Moggill | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Abermain Bulk | 445-1 | Abermain BS | Moggill | 50 POE Load (A) | 230.1151 | 228.311 | 222.9059 | 222.9059 | 221.1066
Abermain Bulk | 475-1 | Karrabin | Amberley | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 475-1 | Karrabin | Amberley | 10 POE Load (A) | 116.273 | 142.5217 | 188.6106 | 211.5617 | 214.5817
Abermain Bulk | 475-1 | Karrabin | Amberley | Power Factor | 0.9578 | 0.95597 | 0.95278 | 0.94361 | 0.94473
Abermain Bulk | 475-1 | Karrabin | Amberley | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Abermain Bulk | 475-1 | Karrabin | Amberley | 50 POE Load (A) | 218.2637 | 269.762 | 359.1669 | 405.5816 | 410.254
Abermain Bulk | 673-1 | Moggill | Kenmore | NCC Rating (A) | 1016 | 1016 | 1016 | 1016 | 1016 | Urban | 70
Abermain Bulk | 673-1 | Moggill | Kenmore | 10 POE Load (A) | 3.4782 | 3.4786 | 3.4796 | 3.4796 | 3.4801
Abermain Bulk | 673-1 | Moggill | Kenmore | Power Factor | 2.3519e-06 | 2.3519e-06 | 2.3519e-06 | 2.3519e-06 | 2.3519e-06
Abermain Bulk | 673-1 | Moggill | Kenmore | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Abermain Bulk | 673-1 | Moggill | Kenmore | 50 POE Load (A)
Algester Bulk | 3400-1 | Algester BS | Calamvale | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70
Algester Bulk | 3400-1 | Algester BS | Calamvale | 10 POE Load (A) | 251.9996 | 251.9996 | 248.4753 | 249.3561 | 248.4753
Algester Bulk | 3400-1 | Algester BS | Calamvale | Power Factor | 0.99439 | 0.99451 | 0.99446 | 0.9945 | 0.99439
Algester Bulk | 3400-1 | Algester BS | Calamvale | ECC Rating (A) | 810 | 810 | 810 | 810 | 810
Algester Bulk | 3400-1 | Algester BS | Calamvale | 50 POE Load (A) | 475.5701 | 475.5701 | 470.2656 | 472.0333 | 470.2656
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 728 | 728 | 728 | 728 | 728 | Urban | 70
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | 10 POE Load (A) | 150.4304 | 148.2766 | 146.5477 | 147.4121 | 147.4121
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | Power Factor | 0.93503 | 0.99 | 0.99369 | 0.99405 | 0.99408
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | ECC Rating (A) | 782 | 782 | 782 | 782 | 782
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | 50 POE Load (A) | 285.75 | 293.7459 | 292.0121 | 293.7459 | 293.7459
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 728 | 728 | 728 | 728 | 728 | Urban | 70
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | 10 POE Load (A) | 150.8584 | 148.7026 | 146.9686 | 147.8355 | 147.8355
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | Power Factor | 0.93506 | 0.99 | 0.9937 | 0.99406 | 0.99409
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | ECC Rating (A) | 782 | 782 | 782 | 782 | 782
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | 50 POE Load (A) | 285.7475 | 293.7443 | 292.0105 | 293.7443 | 293.7443
Algester Bulk | 3405-1 | Algester BS | Calamvale | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70
Algester Bulk | 3405-1 | Algester BS | Calamvale | 10 POE Load (A) | 252.2897 | 252.2897 | 248.7613 | 249.6431 | 248.7613
Algester Bulk | 3405-1 | Algester BS | Calamvale | Power Factor | 0.99438 | 0.99451 | 0.99445 | 0.9945 | 0.99439
Algester Bulk | 3405-1 | Algester BS | Calamvale | ECC Rating (A) | 810 | 810 | 810 | 810 | 810
Algester Bulk | 3405-1 | Algester BS | Calamvale | 50 POE Load (A) | 475.5678 | 475.5678 | 470.2633 | 472.031 | 470.2633
Archerfield Bulk | 597-1 | Rocklea | Salisbury | NCC Rating (A) | 710 | 710 | 710 | 710 | 710 | Urban | 70
Archerfield Bulk | 597-1 | Rocklea | Salisbury | 10 POE Load (A) | 174.9583 | 174.9583 | 172.9084 | 172.9099 | 172.9099
Archerfield Bulk | 597-1 | Rocklea | Salisbury | Power Factor | 0.98506 | 0.98583 | 0.98616 | 0.98603 | 0.98618
Archerfield Bulk | 597-1 | Rocklea | Salisbury | ECC Rating (A) | 710 | 710 | 710 | 710 | 710
Archerfield Bulk | 597-1 | Rocklea | Salisbury | 50 POE Load (A) | 160.8338 | 160.8365 | 157.5328 | 157.5328 | 157.5355
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | NCC Rating (A) | 573 | 573 | 573 | 573 | 573 | Urban | 70
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | 10 POE Load (A) | 296.8321 | 316.1534 | 312.6247 | 314.3888 | 314.3888
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | Power Factor | 0.99792 | 0.93969 | 0.9399 | 0.9403 | 0.94052
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | ECC Rating (A) | 573 | 573 | 573 | 573 | 573
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | 50 POE Load (A)
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | 10 POE Load (A) | 217.775 | 218.6576 | 216.0014 | 216.8837 | 216.8837
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | Power Factor | 0.98199 | 0.98266 | 0.98285 | 0.98299 | 0.98313
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | ECC Rating (A) | 784 | 784 | 784 | 784 | 784
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | 50 POE Load (A) | 412.5836 | 414.3428 | 407.2832 | 409.0417 | 409.0417
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | 10 POE Load (A) | 215.2793 | 216.1517 | 213.526 | 214.3982 | 214.3982
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | Power Factor | 0.98205 | 0.98272 | 0.98291 | 0.98306 | 0.98319
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | ECC Rating (A) | 784 | 784 | 784 | 784 | 784
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | 50 POE Load (A) | 412.5997 | 414.359 | 407.2988 | 409.0575 | 409.0575
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | NCC Rating (A) | 516 | 516 | 516 | 516 | 516 | Urban | 70
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | 10 POE Load (A) | 13.6173 | 13.6173 | 13.6173 | 13.6173 | 13.6173
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | Power Factor | 4.2657e-05 | 4.2657e-05 | 4.2657e-05 | 4.2657e-05 | 4.2657e-05
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | ECC Rating (A) | 516 | 516 | 516 | 516 | 516
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | 50 POE Load (A)
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 598 | 598 | 598 | 598 | 598 | Urban | 70
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | 10 POE Load (A) | 133.5107 | 133.5107 | 131.5783 | 132.2223 | 131.5783
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | Power Factor | 0.99996 | 0.99995 | 0.99995 | 0.99994 | 0.99996
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | ECC Rating (A) | 634 | 634 | 634 | 634 | 634
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | 50 POE Load (A) | 193.6818 | 193.6818 | 191.6553 | 191.6553 | 190.6425
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 851 | 851 | 851 | 851 | 851 | Urban | 70
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | 10 POE Load (A) | 92.2206 | 92.2206 | 90.8882 | 91.3322 | 90.8882
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | Power Factor | 0.99997 | 0.99998 | 0.99998 | 0.99999 | 0.99997
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | ECC Rating (A) | 882 | 882 | 882 | 882 | 882
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | 50 POE Load (A) | 135.4039 | 135.4039 | 133.9883 | 133.9883 | 133.2808
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 634 | 634 | 634 | 634 | 634 | Urban | 70
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | 10 POE Load (A) | 130.6063 | 130.6063 | 128.7393 | 129.3614 | 128.7393
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | Power Factor | 0.99866 | 0.99856 | 0.99861 | 0.99856 | 0.99868
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | ECC Rating (A) | 712 | 712 | 712 | 712 | 712
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | 50 POE Load (A) | 192.2111 | 192.2111 | 190.2187 | 190.2187 | 189.223
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | 10 POE Load (A) | 135.8182 | 135.8182 | 134.0954 | 134.0954 | 133.2342
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | Power Factor | 1 | 0.99999 | 0.99999 | 0.99998 | 0.99998
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | ECC Rating (A) | 659 | 659 | 659 | 659 | 659
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | 50 POE Load (A)
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | 10 POE Load (A) | 135.8698 | 135.8698 | 134.1447 | 134.1447 | 133.2823
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | Power Factor | 1 | 1 | 1 | 1 | 1
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | ECC Rating (A) | 659 | 659 | 659 | 659 | 659
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | 50 POE Load (A)
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | 10 POE Load (A) | 259.2961 | 260.2124 | 258.4481 | 260.2124 | 260.2124
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | Power Factor | 0.98652 | 0.98664 | 0.98662 | 0.98668 | 0.98665
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | 50 POE Load (A) | 501.0396 | 502.8133 | 499.2665 | 502.8133 | 502.8133
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | 10 POE Load (A) | 259.2144 | 260.1329 | 258.3692 | 260.1329 | 260.1329
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | Power Factor | 0.98647 | 0.9866 | 0.98658 | 0.98664 | 0.9866
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | 50 POE Load (A) | 501.039 | 502.8127 | 499.2659 | 502.8127 | 502.8127
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | 10 POE Load (A) | 17.2016 | 17.2016 | 17.2019 | 17.2018 | 17.2019
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | Power Factor | 3.5471e-05 | 3.5471e-05 | 3.5471e-05 | 3.5471e-05 | 3.5471e-05
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | 50 POE Load (A)
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | NCC Rating (A) | 492 | 492 | 492 | 492 | 492 | Urban | 70
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | 10 POE Load (A) | 17.0752 | 17.0752 | 17.0755 | 17.0754 | 17.0755
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | Power Factor | 3.5079e-05 | 3.5079e-05 | 3.5079e-05 | 3.5079e-05 | 3.5079e-05
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | 50 POE Load (A)
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | 10 POE Load (A) | 1.3762 | 1.3762 | 1.3762 | 1.3762 | 1.3762
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | Power Factor | 0.00013446 | 0.00013446 | 0.00013446 | 0.00013446 | 0.00013446
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | 50 POE Load (A)
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | 10 POE Load (A) | 70.517 | 70.5363 | 70.5436 | 72.5086 | 72.5255
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | Power Factor | 0.98942 | 0.98923 | 0.98888 | 0.9887 | 0.98858
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | 50 POE Load (A) | 67.5263 | 69.5304 | 69.5377 | 69.59 | 69.616
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | 10 POE Load (A) | 82.5964 | 90.9231 | 103.4348 | 111.8445 | 112.8889
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | Power Factor | 0.99637 | 0.99482 | 0.99184 | 0.98892 | 0.9874
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | 50 POE Load (A) | 134.9212 | 148.9401 | 169.9843 | 184.1715 | 185.9325
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | 10 POE Load (A) | 55.6028 | 61.2125 | 69.6399 | 75.3047 | 76.008
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | Power Factor | 0.99919 | 0.99968 | 1 | 0.9997 | 0.99936
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | 50 POE Load (A) | 135.9847 | 150.2685 | 171.7698 | 186.3091 | 188.114
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | 10 POE Load (A) | 249.4055 | 254.0001 | 255.7118 | 262.4167 | 266.0981
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | Power Factor | 0.96245 | 0.9624 | 0.96173 | 0.96126 | 0.96055
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | 50 POE Load (A) | 325.8801 | 332.729 | 333.3325 | 340.3399 | 343.1299
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Rural | 170
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | 10 POE Load (A) | 257.1213 | 261.8308 | 263.5355 | 270.3949 | 274.1409
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | Power Factor | 0.98466 | 0.98463 | 0.98417 | 0.98386 | 0.98337
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | 50 POE Load (A) | 479.0572 | 492.5909 | 494.2355 | 505.8273 | 511.5245
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | 10 POE Load (A) | 67.3779 | 71.0356 | 73.7836 | 78.2188 | 81.8372
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | Power Factor | 0.98122 | 0.98113 | 0.98052 | 0.98006 | 0.97946
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | 50 POE Load (A) | 302.3645 | 313.6837 | 317.3714 | 326.766 | 332.3977
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | 10 POE Load (A) | 190.8418 | 192.8286 | 190.7814 | 192.9404 | 192.9895
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | Power Factor | 0.99613 | 0.99616 | 0.99615 | 0.99616 | 0.99613
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | 50 POE Load (A) | 363.2933 | 366.011 | 363.509 | 368.7363 | 368.821
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | NCC Rating (A) | 810 | 810 | 810 | 810 | 810 | Urban | 70
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | 10 POE Load (A) | 264.7602 | 265.0712 | 267.7191 | 268.8477 | 269.1587
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | Power Factor | 0.99103 | 0.99118 | 0.99121 | 0.99128 | 0.99129
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | ECC Rating (A) | 810 | 810 | 810 | 810 | 810
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | 50 POE Load (A) | 448.1524 | 448.1322 | 455.4526 | 457.2505 | 455.4282
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | NCC Rating (A) | 868 | 859 | 868 | 868 | 868 | Urban | 70
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | 10 POE Load (A) | 29.6187 | 30.7103 | 25.8976 | 26.5029 | 27.2817
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | Power Factor | 0.90212 | 0.90047 | 0.90029 | 0.89906 | 0.89668
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | 50 POE Load (A) | 288.1527 | 289.9426 | 286.5577 | 288.4665 | 288.3476
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | NCC Rating (A) | [5 empty] | Rural | 170
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | 10 POE Load (A)
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | Power Factor | 0.98179 | 0.98194 | 0.98198 | 0.9821 | 0.98207
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | 50 POE Load (A)
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | 10 POE Load (A) | 74.7631 | 78.1394 | 76.4506 | 77.2948 | 77.2948
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | Power Factor | 0.98029 | 0.98045 | 0.9805 | 0.98064 | 0.9806
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | 50 POE Load (A) | 146.92 | 152.161 | 150.4129 | 152.161 | 152.161
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | 10 POE Load (A) | 1.4196 | 1.4196 | 1.4196 | 1.4196 | 1.4196
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | Power Factor | 0.00010523 | 0.00010523 | 0.00010523 | 0.00010523 | 0.00010523
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | 50 POE Load (A) | 236.8556 | 248.3155 | 254.1813 | 267.9902 | 277.9628
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Urban | 70
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | 10 POE Load (A) | 234.0547 | 236.2 | 232.058 | 236.2002 | 236.3482
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | Power Factor | 0.99144 | 0.9915 | 0.99145 | 0.99146 | 0.99137
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | 50 POE Load (A) | 453.595 | 456.8565 | 450.9763 | 457.4566 | 457.4566
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | NCC Rating (A) | 469 | 469 | 469 | 469 | 469 | Urban | 70
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | 10 POE Load (A) | 65.1862 | 65.2427 | 63.3183 | 65.2427 | 63.428
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | Power Factor | 0.9902 | 0.99024 | 0.99018 | 0.99017 | 0.99008
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | ECC Rating (A) | 469 | 469 | 469 | 469 | 469
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | 50 POE Load (A) | 67.6313 | 67.7507 | 65.5517 | 65.78 | 65.78
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | NCC Rating (A) | 812 | 812 | 812 | 812 | 812 | Urban | 70
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | 10 POE Load (A) | 169.0694 | 171.1629 | 168.9417 | 171.1631 | 173.1316
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | Power Factor | 0.99609 | 0.99612 | 0.99611 | 0.99611 | 0.99609
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | ECC Rating (A) | 812 | 812 | 812 | 812 | 812
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | 50 POE Load (A) | 386.5246 | 389.6795 | 385.9803 | 392.2562 | 392.2562
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | NCC Rating (A) | 868 | 868 | 868 | 868 | 868 | Urban | 70
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | 10 POE Load (A) | 192.8931 | 192.5821 | 196.9529 | 197.5769 | 197.263
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | Power Factor | 0.98853 | 0.98875 | 0.98879 | 0.9889 | 0.9889
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | ECC Rating (A) | 988 | 988 | 988 | 988 | 988
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | 50 POE Load (A) | 453.1469 | 453.1797 | 460.4568 | 462.397 | 460.4861
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | NCC Rating (A) | 820 | 820 | 820 | 820 | 820 | Urban | 70
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | 10 POE Load (A) | 193.0433 | 192.7323 | 197.105 | 197.7294 | 197.4153
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | Power Factor | 0.98997 | 0.99016 | 0.99019 | 0.99028 | 0.99028
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | 50 POE Load (A) | 453.3018 | 453.3347 | 460.6129 | 462.5546 | 460.6423
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | NCC Rating (A) | 892 | 892 | 892 | 892 | 892 | Urban | 70
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | 10 POE Load (A) | 0.93457 | 0.93454 | 0.93444 | 0.93437 | 0.93442
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | Power Factor | -2.6738e-06 | -2.6755e-06 | -2.6742e-06 | -2.6747e-06 | -2.6755e-06
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | ECC Rating (A) | 896 | 896 | 896 | 896 | 896
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | 50 POE Load (A) | 227.9918 | 227.9968 | 224.5484 | 224.566 | 222.7903
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | NCC Rating (A) | 785 | 785 | 785 | 785 | 785 | Rural | 170
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | 10 POE Load (A) | 77.8062 | 81.3261 | 79.5654 | 80.4456 | 80.4456
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | Power Factor | 0.99898 | 0.99898 | 0.99898 | 0.99898 | 0.99898
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | 50 POE Load (A) | 146.6031 | 151.8364 | 150.0909 | 151.8364 | 151.8364
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | NCC Rating (A) | 785 | 785 | 785 | 785 | 785 | Rural | 170
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | 10 POE Load (A) | 74.5304 | 77.902 | 76.2155 | 77.0586 | 77.0586
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | Power Factor | 0.98101 | 0.98121 | 0.98126 | 0.98144 | 0.98139
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | 50 POE Load (A) | 146.6804 | 151.9181 | 150.1712 | 151.9181 | 151.9181
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | 10 POE Load (A) | 561.0706 | 566.3406 | 561.0459 | 568.0654 | 569.8153
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | Power Factor | 0.99333 | 0.99331 | 0.99317 | 0.99311 | 0.99293
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | 50 POE Load (A) | 551 | 562 | 556 | 561 | 560
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | 10 POE Load (A) | 289.9592 | 291.7443 | 288.2146 | 290.0122 | 290.0255
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | Power Factor | 0.99477 | 0.99514 | 0.99505 | 0.99501 | 0.99486
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | 50 POE Load (A) | 278.6348 | 282.6214 | 280.5103 | 284.5469 | 286.5827
Beerwah Bulk | 324-1 | Woodford | Kilcoy | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Rural | 170
Beerwah Bulk | 324-1 | Woodford | Kilcoy | 10 POE Load (A) | 205.1734 | 200.4431 | 198.0455 | 62.7364 | 62.7364
Beerwah Bulk | 324-1 | Woodford | Kilcoy | Power Factor | 0.99111 | 0.98874 | 0.98821 | 0.98819 | 0.98774
Beerwah Bulk | 324-1 | Woodford | Kilcoy | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
Beerwah Bulk | 324-1 | Woodford | Kilcoy | 50 POE Load (A) | 195.7234 | 191.3063 | 188.9612
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | 10 POE Load (A) | 225.9592 | 218.7844 | 215.861 | 191.4534 | 191.4534
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | Power Factor | 0.9639 | 0.95959 | 0.95799 | 0.95794 | 0.95658
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | 50 POE Load (A) | 214.285 | 207.7094 | 204.8882 | 182.715 | 182.715
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | NCC Rating (A) | 290 | 290 | 290 |  |  | Rural | 170
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | 10 POE Load (A) | 1.2182 | 1.2113 | 1.216
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | Power Factor | 0.00025447 | 0.00025447 | 0.00025447 | 0.00025447 | 0.00025447
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | 50 POE Load (A)
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | 10 POE Load (A) | 1.5709 | 1.5709 | 1.5715 | 1.5709 | 1.5709
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | Power Factor | 0.00031257 | 0.00031257 | 0.00031257 | 0.00031257 | 0.00031257
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | 50 POE Load (A)
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | NCC Rating (A) | 381 | 381 | 381 | 381 | 381 | Rural | 170
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | 10 POE Load (A) | 156.9752 | 156.9752 | 155.0033 | 156.9752 | 156.9752
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | Power Factor | 0.99262 | 0.99277 | 0.99275 | 0.9928 | 0.99273
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | ECC Rating (A) | 381 | 381 | 381 | 381 | 381
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | 50 POE Load (A)
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | 10 POE Load (A) | 156.6789 | 156.6789 | 154.7094 | 156.6789 | 156.6789
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | Power Factor | 0.98689 | 0.9873 | 0.98726 | 0.98741 | 0.98721
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | 50 POE Load (A)
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | 10 POE Load (A) | 216.6701 | 234.9841 | 233.154 | 236.816 | 236.816
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | Power Factor | 0.99179 | 0.99172 | 0.98992 | 0.98932 | 0.98843
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | 50 POE Load (A) | 202 | 219 | 226 | 232 | 232
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | 10 POE Load (A) | 33.824 | 33.824 | 33.288 | 33.3754 | 33.3754
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | Power Factor | 0.82259 | 0.81072 | 0.80261 | 0.79426 | 0.78154
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | ECC Rating (A) | 818 | 818 | 631 | 631 | 631
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | 50 POE Load (A) | 94.287 | 94.0839 | 93.6589 | 93.4558 | 93.4558
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | [5 empty] | Urban | 70
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | 10 POE Load (A)
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | Power Factor
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | ECC Rating (A) | 494 | 494 | 494 | 494 | 494
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | 50 POE Load (A)
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | [5 empty] | Urban | 70
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | 10 POE Load (A)
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | Power Factor
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | ECC Rating (A) | 481 | 481 | 481 | 481 | 481
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | 50 POE Load (A)
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | NCC Rating (A) | 566 | 566 | 566 | 566 | 566 | Urban | 260
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | 10 POE Load (A) | 213.2456 | 215.0652 | 308.0832 | 309.9967 | 309.9967
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | Power Factor | 0.99905 | 0.99944 | 0.99742 | 0.99744 | 0.99734
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | ECC Rating (A) | 602 | 602 | 602 | 602 | 602
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | 50 POE Load (A) | 411.3649 | 415.4773 | 419.5897 | 423.702 | 427.8144
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | 10 POE Load (A) | 191.6759 | 191.6759 | 189.0685 | 189.0685 | 188.1997
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | Power Factor | 0.98896 | 0.98925 | 0.98937 | 0.9895 | 0.98958
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | ECC Rating (A) | 795 | 795 | 795 | 795 | 795
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | 50 POE Load (A) | 360.2332 | 360.2332 | 354.9737 | 356.7265 | 354.9737
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | 10 POE Load (A) | 193.7244 | 193.7244 | 191.0892 | 191.0892 | 190.2111
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | Power Factor | 0.98896 | 0.98925 | 0.98937 | 0.9895 | 0.98958
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | ECC Rating (A) | 795 | 795 | 795 | 795 | 795
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | 50 POE Load (A) | 360.2109 | 360.2109 | 354.9522 | 356.7047 | 354.9522
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Urban | 70
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | 10 POE Load (A) | 142.4386 | 143.1754 | 141.5525 | 142.4386 | 142.4386
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | Power Factor | 0.98929 | 0.98955 | 0.98947 | 0.98958 | 0.98942
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | 50 POE Load (A) | 208.5572 | 208.7844 | 206.5421 | 207.8904 | 207.8904
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Urban | 70
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | 10 POE Load (A) | 144.1126 | 144.8582 | 143.216 | 144.1126 | 144.1126
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | Power Factor | 0.9891 | 0.98937 | 0.98929 | 0.9894 | 0.98924
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | 50 POE Load (A) | 209.7418 | 209.9703 | 207.7152 | 209.0712 | 209.0712
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 447 | 447 | 447 | 447 | 447 | Urban | 70
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | 10 POE Load (A) | 156.238 | 156.238 | 154.4892 | 155.3635 | 155.3635
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | Power Factor | 0.97997 | 0.98026 | 0.98023 | 0.98027 | 0.98015
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | ECC Rating (A) | 494 | 494 | 494 | 494 | 494
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | 50 POE Load (A) | 284.6661 | 286.4245 | 282.9082 | 284.6661 | 284.6661
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 447 | 447 | 447 | 447 | 447 | Urban | 70
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | 10 POE Load (A) | 157.5286 | 157.5286 | 155.7651 | 156.6467 | 156.6467
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | Power Factor | 0.98024 | 0.98055 | 0.98052 | 0.98056 | 0.98044
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | ECC Rating (A) | 494 | 494 | 494 | 494 | 494
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | 50 POE Load (A) | 284.6554 | 286.4136 | 282.8976 | 284.6554 | 284.6554
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | NCC Rating (A) | 788 | 788 | 788 | 788 | 788 | Urban | 70
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | 10 POE Load (A) | 168.9578 | 168.9578 | 165.542 | 165.542 | 164.6883
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | Power Factor | 0.9974 | 0.99755 | 0.99755 | 0.9976 | 0.99755
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | ECC Rating (A) | 902 | 902 | 902 | 902 | 902
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | 50 POE Load (A) | 320.4627 | 318.6723 | 313.3068 | 313.3068 | 311.5202
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | NCC Rating (A) | 810 | 810 | 810 | 810 | 810 | Rural | 170
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | 10 POE Load (A) | 225.7795 | 225.1957 | 221.7586 | 222.3258 | 221.7586
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | Power Factor | 0.99361 | 0.99374 | 0.99371 | 0.99376 | 0.99368
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | ECC Rating (A) | 894 | 894 | 894 | 894 | 894
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | 50 POE Load (A) | 433.0251 | 433.0251 | 427.1387 | 427.1387 | 426.2354
Brendale Bulk | 309-2 | 309 Tee1 | Samford | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Brendale Bulk | 309-2 | 309 Tee1 | Samford | 10 POE Load (A) | 68.3796 | 67.4181 | 66.343 | 66.1368 | 66.343
Brendale Bulk | 309-2 | 309 Tee1 | Samford | Power Factor | 0.99978 | 0.99985 | 0.99988 | 0.99989 | 0.99991
Brendale Bulk | 309-2 | 309 Tee1 | Samford | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Brendale Bulk | 309-2 | 309 Tee1 | Samford | 50 POE Load (A) | 218.0401 | 218.0401 | 214.322 | 214.322 | 212.492
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | NCC Rating (A) | 838 | 838 | 838 | 838 | 838 | Rural | 170
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | 10 POE Load (A) | 158.2499 | 158.6378 | 156.2472 | 157.0381 | 156.2472
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | Power Factor | 0.98914 | 0.98933 | 0.9893 | 0.98937 | 0.98927
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | 50 POE Load (A) | 458.6903 | 458.6903 | 452.9578 | 452.9578 | 452.9141
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | 10 POE Load (A) | 331.6896 | 331.283 | 326.2459 | 327.3013 | 326.2459
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | Power Factor | 0.99338 | 0.99351 | 0.99348 | 0.99353 | 0.99345
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | ECC Rating (A) | 894 | 894 | 894 | 894 | 894
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | 50 POE Load (A) | 448.2049 | 448.2049 | 442.5142 | 442.5142 | 442.5142
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | NCC Rating (A) | 838 | 838 | 838 | 838 | 838 | Urban | 70
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | 10 POE Load (A) | 331.7355 | 331.329 | 326.2911 | 327.3467 | 326.2911
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | Power Factor | 0.9943 | 0.9944 | 0.99437 | 0.99442 | 0.99435
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | 50 POE Load (A) | 448.2534 | 448.2534 | 442.562 | 442.562 | 442.562
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | 10 POE Load (A) | 0.11243 | 0.11243 | 0.11246 | 0.11245 | 0.11246
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | Power Factor | 2.0842e-06 | 2.0842e-06 | 2.0842e-06 | 2.0842e-06 | 2.0842e-06
Brendale Bulk | 333-1 | Brendale BS | Lawnton | NCC Rating (A) | 826 | 826 | 826 | 826 | 826 | Urban | 70
Brendale Bulk | 333-1 | Brendale BS | Lawnton | 10 POE Load (A) | 256.1971 | 265.584 | 270.8926 | 273.7945 | 275.9732
Brendale Bulk | 333-1 | Brendale BS | Lawnton | Power Factor | 0.98412 | 0.98441 | 0.98423 | 0.98433 | 0.98432
Brendale Bulk | 333-1 | Brendale BS | Lawnton | ECC Rating (A) | 846 | 846 | 846 | 846 | 846
Brendale Bulk | 333-1 | Brendale BS | Lawnton | 50 POE Load (A) | 427.4248 | 444.0417 | 452.9925 | 458.2074 | 460.8181
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | NCC Rating (A) | 561 | 561 | 561 | 561 | 561 | Urban | 70
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | 10 POE Load (A) | 104.0048 | 104.0048 | 102.881 | 103.4429 | 104.0048
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | Power Factor | 0.99367 | 0.99427 | 0.99445 | 0.99524 | 0.99557
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | ECC Rating (A) | 561 | 561 | 561 | 561 | 561
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | 50 POE Load (A) | 162.7793 | 162.7793 | 160.9885 | 161.8838 | 162.7793
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | NCC Rating (A) | 645 | 645 | 645 | 645 | 645 | Rural | 170
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | 10 POE Load (A) | 50.005 | 47.836 | 45.5259 | 44.9172 | 43.8964
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | Power Factor | 0.70385 | 0.79359 | 0.93476 | 0.94535 | 0.95377
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | ECC Rating (A) | 865 | 865 | 865 | 865 | 865
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | 50 POE Load (A) | 200.734 | 200.9166 | 197.29 | 197.3482 | 197.3774
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | NCC Rating (A) | 860 | 860 | 860 | 860 | 860 | Rural | 170
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | 10 POE Load (A) | 60.1661 | 59.8217 | 58.786 | 58.7008 | 58.6368
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | Power Factor | 0.9475 | 0.94838 | 0.94859 | 0.94891 | 0.94894
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | ECC Rating (A) | 949 | 949 | 949 | 949 | 949
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | 50 POE Load (A) | 128.734 | 128.8485 | 126.9906 | 127.0286 | 127.0476
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | NCC Rating (A) | 645 | 645 | 645 | 645 | 645 | Rural | 170
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | 10 POE Load (A) | 46.9333 | 50.3154 | 52.4756 | 53.5383 | 54.3385
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | Power Factor | 0.99765 | 0.99758 | 0.99668 | 0.99663 | 0.99649
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | ECC Rating (A) | 865 | 865 | 865 | 865 | 865
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | 50 POE Load (A) | 114.0902 | 120.7174 | 125.4745 | 127.5414 | 128.5763
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | NCC Rating (A) | 531 | 531 | 531 | 531 | 531 | Rural | 170
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | 10 POE Load (A) | 180.7886 | 184.9645 | 186.6994 | 187.9912 | 188.9613
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | Power Factor | 0.96772 | 0.96838 | 0.96761 | 0.96784 | 0.96815
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | ECC Rating (A) | 531 | 531 | 531 | 531 | 531
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | 50 POE Load (A) | 254.8817 | 262.2584 | 265.046 | 267.3682 | 268.5308
Brendale Bulk | 335-2 | 335 Tee | Whiteside | NCC Rating (A) | 860 | 860 | 860 | 860 | 860 | Rural | 170
Brendale Bulk | 335-2 | 335 Tee | Whiteside | 10 POE Load (A) | 71.1949 | 71.5371 | 70.8459 | 70.9518 | 71.0314
Brendale Bulk | 335-2 | 335 Tee | Whiteside | Power Factor | 0.95649 | 0.95726 | 0.95751 | 0.9578 | 0.95799
Brendale Bulk | 335-2 | 335 Tee | Whiteside | ECC Rating (A) | 949 | 949 | 949 | 949 | 949
Brendale Bulk | 335-2 | 335 Tee | Whiteside | 50 POE Load (A) | 127.3211 | 127.3211 | 125.4009 | 125.4009 | 125.4009
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | NCC Rating (A) | 531 | 531 | 531 | 531 | 531 | Rural | 170
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | 10 POE Load (A) | 110.078 | 113.9112 | 116.3355 | 117.5214 | 118.4119
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | Power Factor | 0.9845 | 0.98444 | 0.98286 | 0.98283 | 0.98306
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | ECC Rating (A) | 531 | 531 | 531 | 531 | 531
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | 50 POE Load (A) | 180.6527 | 187.4288 | 190.7624 | 192.8942 | 193.9614
Brendale Bulk | 336-1 | Brendale BS | Strathpine | NCC Rating (A) | 515 | 515 | 515 | 515 | 515 | Urban | 70
Brendale Bulk | 336-1 | Brendale BS | Strathpine | 10 POE Load (A) | 118.8346 | 118.8346 | 117.549 | 118.1917 | 118.8346
Brendale Bulk | 336-1 | Brendale BS | Strathpine | Power Factor | 0.99953 | 0.99968 | 0.99972 | 0.99987 | 0.99992
Brendale Bulk | 336-1 | Brendale BS | Strathpine | ECC Rating (A) | 515 | 515 | 515 | 515 | 515
Brendale Bulk | 336-1 | Brendale BS | Strathpine | 50 POE Load (A) | 173.2503 | 173.2503 | 171.3435 | 172.2968 | 173.2503
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | NCC Rating (A) | 788 | 788 | 788 | 788 | 788 | Urban | 70
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | 10 POE Load (A) | 173.176 | 173.176 | 169.6198 | 169.6198 | 168.7999
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | Power Factor | 0.99717 | 0.99733 | 0.99733 | 0.99737 | 0.99733
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | ECC Rating (A) | 902 | 902 | 902 | 902 | 902
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | 50 POE Load (A) | 320.156 | 318.3703 | 313.0188 | 313.0188 | 311.2367
Brendale Bulk | 337-1 | Brendale BS | Strathpine | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Urban | 70
Brendale Bulk | 337-1 | Brendale BS | Strathpine | 10 POE Load (A) | 97.4598 | 97.4598 | 96.4057 | 96.9327 | 97.4598
Brendale Bulk | 337-1 | Brendale BS | Strathpine | Power Factor | 0.99613 | 0.99655 | 0.99668 | 0.99723 | 0.99746
Brendale Bulk | 337-1 | Brendale BS | Strathpine | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
Brendale Bulk | 337-1 | Brendale BS | Strathpine | 50 POE Load (A) | 152.6463 | 152.6463 | 150.9661 | 151.8061 | 152.6463
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | NCC Rating (A) | 654 | 654 | 654 | 654 | 654 | Urban | 70
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | 10 POE Load (A) | 52.1399 | 52.1399 | 51.2827 | 51.2827 | 51.2827
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | Power Factor | 0.99947 | 0.9995 | 0.9995 | 0.99951 | 0.99949
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | 50 POE Load (A) | 98.0419 | 98.0419 | 98.0419 | 98.0419 | 98.0419
Brendale Bulk | 349-1 | Brendale BS | Lawnton | NCC Rating (A) | 805 | 805 | 805 | 805 | 805 | Urban | 70
Brendale Bulk | 349-1 | Brendale BS | Lawnton | 10 POE Load (A) | 276.5835 | 286.7203 | 292.453 | 295.5867 | 297.9394
Brendale Bulk | 349-1 | Brendale BS | Lawnton | Power Factor | 0.98372 | 0.98402 | 0.98379 | 0.98389 | 0.98387
Brendale Bulk | 349-1 | Brendale BS | Lawnton | ECC Rating (A) | 822 | 822 | 822 | 822 | 822
Brendale Bulk | 349-1 | Brendale BS | Lawnton | 50 POE Load (A) | 436.5112 | 453.6753 | 462.5723 | 467.8865 | 470.5468
Brendale Bulk | 464-1 | Brendale BS | Samford | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Brendale Bulk | 464-1 | Brendale BS | Samford | 10 POE Load (A) | 165.4622 | 164.6505 | 162.1187 | 162.3458 | 162.1187
Brendale Bulk | 464-1 | Brendale BS | Samford | Power Factor | 0.99589 | 0.99597 | 0.99596 | 0.99599 | 0.99595
Brendale Bulk | 464-1 | Brendale BS | Samford | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Brendale Bulk | 464-1 | Brendale BS | Samford | 50 POE Load (A) | 241.9493 | 241.9493 | 238.4255 | 238.4255 | 237.4797
Browns Plains Bulk | 406A-1 | Bethania | Kingston | NCC Rating (A) | 1000 | 1000 | 1000 | 1000 | 1000 | Urban | 70
Browns Plains Bulk | 406A-1 | Bethania | Kingston | 10 POE Load (A) | 1.067 | 1.0669 | 1.067 | 1.0669 | 1.0669
Browns Plains Bulk | 406A-1 | Bethania | Kingston | Power Factor | 5.1151e-05 | 5.1146e-05 | 5.1149e-05 | 5.1161e-05 | 5.1154e-05
Browns Plains Bulk | 406A-1 | Bethania | Kingston | ECC Rating (A)
Browns Plains Bulk | 406A-1 | Bethania | Kingston | 50 POE Load (A)
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | NCC Rating (A) | 853 | 853 | 853 | 853 | 853 | Urban | 70
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | 10 POE Load (A) | 1.7009 | 1.7009 | 1.701 | 1.7008 | 1.7008
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | Power Factor | 5.9384e-06 | 5.9381e-06 | 5.9377e-06 | 5.9382e-06 | 5.9381e-06
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | ECC Rating (A)
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | 50 POE Load (A)
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | NCC Rating (A) | 861 | 861 | 861 | 861 | 861 | Rural | 170
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | 10 POE Load (A) | 2.1805 | 2.1805 | 2.1805 | 2.1805 | 2.1805
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | Power Factor | 5.063e-05 | 5.063e-05 | 5.063e-05 | 5.063e-05 | 5.063e-05
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | 50 POE Load (A) | 397.176 | 404.8266 | 404.8266 | 414.4107 | 420.1907
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 741 | 741 | 741 | 741 | 741 | Urban | 70
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | 10 POE Load (A) | 221.5533 | 222.4405 | 219.7798 | 226.88 | 227.7687
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | Power Factor | 0.9898 | 0.99012 | 0.99008 | 0.99011 | 0.98986
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | 50 POE Load (A) | 495.8238 | 498.84 | 494.0667 | 504.2553 | 506.2601
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 741 | 741 | 741 | 741 | 741 | Urban | 70
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | 10 POE Load (A) | 222.7785 | 223.6705 | 220.995 | 228.1348 | 229.0285
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | Power Factor | 0.98963 | 0.98995 | 0.98991 | 0.98993 | 0.98969
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | ECC Rating (A) | 775 | 775 | 775 | 775 | 775
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | 50 POE Load (A) | 498.5957 | 501.6288 | 496.8287 | 507.0745 | 509.0905
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | NCC Rating (A) | 745 | 745 | 745 | 745 | 745 | Urban | 70
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | 10 POE Load (A) | 418.7767 | 418.7767 | 413.4597 | 415.0761 | 413.4597
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | Power Factor | 0.99416 | 0.99413 | 0.99406 | 0.99409 | 0.99402
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | ECC Rating (A) | 745 | 745 | 745 | 745 | 745
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | 50 POE Load (A)
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | 10 POE Load (A) | 552.8406 | 555.5904 | 553.2449 | 556.4936 | 557.2388
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | Power Factor | 0.9682 | 0.96822 | 0.96623 | 0.96619 | 0.96584
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | 50 POE Load (A) | 890.6292 | 893.1112 | 891.31 | 897.1595 | 898.4053
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | 10 POE Load (A) | 552.541 | 555.2893 | 552.945 | 556.192 | 556.9368
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | Power Factor | 0.9682 | 0.96823 | 0.96623 | 0.9662 | 0.96584
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | 50 POE Load (A) | 890.464 | 892.9456 | 891.1447 | 896.9932 | 898.2388
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | 10 POE Load (A) | 172.399 | 173.2648 | 172.336 | 173.4831 | 173.6768
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | Power Factor | 0.98209 | 0.98215 | 0.97971 | 0.97968 | 0.97931
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | 50 POE Load (A) | 259.3872 | 260.0326 | 259.3995 | 261.0731 | 261.3971
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | NCC Rating (A) | 614 | 614 | 614 | 614 | 614 | Urban | 70
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | 10 POE Load (A) | 142.5078 | 143.2874 | 140.5264 | 142.6994 | 142.4951
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | Power Factor | 0.99504 | 0.99542 | 0.98897 | 0.9889 | 0.98721
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | ECC Rating (A) | 614 | 614 | 614 | 614 | 614
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | 50 POE Load (A) | 330.4408 | 330.4541 | 328.5353 | 330.3304 | 330.3371
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | 10 POE Load (A) | 49.4206 | 49.1548 | 49.6896 | 48.7487 | 49.5049
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | Power Factor | 0.84232 | 0.84036 | 0.86717 | 0.86325 | 0.86566
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | 50 POE Load (A) | 223.5085 | 224.3332 | 224.3488 | 226.0965 | 226.7695
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | NCC Rating (A) | 790 | 790 | 790 | 790 | 790 | Urban | 70
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | 10 POE Load (A) | 49.6029 | 49.3382 | 49.8582 | 48.9196 | 49.6744
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | Power Factor | 0.83924 | 0.83726 | 0.86425 | 0.86025 | 0.86272
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | 50 POE Load (A) | 223.6013 | 224.422 | 224.434 | 226.1816 | 226.8547
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Urban | 70
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | 10 POE Load (A) | 277.992 | 281.7333 | 281.7347 | 285.3414 | 287.2099
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | Power Factor | 0.98205 | 0.98197 | 0.98204 | 0.982 | 0.98184
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | 50 POE Load (A) | 261.7418 | 265.49 | 265.5039 | 271.1524 | 273.033
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | NCC Rating (A) | 747 | 747 | 747 | 747 | 747 | Urban | 70
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | 10 POE Load (A) | 412.1138 | 415.7945 | 412.1138 | 417.6361 | 419.4786
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | Power Factor | 0.99368 | 0.99367 | 0.99359 | 0.99354 | 0.99358
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | NCC Rating (A) | 806 | 806 | 806 | 806 | 806 | Urban | 70
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | 10 POE Load (A) | 198.1466 | 199.1434 | 198.0172 | 199.3681 | 199.5811
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | Power Factor | 0.98094 | 0.98103 | 0.97831 | 0.97828 | 0.97786
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | ECC Rating (A) | 806 | 806 | 806 | 806 | 806
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | 50 POE Load (A) | 331.7084 | 331.7084 | 329.894 | 331.703 | 331.703
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | 10 POE Load (A) | 2.5602 | 2.5602 | 2.5602 | 2.5602 | 2.5602
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | Power Factor | 1.828e-05 | 1.828e-05 | 1.828e-05 | 1.828e-05 | 1.828e-05
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | NCC Rating (A) | 706 | 706 | 706 | 706 | 706 | Urban | 70
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | 10 POE Load (A) | 1.5753 | 1.5753 | 1.5753 | 1.5753 | 1.5753
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | Power Factor | 3.1331e-05 | 3.1331e-05 | 3.1331e-05 | 3.1331e-05 | 3.1331e-05
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | NCC Rating (A) | 840 | 840 | 840 | 840 | 840 | Urban | 70
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | 10 POE Load (A) | 0.47829 | 0.47829 | 0.47829 | 0.47829 | 0.47829
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | Power Factor | 2.8112e-05 | 2.8113e-05 | 2.8112e-05 | 2.8112e-05 | 2.8113e-05
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | NCC Rating (A) | 863 | 863 | 863 | 863 | 863 | Urban | 70
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | 10 POE Load (A) | 0.31769 | 0.31769 | 0.31769 | 0.31769 | 0.31769
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | Power Factor | 4.0388e-06 | 4.0388e-06 | 4.0388e-06 | 4.0388e-06 | 4.0388e-06
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | 10 POE Load (A) | 212.6089 | 214.5862 | 213.881 | 216.6273 | 218.5122
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | Power Factor | 0.99295 | 0.99304 | 0.99292 | 0.99285 | 0.99268
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | 50 POE Load (A) | 306.4325 | 309.138 | 308.1801 | 312.3358 | 314.0864
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | 10 POE Load (A) | 223.5418 | 225.6207 | 224.8793 | 227.7666 | 229.7483
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | Power Factor | 0.98821 | 0.98832 | 0.98817 | 0.98809 | 0.98786
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | 50 POE Load (A) | 313.3304 | 316.0949 | 315.1163 | 319.3624 | 321.1512
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | 10 POE Load (A) | 65.7717 | 65.7783 | 64.0193 | 64.0283 | 64.0345
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | Power Factor | 0.99547 | 0.99558 | 0.99557 | 0.99559 | 0.99553
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | ECC Rating (A) | 584 | 584 | 584 | 584 | 584
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | 50 POE Load (A) | 62.5112 | 62.5198 | 60.7561 | 60.769 | 60.7744
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | NCC Rating (A) | 489 | 489 | 489 | 489 | 489 | Rural | 170
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | 10 POE Load (A) | 65.9339 | 65.9405 | 64.1789 | 64.1879 | 64.1941
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | Power Factor | 0.99349 | 0.99358 | 0.99357 | 0.99359 | 0.99354
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | ECC Rating (A) | 489 | 489 | 489 | 489 | 489
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | 50 POE Load (A) | 62.6684 | 62.677 | 60.9106 | 60.9236 | 60.929
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | NCC Rating (A) | 382 | 382 | 382 | 382 | 382 | Rural | 170
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | 10 POE Load (A) | 0.75577 | 0.75571 | 0.75587 | 0.7558 | 0.75574
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | Power Factor | 0.00012196 | 0.00012191 | 0.00012186 | 0.0001219 | 0.00012199
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | ECC Rating (A) | 382 | 382 | 382 | 382 | 382
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | 50 POE Load (A)
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | 10 POE Load (A) | 352.0936 | 370.1973 | 364.573 | 366.8874 | 365.5631
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | Power Factor | 0.99456 | 0.99464 | 0.99458 | 0.99458 | 0.99445
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | 50 POE Load (A) | 645.1764 | 675.5939 | 666.1994 | 670.9845 | 666.1994
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | NCC Rating (A) | 823 | 823 | 823 | 823 | 823 | Rural | 170
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | 10 POE Load (A) | 295.4025 | 304.009 | 299.8609 | 301.4388 | 300.8488
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | Power Factor | 0.98545 | 0.98563 | 0.98549 | 0.9855 | 0.98521
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | ECC Rating (A) | 1018 | 1018 | 1018 | 1018 | 1018
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | 50 POE Load (A) | 661.3804 | 698.0316 | 688.2719 | 693.2014 | 688.2719
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | 10 POE Load (A) | 204.3737 | 198.6898 | 196.8289 | 197.2777 | 197.7899
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | Power Factor | 0.99725 | 0.99731 | 0.99727 | 0.99728 | 0.99719
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | 50 POE Load (A) | 505.7013 | 510.7405 | 503.5276 | 508.1683 | 503.5276
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | NCC Rating (A) | 419 | 419 | 419 | 419 | 419 | Urban | 70
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | 10 POE Load (A) | 191.8769 | 193.199 | 190.2463 | 191.2389 | 191.2107
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | Power Factor | 0.99527 | 0.99536 | 0.99531 | 0.99532 | 0.99519
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | ECC Rating (A) | 470 | 470 | 470 | 470 | 470
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | 50 POE Load (A) | 363.6834 | 366.2719 | 362.3097 | 364.3017 | 362.3097
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | 10 POE Load (A) | 427.4502 | 432.4495 | 432.1114 | 439.1541 | 444.3593
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | Power Factor | 0.98421 | 0.98391 | 0.9835 | 0.98322 | 0.98266
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | ECC Rating (A) | 822 | 822 | 822 | 822 | 822
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | 50 POE Load (A) | 495.2259 | 499.7529 | 498.923 | 507.4427 | 511.1497
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | NCC Rating (A) | 737 | 737 | 737 | 737 | 737 | Urban | 70
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | 10 POE Load (A) | 402.4107 | 407.8807 | 407.8727 | 415.1739 | 420.6568
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | Power Factor | 0.99482 | 0.99465 | 0.9945 | 0.99438 | 0.99417
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | ECC Rating (A) | 737 | 737 | 737 | 737 | 737
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | 50 POE Load (A) | 380.4922 | 384.158 | 384.1541 | 391.4749 | 395.1478
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | NCC Rating (A) | 504 | 504 | 504 | 504 | 504 | Urban | 70
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | 10 POE Load (A) | 28.0955 | 28.1338 | 27.8081 | 27.3428 | 27.5727
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | Power Factor | 0.93001 | 0.92282 | 0.92139 | 0.91936 | 0.91886
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | ECC Rating (A) | 504 | 504 | 504 | 504 | 504
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | 50 POE Load (A) | 116.5495 | 117.4387 | 116.612 | 117.8539 | 117.9108
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | NCC Rating (A) | 425 | 425 | 425 | 425 | 425 | Urban | 70
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | 10 POE Load (A) | 190.8511 | 192.1661 | 189.2292 | 190.2165 | 190.1884
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | Power Factor | 0.99647 | 0.99654 | 0.99649 | 0.9965 | 0.99639
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | ECC Rating (A) | 618 | 618 | 618 | 618 | 618
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | 50 POE Load (A) | 363.9649 | 366.5561 | 362.5901 | 364.5839 | 362.5901
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 238
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | 10 POE Load (A) | 401.0965 | 406.2195 | 405.1753 | 411.3206 | 415.6734
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | Power Factor | 0.98564 | 0.98554 | 0.98526 | 0.98508 | 0.98469
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | ECC Rating (A) | 797 | 797 | 797 | 797 | 797
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | 50 POE Load (A) | 677.5021 | 684.0156 | 683.5383 | 693.2653 | 699.3139
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 239
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | 10 POE Load (A) | 403.9811 | 409.141 | 408.0893 | 414.2788 | 418.663
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | Power Factor | 0.98567 | 0.98557 | 0.98529 | 0.98511 | 0.98472
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | ECC Rating (A) | 797 | 797 | 797 | 797 | 797
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | 50 POE Load (A) | 678.4376 | 684.9597 | 684.4817 | 694.2214 | 700.278
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 775 | 775 | 775 | 775 | 775 | Urban | 70
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | 10 POE Load (A) | 403.2651 | 402.683 | 399.8587 | 401.9123 | 401.9123
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | Power Factor | 0.99148 | 0.99371 | 0.99366 | 0.99367 | 0.99353
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | ECC Rating (A) | 775 | 775 | 775 | 775 | 775
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | 50 POE Load (A) | 539.1089 | 541.1702 | 535.912 | 539.599 | 538.5187
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | NCC Rating (A) | 649 | 649 | 649 | 649 | 649 | Urban | 70
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | 10 POE Load (A) | 63.0956 | 62.8463 | 62.3582 | 62.4743 | 61.6553
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | Power Factor | 0.96993 | 0.97084 | 0.9711 | 0.97127 | 0.97112
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | 50 POE Load (A) | 226.4833 | 226.4936 | 222.776 | 222.8217 | 222.761
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | NCC Rating (A) | 848 | 848 | 848 | 848 | 848 | Urban | 70
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | 10 POE Load (A) | 27.7177 | 28.4847 | 28.9955 | 29.529 | 29.529
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | Power Factor | 0.99998 | 0.99325 | 0.99487 | 0.9958 | 0.99652
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | 50 POE Load (A) | 262.7431 | 264.5803 | 262.6917 | 264.5803 | 266.4184
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | 10 POE Load (A) | 27.9789 | 28.7326 | 29.2339 | 29.7606 | 29.7606
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | Power Factor | 0.99938 | 0.9898 | 0.99205 | 0.99334 | 0.99438
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | 50 POE Load (A) | 262.6513 | 264.4878 | 262.5981 | 264.4878 | 266.3254
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | NCC Rating (A) | 926 | 926 | 926 | 926 | 926 | Urban | 70
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | 10 POE Load (A) | 0.64956 | 0.64953 | 0.64963 | 0.6496 | 0.64957
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | Power Factor | 1.4334e-05 | 1.4334e-05 | 1.4334e-05 | 1.4334e-05 | 1.4334e-05
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | 10 POE Load (A) | 351.4215 | 350.655 | 345.5625 | 345.6452 | 343.7623
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | Power Factor | 0.99179 | 0.99194 | 0.99196 | 0.99202 | 0.99198
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | 50 POE Load (A) | 445.3622 | 445.0513 | 437.5488 | 438.3701 | 436.5866
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 648 | 648 | 648 | 648 | 648 | Urban | 308
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | 10 POE Load (A) | 325.8143 | 327.2859 | 324.6112 | 327.1113 | 327.4938
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | Power Factor | 0.9948 | 0.99489 | 0.99485 | 0.99486 | 0.99475
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | ECC Rating (A) | 726 | 726 | 726 | 726 | 726
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | 50 POE Load (A) | 591.5829 | 595.0463 | 590.8232 | 594.7224 | 596.947
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | 10 POE Load (A) | 253.6476 | 253.1667 | 249.5212 | 249.2885 | 248.3128
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | Power Factor | -0.98835 | -0.98864 | -0.98866 | -0.98878 | -0.9887
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | 50 POE Load (A) | 419.3739 | 419.2236 | 411.6985 | 412.5492 | 410.6286
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | 10 POE Load (A) | 295.5742 | 295.283 | 291.2453 | 291.3657 | 290.5401
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | Power Factor | 0.98896 | 0.98914 | 0.98915 | 0.98922 | 0.98919
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | 50 POE Load (A) | 450.3656 | 450.4277 | 442.7908 | 443.8058 | 441.9469
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | NCC Rating (A) | 649 | 649 | 649 | 649 | 649 | Rural | 170
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | 10 POE Load (A) | 162.1263 | 161.1877 | 159.9768 | 160.5396 | 160.5396
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | Power Factor | 0.99227 | 0.99536 | 0.99539 | 0.99544 | 0.99538
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | 50 POE Load (A) | 397.935 | 397.9802 | 394.2516 | 397.9802 | 398.0268
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | NCC Rating (A) | 678 | 678 | 678 | 678 | 678 | Rural | 170
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | 10 POE Load (A) | 162.1782 | 161.2392 | 160.0278 | 160.5908 | 160.5908
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | Power Factor | 0.9945 | 0.99701 | 0.99704 | 0.99707 | 0.99704
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | 50 POE Load (A) | 398.0224 | 398.0676 | 394.339 | 398.0676 | 398.1143
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | 10 POE Load (A) | 0.00064805 | 0.00064804 | 0.00064807 | 0.00064806 | 0.00064805
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | Power Factor | 0.00030482 | 0.00030458 | 0.00030488 | 0.00030467 | 0.00030497
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 648 | 648 | 648 | 648 | 648 | Urban | 320
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | 10 POE Load (A) | 329.7702 | 331.2596 | 328.5525 | 331.083 | 331.4701
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | Power Factor | 0.99477 | 0.99487 | 0.99482 | 0.99483 | 0.99473
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | ECC Rating (A) | 726 | 726 | 726 | 726 | 726
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | 50 POE Load (A) | 592.0838 | 595.55 | 591.3235 | 595.2258 | 597.4521
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | 10 POE Load (A) | 178.3774 | 178.1205 | 176.8694 | 177.7784 | 177.7784
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | Power Factor | 0.99874 | 0.9995 | 0.99948 | 0.99949 | 0.99944
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | 50 POE Load (A) | 480.0958 | 481.9606 | 477.1958 | 480.5399 | 479.5643
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | NCC Rating (A) | 562 | 562 | 562 | 562 | 562 | Urban | 70
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | 10 POE Load (A) | 240.422 | 239.5863 | 239.0096 | 240.219 | 240.219
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | Power Factor | 0.98585 | 0.99358 | 0.99356 | 0.99356 | 0.99346
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | ECC Rating (A) | 562 | 562 | 562 | 562 | 562
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | 50 POE Load (A) | 388.5221 | 388.4909 | 384.8585 | 388.4807 | 388.4302
Cleveland Bulk | 484-1 | Capalaba | Birkdale | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Cleveland Bulk | 484-1 | Capalaba | Birkdale | 10 POE Load (A) | 121.8431 | 121.0228 | 118.7549 | 118.6748 | 116.9097
Cleveland Bulk | 484-1 | Capalaba | Birkdale | Power Factor | 0.9999 | 0.99991 | 0.99991 | 0.99992 | 0.99991
Cleveland Bulk | 484-1 | Capalaba | Birkdale | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Cleveland Bulk | 484-1 | Capalaba | Birkdale | 50 POE Load (A) | 452.9825 | 451.1084 | 443.3025 | 443.3471 | 441.4055
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 70
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | 10 POE Load (A) | 220.6714 | 222.4086 | 220.6714 | 223.2775 | 224.1467
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | Power Factor | 0.99989 | 0.99989 | 0.99987 | 0.99987 | 0.99982
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | 50 POE Load (A) | 419.3059 | 422.8592 | 421.0822 | 424.6367 | 426.4149
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | NCC Rating (A) | 848 | 848 | 848 | 848 | 848 | Urban | 70
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | 10 POE Load (A) | 252.9283 | 264.7135 | 273.0531 | 327.3402 | 341.7239
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | Power Factor | 0.98629 | 0.98545 | 0.98465 | 0.98404 | 0.98308
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | 50 POE Load (A) | 476.0682 | 499.1075 | 514.581 | 626.1394 | 654.6032
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | NCC Rating (A) | 848 | 848 | 848 | 848 | 848 | Urban | 70
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | 10 POE Load (A) | 254.9239 | 266.8018 | 275.2071 | 329.9217 | 344.4186
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | Power Factor | 0.98624 | 0.98539 | 0.98459 | 0.98397 | 0.98302
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | 50 POE Load (A) | 475.9024 | 498.9216 | 514.3807 | 626.6253 | 655.1673
Coomera Bulk | 394-1 | Coomera BS | Hope Is | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 70
Coomera Bulk | 394-1 | Coomera BS | Hope Is | 10 POE Load (A) | 225.9558 | 227.7355 | 225.9558 | 228.6256 | 229.516
Coomera Bulk | 394-1 | Coomera BS | Hope Is | Power Factor | 0.99999 | 0.99999 | 1 | 1 | 1
Coomera Bulk | 394-1 | Coomera BS | Hope Is | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
Coomera Bulk | 394-1 | Coomera BS | Hope Is | 50 POE Load (A) | 419.4105 | 422.9657 | 421.1878 | 424.7442 | 426.5233
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | 10 POE Load (A) | 176.1318 | 176.1318 | 174.3759 | 175.2538 | 174.3759
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | Power Factor | 0.99589 | 0.99567 | 0.99561 | 0.99562 | 0.99555
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | 50 POE Load (A) | 327.4005 | 329.2036 | 323.7972 | 325.5984 | 325.5984
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | 10 POE Load (A) | 172.7466 | 172.7466 | 171.0245 | 171.8855 | 171.0245
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | Power Factor | 0.99587 | 0.99565 | 0.99559 | 0.9956 | 0.99553
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | 50 POE Load (A) | 327.6288 | 329.4355 | 324.0184 | 325.8231 | 325.8231
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | NCC Rating (A) | 764 | 764 | 764 | 764 | 764 | Urban | 70
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | 10 POE Load (A) | 2.2095 | 2.2095 | 2.2095 | 2.2095 | 2.2095
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | Power Factor | 6.6105e-07 | 6.6104e-07 | 6.6105e-07 | 6.6105e-07 | 6.6104e-07
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 820 | 820 | 820 | 820 | 820 | Urban | 70
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | 10 POE Load (A) | 256.3891 | 256.3891 | 253.7426 | 253.7426 | 252.8608
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | Power Factor | 0.99182 | 0.992 | 0.99199 | 0.99204 | 0.99191
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | 50 POE Load (A) | 480.289 | 482.0558 | 474.9912 | 476.7567 | 474.9912
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 820 | 820 | 820 | 820 | 820 | Urban | 70
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | 10 POE Load (A) | 256.3891 | 256.3891 | 253.7426 | 253.7426 | 252.8608
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | Power Factor | 0.99182 | 0.992 | 0.99199 | 0.99204 | 0.99191
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | 50 POE Load (A) | 480.289 | 482.0558 | 474.9912 | 476.7567 | 474.9912
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | 10 POE Load (A) | 0.59933 | 0.59933 | 0.59935 | 0.59934 | 0.59935
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | Power Factor | 1.126e-05 | 1.126e-05 | 1.126e-05 | 1.126e-05 | 1.126e-05
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | 10 POE Load (A) | 0.059522 | 0.059522 | 0.059524 | 0.059523 | 0.059524
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | Power Factor | 1.5495e-05 | 1.5496e-05 | 1.5497e-05 | 1.5498e-05 | 1.5499e-05
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | NCC Rating (A) | 898 | 898 | 898 | 898 | 898 | Urban | 70
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | 10 POE Load (A) | 0.88447 | 0.88447 | 0.88449 | 0.88448 | 0.88449
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | Power Factor | 2.2115e-05 | 2.2116e-05 | 2.2116e-05 | 2.2116e-05 | 2.2116e-05
Doboy Bulk | 3426-1 | Queensport | Bulimba | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Doboy Bulk | 3426-1 | Queensport | Bulimba | 10 POE Load (A) | 198.6037 | 198.6058 | 195.5367 | 195.5388 | 194.5198
Doboy Bulk | 3426-1 | Queensport | Bulimba | Power Factor | 0.99371 | 0.99376 | 0.99373 | 0.99377 | 0.9937
Doboy Bulk | 3426-1 | Queensport | Bulimba | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Doboy Bulk | 3426-1 | Queensport | Bulimba | 50 POE Load (A) | 320.5878 | 320.5912 | 317.0889 | 317.0923 | 315.3486
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | 10 POE Load (A) | 128.1268 | 128.1306 | 127.457 | 127.5219 | 126.7962
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | Power Factor | 0.99404 | 0.99387 | 0.99389 | 0.99395 | 0.99389
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | 50 POE Load (A) | 286.9667 | 286.9667 | 283.4082 | 283.4082 | 281.6301
Doboy Bulk | 416-1 | Doboy BS | Murarrie | NCC Rating (A) | 397 | 397 | 397 | 397 | 397 | Urban | 70
Doboy Bulk | 416-1 | Doboy BS | Murarrie | 10 POE Load (A) | 160.1346 | 160.1346 | 159.2222 | 160.1346 | 160.1346
Doboy Bulk | 416-1 | Doboy BS | Murarrie | Power Factor | 0.96798 | 0.96817 | 0.96798 | 0.96809 | 0.96792
Doboy Bulk | 416-1 | Doboy BS | Murarrie | ECC Rating (A) | 528 | 528 | 528 | 528 | 528
Doboy Bulk | 416-1 | Doboy BS | Murarrie | 50 POE Load (A) | 305.2011 | 307.0843 | 303.3195 | 305.2011 | 307.0843
Doboy Bulk | 443-1 | Queensport | Bulimba | NCC Rating (A) | 652 | 652 | 652 | 652 | 652 | Urban | 70
Doboy Bulk | 443-1 | Queensport | Bulimba | 10 POE Load (A) | 140.4935 | 140.495 | 138.3245 | 138.326 | 137.6053
Doboy Bulk | 443-1 | Queensport | Bulimba | Power Factor | 0.99632 | 0.99636 | 0.99634 | 0.99636 | 0.99631
Doboy Bulk | 443-1 | Queensport | Bulimba | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Doboy Bulk | 443-1 | Queensport | Bulimba | 50 POE Load (A) | 321.642 | 321.6455 | 318.124 | 318.1274 | 316.3743
Doboy Bulk | 558-1 | Hemmant | Tingalpa | NCC Rating (A) | 680 | 680 | 680 | 680 | 680 | Urban | 70
Doboy Bulk | 558-1 | Hemmant | Tingalpa | 10 POE Load (A) | 170.0868 | 170.0825 | 167.2791 | 167.2156 | 166.1951
Doboy Bulk | 558-1 | Hemmant | Tingalpa | Power Factor | 0.9916 | 0.99191 | 0.99188 | 0.99192 | 0.99186
Doboy Bulk | 558-1 | Hemmant | Tingalpa | ECC Rating (A) | 680 | 680 | 680 | 680 | 680
Doboy Bulk | 558-1 | Hemmant | Tingalpa | 50 POE Load (A) | 285.6793 | 285.6804 | 282.1853 | 282.1878 | 280.4301
Doboy Bulk | 563-1 | Doboy BS | Hemmant | NCC Rating (A) | 389 | 389 | 389 | 389 | 389 | Urban | 70
Doboy Bulk | 563-1 | Doboy BS | Hemmant | 10 POE Load (A) | 143.9068 | 143.8932 | 152.9023 | 153.7411 | 153.2193
Doboy Bulk | 563-1 | Doboy BS | Hemmant | Power Factor | 0.99745 | 0.99643 | 0.99662 | 0.9967 | 0.99665
Doboy Bulk | 563-1 | Doboy BS | Hemmant | ECC Rating (A) | 452 | 452 | 452 | 452 | 452
Doboy Bulk | 563-1 | Doboy BS | Hemmant | 50 POE Load (A) | 259.7789 | 261.3384 | 276.8195 | 278.4082 | 279.0108
Doboy Bulk | 564-1 | Doboy BS | Hemmant | NCC Rating (A) | 389 | 389 | 389 | 389 | 389 | Urban | 70
Doboy Bulk | 564-1 | Doboy BS | Hemmant | 10 POE Load (A) | 138.2059 | 138.1929 | 146.8452 | 147.6507 | 147.1496
Doboy Bulk | 564-1 | Doboy BS | Hemmant | Power Factor | 0.99648 | 0.99523 | 0.99545 | 0.99555 | 0.99549
Doboy Bulk | 564-1 | Doboy BS | Hemmant | ECC Rating (A) | 452 | 452 | 452 | 452 | 452
Doboy Bulk | 564-1 | Doboy BS | Hemmant | 50 POE Load (A) | 258.954 | 260.5093 | 275.9434 | 277.5272 | 278.128
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | NCC Rating (A) | 397 | 397 | 397 | 397 | 397 | Urban | 70
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | 10 POE Load (A) | 151.2767 | 151.2767 | 150.4141 | 151.2767 | 151.2767
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | Power Factor | 0.96629 | 0.9665 | 0.96629 | 0.9664 | 0.96623
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | ECC Rating (A) | 532 | 532 | 532 | 532 | 532
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | 50 POE Load (A) | 305.8552 | 307.7494 | 303.4858 | 305.8552 | 307.7494
Doboy Bulk | 581-1 | Doboy BS | Queensport | NCC Rating (A) | 699 | 699 | 699 | 699 | 699 | Urban | 166
Doboy Bulk | 581-1 | Doboy BS | Queensport | 10 POE Load (A) | 387.3159 | 388.1596 | 383.9565 | 384.7998 | 384.8051
Doboy Bulk | 581-1 | Doboy BS | Queensport | Power Factor | 0.9815 | 0.98159 | 0.98151 | 0.98157 | 0.98152
Doboy Bulk | 581-1 | Doboy BS | Queensport | ECC Rating (A) | 828 | 828 | 828 | 828 | 828
Doboy Bulk | 581-1 | Doboy BS | Queensport | 50 POE Load (A) | 713.7047 | 715.3257 | 708.8696 | 710.4899 | 710.5039
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | NCC Rating (A) | 468 | 468 | 468 | 468 | 468 | HighSec | 0
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | 10 POE Load (A) | 5.3007 | 5.3007 | 5.3007 | 5.3007 | 5.3007
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | Power Factor | 2.1138e-05 | 2.1138e-05 | 2.1138e-05 | 2.1138e-05 | 2.1138e-05
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | 50 POE Load (A)
Doboy Bulk | 677-1 | Doboy BS | Queensport | NCC Rating (A) | 699 | 699 | 699 | 699 | 699 | Urban | 166
Doboy Bulk | 677-1 | Doboy BS | Queensport | 10 POE Load (A) | 386.2384 | 387.0797 | 382.8883 | 383.7293 | 383.7346
Doboy Bulk | 677-1 | Doboy BS | Queensport | Power Factor | 0.98151 | 0.9816 | 0.98152 | 0.98159 | 0.98153
Doboy Bulk | 677-1 | Doboy BS | Queensport | ECC Rating (A) | 828 | 828 | 828 | 828 | 828
Doboy Bulk | 677-1 | Doboy BS | Queensport | 50 POE Load (A) | 713.5428 | 715.1634 | 708.7086 | 710.3286 | 710.3427
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | NCC Rating (A) | 818 | 891 | 891 | 891 | 891 | Rural | 170
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | 10 POE Load (A) | 171.5756 | 194.4945 | 192.9325 | 194.4945 | 193.91
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | Power Factor | 0.975 | 0.97369 | 0.97376 | 0.97396 | 0.97397
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | ECC Rating (A) | 1041 | 1041 | 1041 | 1041 | 1041
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | 50 POE Load (A) | 281.8034 | 281.2524 | 279.4165 | 281.2524 | 281.2524
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | 10 POE Load (A) | 0.0043958 | 0.0043957 | 0.0043958 | 0.0043958 | 0.0043958
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | Power Factor | 4.512e-05 | 4.5093e-05 | 4.5126e-05 | 4.5108e-05 | 4.5112e-05
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | 10 POE Load (A) | 186.9987 | 194.5589 | 192.9967 | 194.5589 | 193.9742
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | Power Factor | 0.97456 | 0.97327 | 0.97334 | 0.97354 | 0.97355
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | 50 POE Load (A) | 281.8655 | 281.3145 | 279.4784 | 281.3145 | 281.3145
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | 10 POE Load (A) | 187.2011 | 194.7569 | 193.1941 | 194.7569 | 194.1718
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | Power Factor | 0.97849 | 0.97766 | 0.97772 | 0.97785 | 0.97787
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | 50 POE Load (A) | 282.0606 | 281.5093 | 279.673 | 281.5093 | 281.5093
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | 10 POE Load (A) | 0.59134 | 0.59104 | 0.59112 | 0.59109 | 0.59109
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | Power Factor | 3.1249e-05 | 3.0304e-05 | 3.0304e-05 | 3.0304e-05 | 3.0304e-05
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | NCC Rating (A) | 809 | 809 | 809 | 809 | 809 | Rural | 170
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | 10 POE Load (A) | 25.9552 | 25.9552 | 25.9552 | 25.9552 | 25.9552
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | Power Factor | 0.95695 | 0.9579 | 0.95806 | 0.95855 | 0.95877
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | 50 POE Load (A) | 48.5628 | 48.5628 | 48.5628 | 48.5628 | 48.5628
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | NCC Rating (A) | 809 | 809 | 809 | 809 | 809 | Rural | 170
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | 10 POE Load (A) | 25.9493 | 25.9493 | 25.9493 | 25.9493 | 25.9493
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | Power Factor | 0.9567 | 0.95765 | 0.95781 | 0.95829 | 0.95851
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | 50 POE Load (A) | 48.5628 | 48.5628 | 48.5628 | 48.5628 | 48.5628
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | NCC Rating (A) | 891 | 891 | 891 | 891 | 891 | Rural | 170
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | 10 POE Load (A) | 198.3966 | 214.8601 | 212.6834 | 214.8601 | 213.5148
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | Power Factor | 0.97656 | 0.97409 | 0.97421 | 0.97446 | 0.97452
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | ECC Rating (A) | 891 | 891 | 891 | 891 | 891
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | 50 POE Load (A) | 374.8169 | 397.7555 | 395.8605 | 397.7555 | 397.7555
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | 10 POE Load (A) | 0.0045544 | 0.0045544 | 0.0045544 | 0.0045544 | 0.0045544
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | Power Factor | 4.3514e-05 | 4.3531e-05 | 4.354e-05 | 4.3524e-05 | 4.3528e-05
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | 10 POE Load (A) | 199.2662 | 215.7694 | 213.5888 | 215.7694 | 214.4206
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | Power Factor | 0.97799 | 0.97586 | 0.97596 | 0.97618 | 0.97623
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | 50 POE Load (A) | 375.7234 | 398.6923 | 396.7964 | 398.6923 | 398.6923
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | 10 POE Load (A) | 0.0045544 | 0.0045544 | 0.0045544 | 0.0045544 | 0.0045544
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | Power Factor | 6.7698e-05 | 6.77e-05 | 6.7699e-05 | 6.7696e-05 | 6.7696e-05
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee1 | 10 POE Load (A) | 0.0045544 | 0.0045544 | 0.0045544 | 0.0045544 | 0.0045544
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee1 | Power Factor | 0.99997 | 0.99999 | 0.99992 | 1 | 0.99999
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | NCC Rating (A) | 878 | 878 | 878 | 878 | 878 | Rural | 170
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | 10 POE Load (A) | 108.3811 | 102.2847 | 102.0207 | 102.2847 | 102.8435
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | Power Factor | 0.98137 | 0.9827 | 0.98266 | 0.98269 | 0.98261
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | 50 POE Load (A) | 285.5349 | 285.529 | 283.652 | 285.529 | 285.529
Gatton Bulk | 531-1 | Gatton | Tenthill | NCC Rating (A) | 293 | 432 | 432 | 432 | 432 | Rural | 170
Gatton Bulk | 531-1 | Gatton | Tenthill | 10 POE Load (A) | 70.9091 | 70.1574 | 68.328 | 68.3353 | 68.3353
Gatton Bulk | 531-1 | Gatton | Tenthill | Power Factor | 0.95006 | 0.95047 | 0.95063 | 0.95085 | 0.95093
Gatton Bulk | 531-1 | Gatton | Tenthill | ECC Rating (A) | 293 | 293 | 432 | 432 | 432
Gatton Bulk | 531-1 | Gatton | Tenthill | 50 POE Load (A) | 64.9303 | 64.3526 | 64.3412 | 64.3412 | 64.3412
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | 10 POE Load (A) | 0.002315 | 0.0023342 | 0.0023355 | 0.0023353 | 0.0023353
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | Power Factor | 8.259e-05 | 8.2615e-05 | 8.2619e-05 | 8.2587e-05 | 8.2662e-05
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | NCC Rating (A) | 144 | 144 | 144 | 144 | 144 | Rural | 170
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | 10 POE Load (A) | 19.8383 | 19.6694 | 19.6583 | 19.6603 | 19.6603
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | Power Factor | 0.91461 | 0.91513 | 0.91524 | 0.91543 | 0.91547
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | ECC Rating (A) | 144 | 144 | 144 | 144 | 144
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | 50 POE Load (A) | 18.3729 | 18.2579 | 18.2548 | 18.2548 | 18.2548
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Rural | 170
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | 10 POE Load (A) | 58.5637 | 40.7516 | 47.9661 | 53.5872 | 58.4125
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | Power Factor | 0.99258 | 0.991 | 0.99289 | 0.99164 | 0.99036
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | 50 POE Load (A) | 113.2342 | 71.6922 | 87.1276 | 95.7241 | 104.3364
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 793 | 793 | 793 | 793 | 793 | Urban | 70
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | 10 POE Load (A) | 271.8953 | 273.728 | 271.4058 | 276.0772 | 276.9953
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | Power Factor | 0.98968 | 0.99025 | 0.98981 | 0.98998 | 0.98978
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | ECC Rating (A) | 827 | 827 | 827 | 827 | 827
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | 50 POE Load (A) | 475.2002 | 476.8405 | 472.3332 | 481.8016 | 483.6536
Goodna Bulk | 3802-1 | Goodna BS | Springfield | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Urban | 70
Goodna Bulk | 3802-1 | Goodna BS | Springfield | 10 POE Load (A) | 241.7192 | 246.7049 | 248.0856 | 263.805 | 268.4036
Goodna Bulk | 3802-1 | Goodna BS | Springfield | Power Factor | 0.98744 | 0.98742 | 0.98687 | 0.98638 | 0.98569
Goodna Bulk | 3802-1 | Goodna BS | Springfield | ECC Rating (A) | 714 | 714 | 714 | 714 | 714
Goodna Bulk | 3802-1 | Goodna BS | Springfield | 50 POE Load (A) | 451.1354 | 460.0331 | 461.8916 | 492.7656 | 500.9538
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | NCC Rating (A) | 550 | 550 | 550 | 550 | 550 | Urban | 70
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | 10 POE Load (A) | 212.2178 | 215.2434 | 215.2161 | 226.3175 | 228.9209
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | Power Factor | 0.97239 | 0.9727 | 0.97238 | 0.97236 | 0.97202
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | 50 POE Load (A) | 312.6077 | 316.5818 | 315.7416 | 331.8157 | 336.2904
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | NCC Rating (A) | 550 | 550 | 550 | 550 | 550 | Urban | 70
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | 10 POE Load (A) | 194.0554 | 196.8221 | 196.7971 | 206.9486 | 209.3292
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | Power Factor | 0.96913 | 0.96946 | 0.96912 | 0.9691 | 0.96874
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | 50 POE Load (A) | 300.4872 | 304.3095 | 303.4832 | 318.9427 | 323.2467
Goodna Bulk | 3806-1 | Goodna BS | Springfield | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Urban | 70
Goodna Bulk | 3806-1 | Goodna BS | Springfield | 10 POE Load (A) | 239.2601 | 244.1887 | 245.5489 | 261.0719 | 265.615
Goodna Bulk | 3806-1 | Goodna BS | Springfield | Power Factor | 0.99666 | 0.99667 | 0.99622 | 0.99583 | 0.99524
Goodna Bulk | 3806-1 | Goodna BS | Springfield | ECC Rating (A) | 714 | 714 | 714 | 714 | 714
Goodna Bulk | 3806-1 | Goodna BS | Springfield | 50 POE Load (A) | 449.5386 | 458.4038 | 460.2549 | 490.9992 | 499.1547
Goodna Bulk | 3807-1 | Goodna BS | Redbank | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Goodna Bulk | 3807-1 | Goodna BS | Redbank | 10 POE Load (A) | 175.0121 | 175.0121 | 197.5222 | 199.2583 | 199.2583
Goodna Bulk | 3807-1 | Goodna BS | Redbank | Power Factor | 0.98495 | 0.98502 | 0.98503 | 0.98508 | 0.98508
Goodna Bulk | 3807-1 | Goodna BS | Redbank | ECC Rating (A) | 1250 | 1250 | 1250 | 1250 | 1250
Goodna Bulk | 3807-1 | Goodna BS | Redbank | 50 POE Load (A)
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 751 | 751 | 751 | 751 | 751 | Urban | 70
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | 10 POE Load (A) | 272.3788 | 274.2148 | 271.8884 | 276.5684 | 277.4882
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | Power Factor | 0.98978 | 0.99035 | 0.98991 | 0.99008 | 0.98989
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | ECC Rating (A) | 803 | 803 | 803 | 803 | 803
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | 50 POE Load (A) | 475.3695 | 477.0103 | 472.5015 | 481.9732 | 483.8259
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Rural | 170
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | 10 POE Load (A) | 66.2055 | 46.0687 | 54.2243 | 60.5787 | 66.0334
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | Power Factor | 0.99326 | 0.99173 | 0.99331 | 0.99223 | 0.99113
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | 50 POE Load (A) | 113.1395 | 71.6611 | 87.0783 | 95.6629 | 104.2618
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | NCC Rating (A) | 794 | 794 | 794 | 794 | 794 | Urban | 70
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | 10 POE Load (A) | 111.8216 | 117.6861 | 121.9691 | 147.2029 | 154.0231
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | Power Factor | 0.99985 | 0.99995 | 0.99996 | 0.99967 | 1
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | ECC Rating (A) | 794 | 794 | 794 | 794 | 794
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | 50 POE Load (A) | 237.1391 | 248.3158 | 255.5146 | 312.4384 | 325.9941
Goodna Bulk | 3881-1 | Springfield | Springfield Central | NCC Rating (A) | 794 | 794 | 794 | 794 | 794 | Urban | 70
Goodna Bulk | 3881-1 | Springfield | Springfield Central | 10 POE Load (A) | 138.6659 | 145.1436 | 149.6699 | 177.6993 | 185.1722
Goodna Bulk | 3881-1 | Springfield | Springfield Central | Power Factor | 0.98073 | 0.98038 | 0.97897 | 0.97776 | 0.97623
Goodna Bulk | 3881-1 | Springfield | Springfield Central | ECC Rating (A) | 794 | 794 | 794 | 794 | 794
Goodna Bulk | 3881-1 | Springfield | Springfield Central | 50 POE Load (A) | 234.3864 | 245.3227 | 252.8672 | 308.2181 | 320.9614
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | NCC Rating (A) | 961 | 961 | 961 | 961 | 961 | Urban | 70
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | 10 POE Load (A) | 75.5841 | 77.3314 | 78.0791 | 85.1973 | 86.9285
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | Power Factor | 0.97113 | 0.97123 | 0.97091 | 0.97066 | 0.97005
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | NCC Rating (A) | 493 | 493 | 493 | 493 | 493 | Urban | 70
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | 10 POE Load (A) | 75.6325 | 77.3746 | 78.1184 | 85.216 | 86.9422
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | Power Factor | 0.91893 | 0.91943 | 0.92063 | 0.9217 | 0.92275
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | ECC Rating (A) | 493 | 493 | 493 | 493 | 493
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | 50 POE Load (A) | 157.2694 | 160.0989 | 160.2843 | 171.1928 | 174.3838
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | NCC Rating (A) | 493 | 493 | 493 | 493 | 493 | Urban | 70
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | 10 POE Load (A) | 75.5603 | 77.3103 | 78.0601 | 85.1892 | 86.9231
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | Power Factor | 0.97004 | 0.97015 | 0.96988 | 0.96967 | 0.9691
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | ECC Rating (A) | 493 | 493 | 493 | 493 | 493
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | 50 POE Load (A) | 157.2769 | 160.111 | 160.2974 | 171.2242 | 174.4201
Griffin Bulk | 312-1 | Kallangur | Narangba | NCC Rating (A) | 489 | 489 | 489 | 489 | 489 | Urban | 70
Griffin Bulk | 312-1 | Kallangur | Narangba | 10 POE Load (A) | 0.64759 | 0.64747 | 0.64748 | 0.64733 | 0.6471
Griffin Bulk | 312-1 | Kallangur | Narangba | Power Factor | 1.3717e-06 | 1.3713e-06 | 1.3714e-06 | 1.3711e-06 | 1.3717e-06
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | 10 POE Load (A) | 252.7617 | 276.5741 | 277.6388 | 286.3025 | 297.2553
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | Power Factor | 0.99987 | 0.99989 | 0.99987 | 0.99985 | 0.99977
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | 50 POE Load (A) | 357.6607 | 397.078 | 398.966 | 411.8344 | 427.1055
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | 10 POE Load (A) | 181.964 | 220.0836 | 223.4776 | 229.3988 | 233.3427
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | Power Factor | 1 | 1 | 1 | 1 | 1
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | 50 POE Load (A) | 364.7632 | 431.8005 | 437.265 | 450.1286 | 461.0055
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | 10 POE Load (A) | 71.6527 | 57.4633 | 55.1516 | 57.9006 | 64.8301
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | Power Factor | 0.98967 | 0.99004 | 0.99073 | 0.99123 | 0.99152
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | 50 POE Load (A) | 223.0326 | 215.0722 | 211.3971 | 220.0624 | 236.1796
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | 10 POE Load (A) | 280.4998 | 291.3367 | 290.5628 | 300.4596 | 315.6546
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | Power Factor | 0.99737 | 0.9973 | 0.99714 | 0.99668 | 0.99576
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | 50 POE Load (A) | 346.6401 | 360.636 | 358.6451 | 371.4749 | 391.2462
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | NCC Rating (A) | 865 | 865 | 865 | 865 | 865 | Urban | 70
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | 10 POE Load (A) | 0.029194 | 0.029193 | 0.029193 | 0.029191 | 0.029188
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | Power Factor | 6.7997e-06 | 6.7997e-06 | 6.7993e-06 | 6.7993e-06 | 6.7997e-06
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 70
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | 10 POE Load (A) | 280.892 | 291.722 | 290.9446 | 300.856 | 316.07
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | Power Factor | 0.99588 | 0.99581 | 0.99565 | 0.99519 | 0.99433
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | 50 POE Load (A) | 347.0463 | 361.0339 | 359.0358 | 371.8805 | 391.6776
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | NCC Rating (A) | 893 | 893 | 893 | 893 | 893 | Urban | 70
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | 10 POE Load (A) | 144.5534 | 149.9441 | 149.5571 | 154.4906 | 162.0635
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | Power Factor | 0.99968 | 0.99965 | 0.9996 | 0.99941 | 0.99899
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | 50 POE Load (A) | 248.8521 | 258.7814 | 257.2212 | 266.3752 | 280.4525
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | 10 POE Load (A) | 0.0016956 | 0.0016955 | 0.0016955 | 0.0016953 | 0.001695
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | Power Factor | 1.9244e-05 | 1.9245e-05 | 1.9244e-05 | 1.9246e-05 | 1.9246e-05
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | NCC Rating (A) | 865 | 865 | 865 | 865 | 865 | Urban | 70
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | 10 POE Load (A) | 144.565 | 149.9553 | 149.5681 | 154.5023 | 162.076
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | Power Factor | 0.99927 | 0.99923 | 0.99916 | 0.99894 | 0.99848
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | 50 POE Load (A) | 248.8736 | 258.8026 | 257.242 | 266.3967 | 280.475
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | NCC Rating (A) | 926 | 926 | 926 | 926 | 926 | Urban | 70
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | 10 POE Load (A) | 108.6633 | 114.057 | 113.6774 | 118.575 | 126.1011
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | Power Factor | 0.99807 | 0.99802 | 0.99794 | 0.99768 | 0.99719
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | 50 POE Load (A) | 192.7362 | 222.3944 | 222.5141 | 231.6364 | 245.6688
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | NCC Rating (A) | 840 | 840 | 840 | 840 | 840 | Urban | 70
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | 10 POE Load (A) | 144.6248 | 150.0127 | 149.6247 | 154.562 | 162.1399
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | Power Factor | 0.99968 | 0.99966 | 0.9996 | 0.99944 | 0.99908
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | 50 POE Load (A) | 248.9802 | 258.9064 | 257.3439 | 266.5022 | 280.5851
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | NCC Rating (A) | 880 | 880 | 880 | 880 | 880 | Urban | 70
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | 10 POE Load (A) | 0.38972 | 0.38935 | 0.38932 | 0.38923 | 0.38916
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | Power Factor | 1.0504e-06 | 1.05e-06 | 1.0509e-06 | 1.0506e-06 | 1.0503e-06
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Urban | 70
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | 10 POE Load (A) | 198.2322 | 226.0591 | 228.0425 | 234.6895 | 241.5244
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | Power Factor | 0.98173 | 0.98202 | 0.98207 | 0.98243 | 0.98275
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | 50 POE Load (A) | 362.5847 | 429.0993 | 434.537 | 447.2529 | 458.184
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Urban | 70
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | 10 POE Load (A) | 198.3183 | 226.1549 | 228.1391 | 234.7875 | 241.623
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | Power Factor | 0.98126 | 0.98155 | 0.9816 | 0.98196 | 0.98231
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | 50 POE Load (A) | 362.6277 | 429.1511 | 434.5895 | 447.3071 | 458.2396
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | NCC Rating (A) | 806 | 806 | 806 | 806 | 806 | Urban | 70
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | 10 POE Load (A) | 198.6832 | 226.5576 | 228.5452 | 235.1986 | 242.0362
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | Power Factor | 0.98149 | 0.98177 | 0.98182 | 0.98219 | 0.98255
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | 50 POE Load (A) | 362.7974 | 429.3536 | 434.7947 | 447.5186 | 458.4565
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | 10 POE Load (A) | 0.43965 | 0.43919 | 0.43916 | 0.43905 | 0.43896
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | Power Factor | 8.5353e-06 | 8.5353e-06 | 8.5353e-06 | 8.5354e-06 | 8.5354e-06
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Urban | 70
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | 10 POE Load (A) | 0.090518 | 0.090421 | 0.090415 | 0.090391 | 0.090372
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | Power Factor | 3.3927e-06 | 3.3928e-06 | 3.3928e-06 | 3.3927e-06 | 3.3927e-06
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | NCC Rating (A) | 917 | 917 | 917 | 917 | 917 | Urban | 70
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | 10 POE Load (A) | 198.158 | 225.9764 | 227.959 | 234.6049 | 241.4392
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | Power Factor | 0.9804 | 0.98072 | 0.98076 | 0.98111 | 0.98139
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | ECC Rating (A) | 917 | 917 | 917 | 917 | 917
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | 50 POE Load (A) | 362.5473 | 429.0539 | 434.491 | 447.2054 | 458.1353
Griffin Bulk | 338-1 | Griffin BS | Strathpine | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
Griffin Bulk | 338-1 | Griffin BS | Strathpine | 10 POE Load (A) | 2.1432 | 2.1432 | 2.1432 | 2.1432 | 2.1432
Griffin Bulk | 338-1 | Griffin BS | Strathpine | Power Factor | 0.00011973 | 0.00011973 | 0.00011973 | 0.00011973 | 0.00011973
Griffin Bulk | 338-1 | Griffin BS | Strathpine | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
Griffin Bulk | 338-1 | Griffin BS | Strathpine | 50 POE Load (A)
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 246 | 246 | 246 | 246 | 246 | Rural | 170
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | 10 POE Load (A) | 69.8002 | 69.8002 | 69.7271 | 69.7271 | 69.7271
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | Power Factor | 0.00028204 | 0.00028204 | 0.00028204 | 0.00028204 | 0.00028204
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | ECC Rating (A) | 246 | 246 | 246 | 246 | 246
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | 50 POE Load (A)
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | 10 POE Load (A) | 67.2066 | 67.2066 | 67.1632 | 67.1632 | 67.1632
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | Power Factor | 0.99895 | 0.99902 | 0.99895 | 0.99896 | 0.99884
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | 50 POE Load (A)
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | 10 POE Load (A) | 103.6823 | 103.6823 | 102.8267 | 102.8267 | 102.8267
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | Power Factor | 0.99999 | 1 | 1 | 1 | 1
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | 50 POE Load (A) | 197.4739 | 199.189 | 195.759 | 197.4739 | 195.759
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | 10 POE Load (A) | 103.7121 | 103.7121 | 102.8563 | 102.8563 | 102.8563
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | Power Factor | 0.99999 | 1 | 1 | 1 | 1
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | 50 POE Load (A) | 197.4751 | 199.1902 | 195.7602 | 197.4751 | 195.7602
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | 10 POE Load (A) | 66.6074 | 66.6074 | 66.5248 | 66.5248 | 66.4362
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | Power Factor | 0.87841 | 0.87995 | 0.88096 | 0.88126 | 0.88125
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | 50 POE Load (A)
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | 10 POE Load (A) | 53.9221 | 53.9221 | 53.8553 | 53.8553 | 53.7837
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | Power Factor | 0.87193 | 0.8735 | 0.87454 | 0.87486 | 0.87485
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | 50 POE Load (A)
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | 10 POE Load (A) | 0.13062 | 0.13062 | 0.13078 | 0.13078 | 0.13094
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | Power Factor | 3.5781e-06 | 3.5781e-06 | 3.5781e-06 | 3.5781e-06 | 3.5781e-06
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Rural | 170
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | 10 POE Load (A) | 170.2335 | 168.0572 | 165.8904 | 165.8904 | 165.8904
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | Power Factor | 0.9085 | 0.9101 | 0.91101 | 0.91135 | 0.91128
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | ECC Rating (A) | 786 | 786 | 786 | 786 | 786
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | 50 POE Load (A)
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | NCC Rating (A) | 322 | 322 | 322 | 322 | 322 | Rural | 170
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | 10 POE Load (A) | 170.6181 | 168.4417 | 166.2749 | 166.2749 | 166.2749
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | Power Factor | 0.91742 | 0.91863 | 0.9194 | 0.91964 | 0.91963
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | ECC Rating (A) | 322 | 322 | 322 | 322 | 322
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | 50 POE Load (A)
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | NCC Rating (A) | 322 | 322 | 322 | 322 | 322 | Rural | 170
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | 10 POE Load (A) | 0.00033654 | 0.00033654 | 0.00033654 | 0.00033654 | 0.00033654
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | Power Factor | 0.00059198 | 0.0005934 | 0.00059345 | 0.00059178 | 0.00059349
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | 10 POE Load (A) | 67.2318 | 67.2318 | 66.4052 | 66.4052 | 65.7242
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | Power Factor | 0.96876 | 0.96767 | 0.9676 | 0.96779 | 0.96775
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | 50 POE Load (A) | 141.8046 | 141.8046 | 138.5785 | 140.0112 | 138.5785
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | 10 POE Load (A) | 0.0018835 | 0.0018835 | 0.0018835 | 0.0018835 | 0.0018835
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | Power Factor | 0.0001059 | 0.00010586 | 0.00010592 | 0.0001058 | 0.00010585
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | 10 POE Load (A) | 67.3017 | 67.3017 | 66.4748 | 66.4748 | 65.8076
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | Power Factor | 0.96816 | 0.96709 | 0.96702 | 0.96721 | 0.96717
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | 50 POE Load (A) | 141.8874 | 141.8874 | 138.6765 | 140.0936 | 138.6765
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | NCC Rating (A) | 401 | 401 | 401 | 401 | 401 | Rural | 170
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | 10 POE Load (A) | 3.3747 | 3.3747 | 3.3749 | 3.3749 | 3.3749
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | Power Factor | 0.00076215 | 0.00076215 | 0.00076215 | 0.00076215 | 0.00076215
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | ECC Rating (A) | 401 | 401 | 401 | 401 | 401
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | 50 POE Load (A)
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Rural | 170
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | 10 POE Load (A) | 1.5376 | 1.5376 | 1.5377 | 1.5377 | 1.5377
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | Power Factor | 0.00014067 | 0.00014067 | 0.00014067 | 0.00014067 | 0.00014067
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | 50 POE Load (A)
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | 10 POE Load (A) | 1.5317 | 1.5317 | 1.5318 | 1.5318 | 1.5318
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | Power Factor | 0.0001403 | 0.0001403 | 0.0001403 | 0.0001403 | 0.0001403
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | 50 POE Load (A)
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | NCC Rating (A) | 401 | 401 | 401 | 401 | 401 | Rural | 170
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | 10 POE Load (A) | 0.59922 | 0.59922 | 0.59925 | 0.59925 | 0.59925
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | Power Factor | 4.3695e-05 | 4.3695e-05 | 4.3695e-05 | 4.3695e-05 | 4.3695e-05
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | 10 POE Load (A) | 68.2525 | 68.2525 | 67.423 | 67.423 | 66.9263
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | Power Factor | 0.9512 | 0.95079 | 0.95076 | 0.95084 | 0.95082
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | 50 POE Load (A) | 142.8084 | 142.8084 | 139.7627 | 141.0115 | 139.7627
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | Rural | 170
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | 10 POE Load (A) | 182.8037 | 182.8037 | 181.0094 | 181.0094 | 181.0094
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | Power Factor | 0.99997 | 0.99996 | 0.99997 | 0.99997 | 0.99997
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | ECC Rating (A) | 194 | 194 | 194 | 194 | 194
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | 50 POE Load (A)
Gympie Bulk | 341-2 | 341 Tee1 | Customer | NCC Rating (A) | 454 | 454 | 454 | 454 | 454 | Rural | 170
Gympie Bulk | 341-2 | 341 Tee1 | Customer | 10 POE Load (A) | 50.1969 | 49.2525 | 48.7425 | 48.7425 | 48.7425
Gympie Bulk | 341-2 | 341 Tee1 | Customer | Power Factor | 0.98851 | 0.98874 | 0.98851 | 0.98851 | 0.98807
Gympie Bulk | 341-2 | 341 Tee1 | Customer | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Gympie Bulk | 341-2 | 341 Tee1 | Customer | 50 POE Load (A)
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | NCC Rating (A) | 292 | 292 | 292 | 292 | 292 | Rural | 170
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | 10 POE Load (A) | 143.6096 | 143.6096 | 143.4854 | 143.4854 | 143.4854
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | Power Factor | 0.9997 | 0.99974 | 0.9997 | 0.9997 | 0.99962
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | ECC Rating (A) | 292 | 292 | 292 | 292 | 292
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | 50 POE Load (A)
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | NCC Rating (A) | 926 | 926 | 926 | 926 | 926 | Rural | 170
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | 10 POE Load (A) | 136.7723 | 136.7723 | 136.6541 | 136.6541 | 136.6541
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | Power Factor | 0.9997 | 0.99974 | 0.9997 | 0.9997 | 0.99963
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | 50 POE Load (A)
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | 10 POE Load (A) | 77.3522 | 77.3522 | 76.4022 | 76.4022 | 75.6424
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | Power Factor | 0.96453 | 0.9634 | 0.96333 | 0.96353 | 0.96348
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | 50 POE Load (A) | 142.6097 | 142.6097 | 139.5579 | 140.8176 | 139.5579
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Rural | 170
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | 10 POE Load (A) | 254.1073 | 254.1073 | 251.7772 | 251.7772 | 251.7772
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | Power Factor | 0.97971 | 0.97978 | 0.97971 | 0.97971 | 0.97958
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | 50 POE Load (A) | 284.5077 | 284.5077 | 282.4306 | 282.4306 | 282.4306
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | NCC Rating (A) | 492 | 492 | 492 | 492 | 492 | Rural | 170
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | 10 POE Load (A) | 47.9699 | 47.9699 | 47.9462 | 47.9462 | 47.9462
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | Power Factor | 0.99729 | 0.99731 | 0.99731 | 0.99732 | 0.99731
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | ECC Rating (A) | 492 | 492 | 492 | 492 | 492
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | 50 POE Load (A) | 44.4686 | 44.4686 | 44.4498 | 44.4498 | 44.4498
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | NCC Rating (A) | 454 | 454 | 454 | 454 | 454 | Rural | 170
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | 10 POE Load (A) | 208.1131 | 208.1131 | 205.7933 | 205.7933 | 205.7933
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | Power Factor | 0.98574 | 0.98581 | 0.98576 | 0.98578 | 0.98568
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | 50 POE Load (A) | 241.1236 | 241.1236 | 239.0563 | 239.0563 | 239.0563
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 266
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | 10 POE Load (A) | 529.9865 | 532.2171 | 529.4914 | 532.5557 | 534.234
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | Power Factor | 0.98955 | 0.98959 | 0.98937 | 0.98927 | 0.98895
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | 50 POE Load (A) | 756.1262 | 762.0882 | 759.4926 | 768.3206 | 772.7803
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 681 | 681 | 681 | 681 | 681 | Urban | 154 | 0.5
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | 10 POE Load (A) | 175.3456 | 176.0842 | 175.1826 | 176.1971 | 176.7528
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | Power Factor | 0.99469 | 0.99472 | 0.99458 | 0.99451 | 0.9943
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | ECC Rating (A) | 681 | 681 | 681 | 681 | 681
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | 50 POE Load (A) | 542.5509 | 545.3267 | 542.2244 | 547.1415 | 548.9916
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | NCC Rating (A) | 921 | 921 | 921 | 921 | 921 | Urban | 256
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | 10 POE Load (A) | 317.6655 | 320.6394 | 320.5127 | 324.5958 | 326.8348
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | Power Factor | 0.992 | 0.99203 | 0.99188 | 0.9918 | 0.99157
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | 50 POE Load (A) | 653.4191 | 661.3868 | 661.4557 | 671.4964 | 677.4439
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | NCC Rating (A) | 734 | 734 | 734 | 734 | 734 | Urban | 70
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | 10 POE Load (A) | 260.497 | 263.3189 | 261.5895 | 264.4131 | 265.7195
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | Power Factor | 0.99658 | 0.99659 | 0.99656 | 0.99657 | 0.99653
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | 50 POE Load (A) | 337.58 | 340.7503 | 337.9362 | 342.2317 | 344.0473
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | NCC Rating (A) | 508 | 508 | 508 | 508 | 508 | Urban | 170
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | 10 POE Load (A) | 0.86448 | 0.86418 | 0.86428 | 0.86391 | 0.86379
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | Power Factor | 4.3786e-07 | 4.3773e-07 | 4.3773e-07 | 4.3772e-07 | 4.3772e-07
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | ECC Rating (A) | 508 | 508 | 508 | 508 | 508
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | 50 POE Load (A) | 392.8353 | 396.7999 | 396.7798 | 404.6437 | 408.5956
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | 10 POE Load (A) | 41.187 | 41.9061 | 41.8605 | 42.579 | 43.0429
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | Power Factor | 0.99833 | 0.99798 | 0.99764 | 0.99721 | 0.99683
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | 50 POE Load (A) | 270.8383 | 274.4227 | 272.6023 | 276.2127 | 278.0114
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | 10 POE Load (A) | 322.6625 | 267.6742 | 272.9201 | 280.2261 | 287.5533
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | Power Factor | 0.96993 | 0.96964 | 0.96896 | 0.96848 | 0.96828
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | 50 POE Load (A)
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | 10 POE Load (A) | 77.0443 | 78.7998 | 78.6271 | 80.3816 | 81.4942
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | Power Factor | 0.99666 | 0.99655 | 0.99644 | 0.99632 | 0.99632
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | ECC Rating (A) | 864 | 864 | 864 | 864 | 864
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | 50 POE Load (A) | 197.6089 | 199.8122 | 199.0052 | 201.8959 | 203.6614
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 595 | 595 | 595 | 595 | 595 | Urban | 70
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | 10 POE Load (A) | 232.3458 | 234.1206 | 232.2555 | 234.0332 | 234.5969
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | Power Factor | 0.98962 | 0.98967 | 0.98955 | 0.98956 | 0.98939
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | ECC Rating (A) | 864 | 864 | 864 | 864 | 864
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | 50 POE Load (A) | 341.6481 | 343.963 | 339.9589 | 343.8204 | 344.7152
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 595 | 430 | 430 | 430 | 430 | Urban | 70
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | 10 POE Load (A) | 233.5583 | 235.3501 | 233.4752 | 235.2622 | 235.8289
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | Power Factor | 0.98705 | 0.98711 | 0.98698 | 0.98699 | 0.9868
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | ECC Rating (A) | 864 | 864 | 864 | 864 | 864
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | 50 POE Load (A) | 342.2664 | 344.5897 | 340.5798 | 344.4471 | 345.3434
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | NCC Rating (A) | 677 | 677 | 677 | 677 | 677 | Urban | 70
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | 10 POE Load (A) | 239.8633 | 242.3755 | 240.7113 | 243.2253 | 244.347
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | Power Factor | 0.98517 | 0.9852 | 0.98509 | 0.98508 | 0.98493
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | 50 POE Load (A) | 343.5599 | 346.6361 | 343.6985 | 348.0554 | 349.8553
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | NCC Rating (A) | 489 | 489 | 489 | 489 | 489 | Urban | 305
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | 10 POE Load (A) | 19.9488 | 22.0701 | 22.9152 | 25.6726 | 27.0875
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | Power Factor | 0.84971 | 0.83545 | 0.81637 | 0.81291 | 0.8183
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | ECC Rating (A) | 489 | 489 | 489 | 489 | 489
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | 50 POE Load (A) | 344.6451 | 350.6101 | 352.506 | 360.4855 | 366.4068
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 300
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | 10 POE Load (A) | 368.1868 | 372.5893 | 372.7296 | 377.8559 | 381.1704
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | Power Factor | 0.97815 | 0.97818 | 0.97786 | 0.97766 | 0.97717
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | 50 POE Load (A) | 649.1773 | 657.1082 | 657.0931 | 666.8473 | 672.7074
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | 10 POE Load (A) | 266.7472 | 280.1455 | 287.8213 | 301.3901 | 312.712
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | Power Factor | 0.9887 | 0.98851 | 0.98808 | 0.98775 | 0.98681
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | 10 POE Load (A) | 420.9896 | 428.7915 | 428.7915 | 438.5844 | 444.4822
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | Power Factor | 0.99349 | 0.99357 | 0.99332 | 0.99312 | 0.99279
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | 50 POE Load (A)
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | 10 POE Load (A) | 107.6109 | 108.9614 | 108.0429 | 127.0044 | 127.0044
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | Power Factor | 0.95672 | 0.95697 | 0.95676 | 0.95426 | 0.94656
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | 50 POE Load (A) | 182.1458 | 182.5968 | 180.6545 | 222.6037 | 221.0156
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | NCC Rating (A) | 442 | 442 | 442 | 442 | 442 | Rural | 170
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | 10 POE Load (A) | 28.7696 | 29.2116 | 29.208 | 29.7204 | 29.7204
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | Power Factor | 0.96628 | 0.95975 | 0.9597 | 0.95972 | 0.959
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | ECC Rating (A) | 800 | 473 | 473 | 473 | 473
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | 50 POE Load (A) | 25.9322 | 26.3738 | 26.3673 | 26.5149 | 26.9514
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | 10 POE Load (A) | 79.1823 | 80.0936 | 79.1759 | 97.6792 | 97.6792
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | Power Factor | 0.94897 | 0.95925 | 0.95905 | 0.95627 | 0.94725
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | 50 POE Load (A) | 156.4394 | 156.4487 | 154.5121 | 196.3576 | 194.3303
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | 10 POE Load (A) | 0.88794 | 0.8876 | 0.8879 | 0.87486 | 0.87482
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | Power Factor | 5.6276e-06 | 5.6276e-06 | 5.6276e-06 | 5.6276e-06 | 5.6276e-06
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | 10 POE Load (A) | 79.4297 | 80.3415 | 79.4234 | 97.9358 | 97.9358
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | Power Factor | 0.9448 | 0.95496 | 0.95482 | 0.9529 | 0.94788
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | 50 POE Load (A) | 156.607 | 156.6163 | 154.6797 | 196.536 | 194.5082
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | 10 POE Load (A) | 37.0094 | 37.0094 | 36.9954 | 37.0094 | 37.0094
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | Power Factor | 0.95038 | 0.97396 | 0.97382 | 0.97388 | 0.97347
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | 50 POE Load (A) | 114.3759 | 114.3759 | 114.3759 | 114.3759 | 114.3759
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | NCC Rating (A) | 324 | 324 | 324 | 324 | 324 | Rural | 170
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | 10 POE Load (A) | 5.2714 | 5.2762 | 5.2684 | 5.2731 | 5.2731
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | Power Factor | 0.99973 | 0.99979 | 0.99977 | 0.99976 | 0.99974
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | ECC Rating (A) | 324 | 324 | 324 | 324 | 324
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | 50 POE Load (A) | 5.9038 | 5.9038 | 5.9038 | 5.9038 | 5.9038
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | 10 POE Load (A) | 32.1214 | 32.1214 | 32.1093 | 32.1214 | 32.1214
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | Power Factor | 0.93708 | 0.96328 | 0.96309 | 0.96299 | 0.96277
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | 50 POE Load (A) | 109.3323 | 109.3323 | 109.3323 | 109.3323 | 109.3323
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | 10 POE Load (A) | 104.4237 | 104.4237 | 103.1501 | 104.4237 | 104.4237
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | Power Factor | 0.9701 | 0.95079 | 0.95048 | 0.95059 | 0.94966
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | 50 POE Load (A) | 214.9056 | 214.9056 | 214.9056 | 214.9056 | 214.9056
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | 10 POE Load (A) | 0.0058802 | 0.0058801 | 0.0058803 | 0.0058802 | 0.0058802
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | Power Factor | 1 | 1 | 1 | 1 | 1
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | 10 POE Load (A) | 104.5623 | 104.5623 | 103.2879 | 104.5623 | 104.5623
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | Power Factor | 0.97311 | 0.95445 | 0.9542 | 0.9543 | 0.95376
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | 50 POE Load (A) | 215.054 | 215.054 | 215.054 | 215.054 | 215.054
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | 10 POE Load (A) | 0.0058802 | 0.0058801 | 0.0058803 | 0.0058802 | 0.0058802
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | Power Factor | 3.3857e-05 | 3.3848e-05 | 3.3853e-05 | 3.3856e-05 | 3.3847e-05
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | 10 POE Load (A) | 104.7732 | 104.7732 | 103.4978 | 104.7732 | 104.7732
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | Power Factor | 0.97319 | 0.95455 | 0.9543 | 0.9544 | 0.95387
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | ECC Rating (A) | 293 | 818 | 818 | 818 | 818
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | 50 POE Load (A) | 215.2651 | 215.2651 | 215.2651 | 215.2651 | 215.2651
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | 10 POE Load (A) | 20.6994 | 20.6994 | 19.764 | 20.6994 | 20.6994
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | Power Factor | 0.97258 | 0.97257 | 0.97248 | 0.97248 | 0.97172
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | 50 POE Load (A) | 19.6947 | 19.6947 | 19.6947 | 19.6947 | 19.6947
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | 10 POE Load (A) | 84.2615 | 84.2615 | 83.8891 | 84.2615 | 84.2615
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | Power Factor | 0.98001 | 0.95363 | 0.95339 | 0.95349 | 0.95351
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | ECC Rating (A) | 293 | 582 | 582 | 582 | 582
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | 50 POE Load (A) | 195.7321 | 195.7321 | 195.7321 | 195.7321 | 195.7321
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | 10 POE Load (A) | 20.8064 | 20.8064 | 19.899 | 20.8064 | 20.8064
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | Power Factor | 0.97193 | 0.97192 | 0.97186 | 0.97186 | 0.97129
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | 50 POE Load (A) | 19.8052 | 19.8052 | 19.8052 | 19.8052 | 19.8052
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | 10 POE Load (A) | 63.9377 | 63.9377 | 64.4586 | 63.9377 | 63.9377
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | Power Factor | 0.98776 | 0.93372 | 0.93298 | 0.93308 | 0.92975
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | ECC Rating (A) | 293 | 432 | 432 | 432 | 432
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | 50 POE Load (A) | 176.305 | 176.305 | 176.305 | 176.305 | 176.305
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | 10 POE Load (A) | 104.3425 | 104.3425 | 103.7586 | 104.3425 | 104.3425
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | Power Factor | 0.93133 | 0.9572 | 0.95686 | 0.95698 | 0.95623
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | 50 POE Load (A) | 168.9293 | 168.9293 | 168.9293 | 168.9293 | 168.9293
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | 10 POE Load (A) | 0.010143 | 0.010143 | 0.010143 | 0.010143 | 0.010143
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | Power Factor | 1.9412e-05 | 1.9414e-05 | 1.9413e-05 | 1.9414e-05 | 1.9414e-05
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | 10 POE Load (A) | 104.7389 | 104.7389 | 104.1535 | 104.7389 | 104.7389
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | Power Factor | 0.94497 | 0.96697 | 0.96678 | 0.96685 | 0.96682
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | 50 POE Load (A) | 169.3452 | 169.3452 | 169.3452 | 169.3452 | 169.3452
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | NCC Rating (A) | 817 | 817 | 817 | 817 | 817 | Rural | 170
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | 10 POE Load (A) | 75.2595 | 75.2595 | 75.2316 | 75.2595 | 75.2595
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | Power Factor | 0.98905 | 0.98097 | 0.98088 | 0.98093 | 0.9808
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | ECC Rating (A) | 293 | 912 | 912 | 912 | 912
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | 50 POE Load (A) | 167.4636 | 167.4636 | 167.4636 | 167.4636 | 167.4636
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | 10 POE Load (A) | 85.5711 | 85.5711 | 85.539 | 85.5711 | 85.5711
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | Power Factor | 0.91846 | 0.9304 | 0.9301 | 0.93023 | 0.93004
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | 50 POE Load (A) | 163.3903 | 163.3903 | 163.3903 | 163.3903 | 163.3903
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | 10 POE Load (A) | 107.819 | 107.819 | 105.9984 | 105.9984 | 105.9984
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | Power Factor | 0.96906 | 0.9691 | 0.96913 | 0.96912 | 0.96906
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | 50 POE Load (A)
Lockrose Bulk | 3832-1 | Tarampa | 383 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 3832-1 | Tarampa | 383 Tee1 | 10 POE Load (A) | 0.0051897 | 0.0051897 | 0.0051897 | 0.0051897 | 0.0051875
Lockrose Bulk | 3832-1 | Tarampa | 383 Tee1 | Power Factor | 1 | 1 | 1 | 1 | 1
Lockrose Bulk | 3832-2 | 3832 Tee1 | 381 Tee1 | NCC Rating (A) | [5 empty] | Rural | 170
Lockrose Bulk | 3832-2 | 3832 Tee1 | 381 Tee1 | 10 POE Load (A)
Lockrose Bulk | 3832-2 | 3832 Tee1 | 381 Tee1 | Power Factor | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | NCC Rating (A) | 858 | 858 | 858 | 858 | 858 | Rural | 170
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | 10 POE Load (A) | 0.73391 | 0.73391 | 0.73391 | 0.73391 | 0.7336
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | Power Factor | 8.0548e-06 | 8.0547e-06 | 8.0548e-06 | 8.0548e-06 | 8.0548e-06
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | ECC Rating (A) | 434 | 434 | 434 | 434 | 434
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | 50 POE Load (A) | 0.74584 | 0.74584 | 0.74584 | 0.74584 | 0.74584
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | 10 POE Load (A) | 34.2737 | 34.2737 | 34.2607 | 34.2737 | 34.2737
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | Power Factor | 0.98339 | 0.96056 | 0.96047 | 0.96064 | 0.96057
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | 50 POE Load (A) | 130.1359 | 130.1359 | 130.1359 | 130.1359 | 130.1359
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | NCC Rating (A) | 451 | 451 | 451 | 451 | 451 | Rural | 170
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | 10 POE Load (A) | 111.8394 | 113.2446 | 112.2904 | 131.9864 | 131.9864
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | Power Factor | 0.95578 | 0.97844 | 0.97837 | 0.97831 | 0.97594
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | ECC Rating (A) | 451 | 451 | 451 | 451 | 451
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | 50 POE Load (A) | 183.3407 | 183.7894 | 181.8052 | 224.3823 | 222.7574
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | NCC Rating (A) | 442 | 442 | 442 | 442 | 442 | Rural | 170
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | 10 POE Load (A) | 28.7037 | 29.1442 | 29.1414 | 29.6374 | 29.6374
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | Power Factor | 0.90884 | 0.96456 | 0.9645 | 0.96452 | 0.9636
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | ECC Rating (A) | 689 | 689 | 689 | 689 | 689
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | 50 POE Load (A) | 25.858 | 26.2985 | 26.2928 | 26.419 | 26.8553
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | 10 POE Load (A) | 83.3164 | 84.2817 | 83.3311 | 102.5211 | 102.5211
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | Power Factor | 0.9932 | 0.9899 | 0.98983 | 0.98895 | 0.98616
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | 50 POE Load (A) | 157.6865 | 157.6946 | 155.7148 | 128.5301 | 196.1372
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | NCC Rating (A) | 898 | 898 | 898 | 898 | 898 | Rural | 170
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | 10 POE Load (A) | 122.7658 | 122.7658 | 122.7658 | 122.7658 | 124.6436
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | Power Factor | 0.97938 | 0.97966 | 0.97962 | 0.97964 | 0.97957
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | ECC Rating (A) | 917 | 917 | 917 | 917 | 917
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | 50 POE Load (A) | 115.546 | 115.546 | 115.546 | 117.4101 | 117.4101
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | 10 POE Load (A) | 84.1785 | 84.1785 | 84.1785 | 84.1785 | 86.0395
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | Power Factor | 0.98206 | 0.98233 | 0.98232 | 0.98233 | 0.98227
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | 50 POE Load (A) | 80.4393 | 80.4393 | 80.4393 | 82.282 | 82.282
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | NCC Rating (A) | 777 | 777 | 777 | 777 | 777 | Urban | 70
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | 10 POE Load (A) | 240.9624 | 241.9066 | 239.0748 | 240.0185 | 240.0185
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | Power Factor | 0.98098 | 0.98146 | 0.98159 | 0.98183 | 0.98192
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | ECC Rating (A) | 832 | 832 | 832 | 832 | 832
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | 50 POE Load (A) | 444.4709 | 446.2929 | 440.9752 | 442.6496 | 442.6496
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | NCC Rating (A) | 724 | 724 | 724 | 724 | 724 | Urban | 280
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | 10 POE Load (A) | 301.0515 | 305.0627 | 304.0594 | 302.0537 | 304.0594
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | Power Factor | 0.9497 | 0.95008 | 0.94963 | 0.94945 | 0.94883
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | 50 POE Load (A) | 527.159 | 534.5096 | 532.6707 | 528.9955 | 532.6707
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | 10 POE Load (A) | 215.2776 | 216.121 | 213.5915 | 214.4344 | 214.4344
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | Power Factor | 0.98302 | 0.98346 | 0.98359 | 0.98381 | 0.9839
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | 50 POE Load (A) | 445.9381 | 447.773 | 442.2706 | 444.104 | 444.104
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | NCC Rating (A) | 692 | 692 | 692 | 692 | 692 | Urban | 70
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | 10 POE Load (A) | 238.2048 | 238.2048 | 234.7287 | 234.7287 | 232.9914
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | Power Factor | 0.00013335 | 0.00013341 | 0.0001335 | 0.00013342 | 0.00013353
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | ECC Rating (A) | 692 | 692 | 692 | 692 | 692
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | 50 POE Load (A)
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | NCC Rating (A) | 567 | 567 | 567 | 567 | 567 | Urban | 280
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | 10 POE Load (A) | 244.4633 | 247.7204 | 246.9057 | 245.2771 | 246.9057
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | Power Factor | 0.98221 | 0.98244 | 0.98217 | 0.98206 | 0.98168
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | ECC Rating (A) | 567 | 567 | 567 | 567 | 567
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | 50 POE Load (A) | 529.7464 | 536.6956 | 534.8425 | 531.139 | 534.8425
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 690 | 690 | 690 | 690 | 690 | Urban | 70
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | 10 POE Load (A) | 201.2275 | 201.2275 | 256.1184 | 269.1948 | 293.7818
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | ECC Rating (A) | 690 | 690 | 690 | 690 | 690
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | 50 POE Load (A) | 397.2558 | 397.2558 | 510.6062 | 537.6863 | 587.0656
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | 10 POE Load (A) | 200.7927 | 200.7927 | 255.5626 | 268.6102 | 293.143
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | 50 POE Load (A) | 397.2784 | 397.2784 | 510.6484 | 537.7342 | 587.1252
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | NCC Rating (A) | 664 | 664 | 664 | 664 | 664 | HighSec | 0
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | 10 POE Load (A) | 155.2493 | 155.2493 | 153.4513 | 154.3502 | 153.4513
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | ECC Rating (A) | 664 | 664 | 664 | 664 | 664
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | 50 POE Load (A) | 302.147 | 302.147 | 296.8624 | 298.6236 | 296.8624
Lytton Bulk | 491-1 | Lytton BS | Lytton | NCC Rating (A) | 511 | 511 | 511 | 511 | 511 | HighSec | 314
Lytton Bulk | 491-1 | Lytton BS | Lytton | 10 POE Load (A) | 220.7853 | 220.7853 | 217.1573 | 232.836 | 231.9339
Lytton Bulk | 491-1 | Lytton BS | Lytton | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 491-1 | Lytton BS | Lytton | ECC Rating (A) | 511 | 511 | 511 | 511 | 511
Lytton Bulk | 491-1 | Lytton BS | Lytton | 50 POE Load (A) | 436.8225 | 436.8225 | 431.1939 | 460.9837 | 460.9837
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | HighSec | 0
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | 10 POE Load (A) | 148.9003 | 148.9003 | 147.1742 | 148.0372 | 147.1742
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | 50 POE Load (A) | 302.3585 | 302.3585 | 297.0664 | 298.83 | 297.0664
Lytton Bulk | 493-1 | Lytton BS | Lytton | NCC Rating (A) | 573 | 573 | 573 | 573 | 573 | HighSec | 0
Lytton Bulk | 493-1 | Lytton BS | Lytton | 10 POE Load (A) | 221.5239 | 221.5239 | 217.8987 | 233.5651 | 232.6611
Lytton Bulk | 493-1 | Lytton BS | Lytton | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 493-1 | Lytton BS | Lytton | ECC Rating (A) | 573 | 573 | 573 | 573 | 573
Lytton Bulk | 493-1 | Lytton BS | Lytton | 50 POE Load (A) | 436.3527 | 436.3527 | 430.7305 | 460.4656 | 460.4656
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | NCC Rating (A) | 546 | 546 | 546 | 546 | 546 | Urban | 70
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | 10 POE Load (A) | 76.9071 | 76.9071 | 131.9137 | 144.7738 | 167.9903
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | ECC Rating (A) | 546 | 546 | 546 | 546 | 546
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | 50 POE Load (A) | 151.6405 | 151.6405 | 264.2127 | 288.3066 | 335.0751
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | 10 POE Load (A) | 77.9877 | 77.9877 | 134.1158 | 147.2393 | 170.9319
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | 50 POE Load (A) | 150.6666 | 150.6666 | 262.9824 | 287.0236 | 333.6808
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | 10 POE Load (A) | 133.2332 | 133.2332 | 130.8801 | 130.8801 | 130.2924
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | Power Factor | 0.99985 | 0.99982 | 0.99983 | 0.99982 | 0.99984
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | 50 POE Load (A) | 390.1497 | 388.1904 | 382.1146 | 382.1146 | 380.1673
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | 10 POE Load (A) | 54.8499 | 54.8499 | 53.8789 | 53.8789 | 53.6364
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | Power Factor | 0.99792 | 0.99798 | 0.99797 | 0.998 | 0.99795
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | 50 POE Load (A) | 160.6351 | 159.8282 | 157.3231 | 157.3231 | 156.5212
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 840 | 840 | 840 | 840 | 840 | Urban | 70
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | 10 POE Load (A) | 133.2184 | 133.2184 | 130.866 | 130.866 | 130.2785
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | Power Factor | 0.99992 | 0.9999 | 0.99991 | 0.9999 | 0.99991
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | 50 POE Load (A) | 229.7871 | 228.6333 | 225.0534 | 225.0534 | 223.9067
Lytton Bulk | 560-16 | Lota | 560 Tee1 | NCC Rating (A) | 1053 | 1053 | 1053 | 1053 | 1053 | Urban | 70
Lytton Bulk | 560-16 | Lota | 560 Tee1 | 10 POE Load (A) | 134.1641 | 134.1641 | 131.7928 | 131.7928 | 131.2006
Lytton Bulk | 560-16 | Lota | 560 Tee1 | Power Factor | 0.99221 | 0.99226 | 0.99225 | 0.99228 | 0.99223
Lytton Bulk | 560-16 | Lota | 560 Tee1 | ECC Rating (A) | 1053 | 1053 | 1053 | 1053 | 1053
Lytton Bulk | 560-16 | Lota | 560 Tee1 | 50 POE Load (A) | 391.5958 | 389.6304 | 383.5096 | 383.5096 | 381.5563
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | 10 POE Load (A) | 0.10195 | 0.10196 | 0.10197 | 0.10197 | 0.10197
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | Power Factor | 1.9408e-06 | 1.9406e-06 | 1.9409e-06 | 1.9409e-06 | 1.9395e-06
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | 10 POE Load (A) | 133.2719 | 133.2719 | 130.9167 | 130.9167 | 130.3286
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | Power Factor | 0.99866 | 0.99872 | 0.9987 | 0.99873 | 0.99868
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | 50 POE Load (A) | 390.2818 | 388.3218 | 382.2416 | 382.2416 | 380.2936
Lytton Bulk | 560-5 | Lota | 560 Tee2 | NCC Rating (A) | 775 | 775 | 775 | 775 | 775 | Urban | 70
Lytton Bulk | 560-5 | Lota | 560 Tee2 | 10 POE Load (A) | 78.5014 | 78.5014 | 77.1141 | 77.1141 | 76.7439
Lytton Bulk | 560-5 | Lota | 560 Tee2 | Power Factor | 0.99877 | 0.99883 | 0.99882 | 0.99885 | 0.9988
Lytton Bulk | 560-5 | Lota | 560 Tee2 | ECC Rating (A) | 775 | 775 | 775 | 775 | 775
Lytton Bulk | 560-5 | Lota | 560 Tee2 | 50 POE Load (A) | 229.7426 | 228.589 | 225.0108 | 225.0108 | 223.8642
Lytton Bulk | 569-1 | Lytton BS | Lota | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Urban | 70
Lytton Bulk | 569-1 | Lytton BS | Lota | 10 POE Load (A) | 274.9522 | 274.9522 | 270.0946 | 270.0946 | 268.8814
Lytton Bulk | 569-1 | Lytton BS | Lota | Power Factor | 0.99585 | 0.99593 | 0.99592 | 0.99596 | 0.99589
Lytton Bulk | 569-1 | Lytton BS | Lota | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Lytton Bulk | 569-1 | Lytton BS | Lota | 50 POE Load (A) | 379.2924 | 377.4706 | 372.0107 | 372.0107 | 370.1927
Lytton Bulk | 599-1 | Hemmant | Lindum | NCC Rating (A) | 630 | 630 | 630 | 630 | 630 | Urban | 70
Lytton Bulk | 599-1 | Hemmant | Lindum | 10 POE Load (A) | 1.7462 | 1.7462 | 1.7462 | 1.7462 | 1.7462
Lytton Bulk | 599-1 | Hemmant | Lindum | Power Factor | 1.164e-06 | 1.1625e-06 | 1.1632e-06 | 1.1633e-06 | 1.1636e-06
Lytton Bulk | 599-1 | Hemmant | Lindum | ECC Rating (A) | 630 | 630 | 630 | 630 | 630
Lytton Bulk | 599-1 | Hemmant | Lindum | 50 POE Load (A)
Lytton Bulk | 681-1 | Lindum | Wynnum | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Lytton Bulk | 681-1 | Lindum | Wynnum | 10 POE Load (A) | 173.9254 | 174.8213 | 173.0297 | 174.8213 | 174.8213
Lytton Bulk | 681-1 | Lindum | Wynnum | Power Factor | 0.99218 | 0.99222 | 0.99208 | 0.99202 | 0.9918
Lytton Bulk | 681-1 | Lindum | Wynnum | ECC Rating (A) | 837 | 837 | 837 | 837 | 837
Lytton Bulk | 681-1 | Lindum | Wynnum | 50 POE Load (A) | 323.7782 | 325.6106 | 321.9471 | 323.7782 | 325.6106
Lytton Bulk | 682-1 | Lindum | Wynnum | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Lytton Bulk | 682-1 | Lindum | Wynnum | 10 POE Load (A) | 166.6773 | 167.5358 | 165.8189 | 167.5358 | 167.5358
Lytton Bulk | 682-1 | Lindum | Wynnum | Power Factor | 0.97996 | 0.98001 | 0.97984 | 0.97977 | 0.97949
Lytton Bulk | 682-1 | Lindum | Wynnum | ECC Rating (A) | 837 | 837 | 837 | 837 | 837
Lytton Bulk | 682-1 | Lindum | Wynnum | 50 POE Load (A) | 324.3786 | 326.2202 | 322.5383 | 324.3786 | 326.2202
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 70
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | 10 POE Load (A) | 123.6607 | 124.2983 | 123.0232 | 124.2983 | 124.2983
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | Power Factor | 0.99995 | 0.99995 | 0.99994 | 0.99993 | 0.9999
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | 50 POE Load (A) | 316.2502 | 317.9993 | 314.5016 | 316.2502 | 317.9993
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | NCC Rating (A) | 517 | 517 | 517 | 517 | 517 | Urban | 70
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | 10 POE Load (A) | 2.2525 | 2.2525 | 2.2525 | 2.2525 | 2.2525
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | Power Factor | 1.8338e-05 | 1.8338e-05 | 1.8338e-05 | 1.8338e-05 | 1.8338e-05
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | ECC Rating (A) | 517 | 517 | 517 | 517 | 517
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | 50 POE Load (A)
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | 10 POE Load (A) | 123.8159 | 124.4551 | 123.1769 | 124.4551 | 124.4551
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | Power Factor | 0.999 | 0.99902 | 0.99897 | 0.99894 | 0.99886
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | 50 POE Load (A) | 316.5754 | 318.3261 | 314.8252 | 316.5754 | 318.3261
Lytton Bulk | 688-1 | Lytton BS | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
Lytton Bulk | 688-1 | Lytton BS | Lindum | 10 POE Load (A) | 215.2996 | 216.4115 | 214.188 | 216.4115 | 216.4115
Lytton Bulk | 688-1 | Lytton BS | Lindum | Power Factor | 0.98868 | 0.98873 | 0.98853 | 0.98845 | 0.98812
Lytton Bulk | 688-1 | Lytton BS | Lindum | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Lytton Bulk | 688-1 | Lytton BS | Lindum | 50 POE Load (A) | 316.0544 | 317.7987 | 314.3105 | 316.0544 | 317.7987
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | NCC Rating (A) | 775 | 775 | 775 | 775 | 775 | Urban | 70
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | 10 POE Load (A) | 45.5497 | 45.0155 | 41.681 | 40.0724 | 38.4612
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | Power Factor | 0.9568 | 0.94324 | 0.94342 | 0.94385 | 0.94409
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | 50 POE Load (A) | 136.2694 | 136.2726 | 134.5402 | 134.5498 | 134.5578
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 771 | 771 | 771 | 771 | 771 | Urban | 70
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | 10 POE Load (A) | 126.4128 | 127.91 | 134.1958 | 138.7101 | 143.2351
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | Power Factor | 0.95594 | 0.95211 | 0.9514 | 0.95104 | 0.95038
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | ECC Rating (A) | 843 | 843 | 843 | 843 | 843
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | 50 POE Load (A) | 209.7741 | 212.3668 | 223.2529 | 231.0715 | 237.6015
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 771 | 771 | 771 | 771 | 771 | Urban | 70
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | 10 POE Load (A) | 125.4176 | 126.903 | 133.1385 | 137.6168 | 142.1056
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | Power Factor | 0.95606 | 0.95222 | 0.95151 | 0.95114 | 0.95048
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | ECC Rating (A) | 843 | 843 | 843 | 843 | 843
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | 50 POE Load (A) | 209.3359 | 211.9233 | 222.7866 | 230.5889 | 237.1053
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | 10 POE Load (A) | 98.4149 | 98.9501 | 100.5463 | 102.1594 | 103.7761
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | Power Factor | 0.95231 | 0.9467 | 0.9464 | 0.94635 | 0.94608
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | 50 POE Load (A) | 135.3667 | 135.3667 | 133.6222 | 133.6222 | 134.8239
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 889 | 889 | 889 | 889 | 889 | Urban | 70
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | 10 POE Load (A) | 0.8432 | 0.8432 | 0.8432 | 0.8432 | 0.8432
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | Power Factor | 5.6181e-06 | 5.6182e-06 | 5.6184e-06 | 5.6184e-06 | 5.6182e-06
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 841 | 841 | 841 | 841 | 841 | Urban | 70
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | 10 POE Load (A) | 0.56996 | 0.56996 | 0.56996 | 0.56996 | 0.56996
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | Power Factor | 9.097e-06 | 9.0972e-06 | 9.097e-06 | 9.097e-06 | 9.0972e-06
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | NCC Rating (A) | 790 | 790 | 790 | 790 | 790 | Urban | 70
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | 10 POE Load (A) | 254.9532 | 273.2716 | 270.9392 | 283.8445 | 284.6176
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | Power Factor | 0.99311 | 0.99325 | 0.99277 | 0.99281 | 0.99222
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | 50 POE Load (A) | 414.3567 | 437.9728 | 434.0061 | 451.3031 | 451.8032
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | 10 POE Load (A) | 202.6873 | 217.2533 | 215.3988 | 225.6604 | 226.2751
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | Power Factor | 0.99672 | 0.9968 | 0.99655 | 0.99657 | 0.99625
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | 50 POE Load (A) | 334.4569 | 360.8583 | 357.2362 | 375.511 | 375.5636
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | 10 POE Load (A) | 262.0547 | 255.3635 | 254.6263 | 251.9022 | 253.2869
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | Power Factor | 0.99407 | 0.99418 | 0.99413 | 0.99413 | 0.99406
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | 50 POE Load (A) | 554.4505 | 555.3137 | 551.6792 | 556.6685 | 559.2989
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | 10 POE Load (A) | 187.6691 | 189.2415 | 189.9265 | 193.6602 | 196.3899
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | Power Factor | 0.98337 | 0.98342 | 0.98313 | 0.98309 | 0.9828
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | 50 POE Load (A) | 315.4693 | 320.7962 | 320.8736 | 327.9567 | 331.5147
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | 10 POE Load (A) | 76.8238 | 68.902 | 67.5747 | 61.5259 | 60.3181
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | Power Factor | 0.99785 | 0.99758 | 0.99635 | 0.99591 | 0.99439
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | ECC Rating (A) | 749 | 749 | 749 | 749 | 749
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | 50 POE Load (A) | 475.308 | 477.2105 | 471.9759 | 475.6399 | 475.6842
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | 10 POE Load (A) | 69.4557 | 79.4067 | 78.6248 | 78.6248 | 77.8432
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | Power Factor | 0.99793 | 0.99806 | 0.99578 | 0.99589 | 0.99588
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | ECC Rating (A) | 637 | 637 | 637 | 637 | 637
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | 50 POE Load (A) | 154.4947 | 178.6463 | 176.8907 | 176.8907 | 176.8907
Molendinar Bulk | 390-2 | F390 Tee | Bundall | NCC Rating (A) | 701 | 701 | 701 | 701 | 701 | Urban | 70
Molendinar Bulk | 390-2 | F390 Tee | Bundall | 10 POE Load (A) | 69.8868 | 79.8554 | 79.0719 | 79.0719 | 78.2887
Molendinar Bulk | 390-2 | F390 Tee | Bundall | Power Factor | 0.99188 | 0.99199 | 0.99041 | 0.99049 | 0.99048
Molendinar Bulk | 390-2 | F390 Tee | Bundall | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
Molendinar Bulk | 390-2 | F390 Tee | Bundall | 50 POE Load (A) | 155.1577 | 179.3423 | 177.5907 | 177.5907 | 177.5907
Molendinar Bulk | 390-3 | F390 Tee | Miami | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Molendinar Bulk | 390-3 | F390 Tee | Miami | 10 POE Load (A) | 0.18503 | 0.18482 | 0.18484 | 0.18484 | 0.18485
Molendinar Bulk | 390-3 | F390 Tee | Miami | Power Factor | 1 | 1 | 1 | 1 | 1
Molendinar Bulk | 390-3 | F390 Tee | Miami | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Molendinar Bulk | 390-3 | F390 Tee | Miami | 50 POE Load (A)
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | 10 POE Load (A) | 86.3674 | 99.1111 | 98.1401 | 98.1401 | 97.1696
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | Power Factor | 0.98493 | 0.98515 | 0.98167 | 0.98183 | 0.98181
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | 50 POE Load (A) | 153.0234 | 176.4975 | 174.6812 | 174.6812 | 174.6812
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | 10 POE Load (A) | 196.1067 | 196.9758 | 195.2378 | 196.1067 | 196.9758
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | Power Factor | 0.99461 | 0.99498 | 0.99511 | 0.99517 | 0.9951
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | 50 POE Load (A) | 359.9761 | 361.7303 | 358.2223 | 361.7303 | 361.7303
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 553
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | 10 POE Load (A) | 363.5961 | 369.5379 | 365.8511 | 370.8761 | 371.5506
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | Power Factor | 0.99153 | 0.99183 | 0.99176 | 0.99187 | 0.99165
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | ECC Rating (A) | 764 | 764 | 764 | 764 | 764
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | 50 POE Load (A) | 620.76 | 631.6699 | 624.127 | 634.0621 | 634.9863
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | 10 POE Load (A) | 146.3742 | 150.2244 | 149.5131 | 152.9508 | 153.7329
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | Power Factor | 0.99597 | 0.99603 | 0.99596 | 0.99595 | 0.99584
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | 50 POE Load (A) | 321.1174 | 326.7254 | 326.7254 | 334.224 | 337.9826
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | NCC Rating (A) | 794 | 794 | 794 | 794 | 794 | Urban | 70
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | 10 POE Load (A) | 196.5492 | 197.4203 | 195.6784 | 196.5492 | 197.4203
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | Power Factor | 0.99459 | 0.99496 | 0.99509 | 0.99515 | 0.99509
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | 50 POE Load (A) | 359.9622 | 361.7164 | 358.2086 | 361.7164 | 361.7164
Molendinar Bulk | 474A-1 | Arundel | Hollywell | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 517
Molendinar Bulk | 474A-1 | Arundel | Hollywell | 10 POE Load (A) | 423.9546 | 434.0824 | 431.9304 | 440.231 | 441.5792
Molendinar Bulk | 474A-1 | Arundel | Hollywell | Power Factor | 0.98922 | 0.98927 | 0.9891 | 0.98906 | 0.98885
Molendinar Bulk | 474A-1 | Arundel | Hollywell | ECC Rating (A) | 2000 | 2000 | 2000 | 2000 | 2000
Molendinar Bulk | 474A-1 | Arundel | Hollywell | 50 POE Load (A) | 474.4099 | 490.9339 | 486.9264 | 500.4694 | 501.5099
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | 10 POE Load (A) | 3.8432 | 3.8423 | 3.8426 | 3.8417 | 3.8416
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | Power Factor | 5.1781e-05 | 5.1781e-05 | 5.1781e-05 | 5.1781e-05 | 5.1781e-05
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | ECC Rating (A) | 935 | 935 | 935 | 935 | 935
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | 50 POE Load (A)
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 70
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | 10 POE Load (A) | 363.8591 | 369.8052 | 366.1157 | 371.1444 | 371.8194
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | Power Factor | 0.99151 | 0.99182 | 0.99174 | 0.99186 | 0.99164
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | ECC Rating (A) | 764 | 764 | 764 | 764 | 764
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | 50 POE Load (A) | 620.8511 | 631.7626 | 624.2187 | 634.1552 | 635.0795
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | 10 POE Load (A) | 190.2252 | 191.0747 | 188.5818 | 190.2252 | 190.2803
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | Power Factor | 0.99315 | 0.9932 | 0.99314 | 0.99311 | 0.993
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | 50 POE Load (A) | 366.3565 | 368.1553 | 364.5584 | 368.1553 | 368.1553
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | 10 POE Load (A) | 0.0043024 | 0.0043024 | 0.0043024 | 0.0043024 | 0.0043024
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | Power Factor | 6.6114e-05 | 6.6116e-05 | 6.6127e-05 | 6.6128e-05 | 6.6108e-05
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | 10 POE Load (A) | 190.2367 | 191.0747 | 188.5932 | 190.2367 | 190.2803
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | Power Factor | 0.99321 | 0.99325 | 0.9932 | 0.99317 | 0.99308
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | 50 POE Load (A) | 366.3844 | 368.1833 | 364.5862 | 368.1833 | 368.1833
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | 10 POE Load (A) | 0.12374 | 0.12373 | 0.12374 | 0.12374 | 0.12373
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | Power Factor | 8.6877e-06 | 8.6871e-06 | 8.6866e-06 | 8.6877e-06 | 8.6869e-06
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | 10 POE Load (A) | 190.2367 | 191.0747 | 188.5932 | 190.2367 | 190.3287
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | Power Factor | 0.99383 | 0.99386 | 0.99382 | 0.9938 | 0.99373
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | 50 POE Load (A) | 366.4134 | 368.2124 | 364.6152 | 368.2124 | 368.2124
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | 10 POE Load (A) | 206.0166 | 206.9364 | 204.2374 | 206.0166 | 206.0763
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | Power Factor | 0.9908 | 0.99084 | 0.99079 | 0.99077 | 0.99068
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | 50 POE Load (A) | 365.571 | 367.3612 | 363.7816 | 367.3612 | 367.3612
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | 10 POE Load (A) | 76.5339 | 77.4691 | 77.4691 | 78.4051 | 78.4051
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | Power Factor | 0.96083 | 0.96087 | 0.96055 | 0.96046 | 0.96005
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | 50 POE Load (A) | 581.185 | 622.7913 | 614.6038 | 617.6748 | 617.6748
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | NCC Rating (A) | 799 | 799 | 799 | 799 | 799 | Rural | 170
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | 10 POE Load (A) | 77.313 | 78.2508 | 78.2508 | 79.1893 | 79.1893
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | Power Factor | 0.95768 | 0.95772 | 0.95745 | 0.95737 | 0.95703
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | ECC Rating (A) | 799 | 799 | 799 | 799 | 799
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | 50 POE Load (A) | 136.0613 | 137.8327 | 137.8327 | 139.6056 | 139.6056
Nambour Bulk | 344-1 | Nambour BS | Maleny | NCC Rating (A) | 293 | 293 | 432 | 432 | 432 | Rural | 170
Nambour Bulk | 344-1 | Nambour BS | Maleny | 10 POE Load (A) | 185.6993 | 187.8597 | 175.1252 | 175.1252 | 175.1252
Nambour Bulk | 344-1 | Nambour BS | Maleny | Power Factor | 0.97112 | 0.97088 | 0.97094 | 0.97085 | 0.97097
Nambour Bulk | 344-1 | Nambour BS | Maleny | ECC Rating (A) | 293 | 293 | 293 | 432 | 432
Nambour Bulk | 344-1 | Nambour BS | Maleny | 50 POE Load (A)
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | 10 POE Load (A) | 86.5914 | 86.4389 | 84.5825 | 84.5825 | 84.5825
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | Power Factor | 0.99171 | 0.99205 | 0.99202 | 0.99206 | 0.99201
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | 50 POE Load (A)
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | 10 POE Load (A) | 169.8775 | 170.7188 | 169.0369 | 169.8775 | 170.7188
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | Power Factor | 0.98254 | 0.98205 | 0.98181 | 0.9817 | 0.98131
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | 50 POE Load (A) | 376.5814 | 378.7375 | 374.4295 | 376.5814 | 376.5814
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | NCC Rating (A) | 515 | 515 | 515 | 515 | 515 | Rural | 170
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | 10 POE Load (A) | 170.2508 | 171.0929 | 169.4093 | 170.2508 | 171.0929
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | Power Factor | 0.98256 | 0.98232 | 0.98214 | 0.98206 | 0.98178
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | ECC Rating (A) | 515 | 515 | 515 | 515 | 515
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | 50 POE Load (A) | 376.9732 | 379.1302 | 374.8203 | 376.9732 | 376.9732
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | 10 POE Load (A) | 1.6848 | 1.6845 | 1.685 | 1.6848 | 1.6848
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | Power Factor | 0.00019082 | 0.00019082 | 0.00019082 | 0.00019082 | 0.00019082
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | 50 POE Load (A) | 212.3842 | 233.2218 | 231.0252 | 233.1743 | 235.282
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | 10 POE Load (A) | 216.9133 | 217.9872 | 215.8401 | 216.9133 | 217.9872
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | Power Factor | 0.97853 | 0.97816 | 0.97794 | 0.97784 | 0.97749
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | 50 POE Load (A) | 367.8979 | 369.9304 | 365.8683 | 367.8979 | 367.8979
Nambour Bulk | 489-1 | Nambour BS | Yandina | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Nambour Bulk | 489-1 | Nambour BS | Yandina | 10 POE Load (A) | 70.0014 | 70.8549 | 70.8549 | 71.7089 | 71.7089
Nambour Bulk | 489-1 | Nambour BS | Yandina | Power Factor | 0.99789 | 0.99788 | 0.99795 | 0.99797 | 0.99806
Nambour Bulk | 489-1 | Nambour BS | Yandina | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Nambour Bulk | 489-1 | Nambour BS | Yandina | 50 POE Load (A) | 253.6917 | 269.4619 | 266.4641 | 268.1192 | 268.1192
Nudgee Bulk | 3280-1 | Hendra | Clayfield | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
Nudgee Bulk | 3280-1 | Hendra | Clayfield | 10 POE Load (A) | 113.1522 | 114.9073 | 114.0327 | 115.7751 | 115.7751
Nudgee Bulk | 3280-1 | Hendra | Clayfield | Power Factor | 0.99934 | 0.9994 | 0.99935 | 0.99934 | 0.99928
Nudgee Bulk | 3280-1 | Hendra | Clayfield | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
Nudgee Bulk | 3280-1 | Hendra | Clayfield | 50 POE Load (A) | 220.1564 | 221.9687 | 221.96 | 223.7489 | 225.5376
Nudgee Bulk | 535-1 | Hendra | Nundah | NCC Rating (A) | [5 empty] | Urban | 70
Nudgee Bulk | 535-1 | Hendra | Nundah | 10 POE Load (A)
Nudgee Bulk | 535-1 | Hendra | Nundah | Power Factor | 0 | 0 | 0 | 0 | 0
Nudgee Bulk | 535-1 | Hendra | Nundah | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
Nudgee Bulk | 535-1 | Hendra | Nundah | 50 POE Load (A)
Nudgee Bulk | 540-1 | Hendra | Nundah | NCC Rating (A) | 775 | 775 | 775 | 775 | 775 | Urban | 70
Nudgee Bulk | 540-1 | Hendra | Nundah | 10 POE Load (A) | 140.7076 | 148.346 | 147.1318 | 148.6376 | 148.6376
Nudgee Bulk | 540-1 | Hendra | Nundah | Power Factor | 0.99797 | 0.99823 | 0.99828 | 0.99831 | 0.99843
Nudgee Bulk | 540-1 | Hendra | Nundah | ECC Rating (A) | 775 | 775 | 775 | 775 | 775
Nudgee Bulk | 540-1 | Hendra | Nundah | 50 POE Load (A) | 320.4381 | 322.2853 | 316.9082 | 318.704 | 318.712
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | NCC Rating (A) | 778 | 778 | 778 | 778 | 778 | Urban | 192
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | 10 POE Load (A) | 470.8981 | 480.5257 | 475.7945 | 477.3514 | 477.3514
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | Power Factor | 0.99431 | 0.99432 | 0.99425 | 0.99428 | 0.99417
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | ECC Rating (A) | 778 | 778 | 778 | 778 | 778
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | 50 POE Load (A) | 578.2284 | 591.6916 | 585.0052 | 588.0367 | 589.643
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | NCC Rating (A) | 459 | 459 | 459 | 459 | 459 | Urban | 70
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | 10 POE Load (A) | 157.7227 | 158.326 | 156.5164 | 157.7227 | 158.326
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | Power Factor | 0.96707 | 0.96743 | 0.96746 | 0.96772 | 0.96784
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | ECC Rating (A) | 522 | 522 | 522 | 522 | 522
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | 50 POE Load (A) | 233.0771 | 233.9863 | 232.168 | 233.9863 | 233.9863
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | NCC Rating (A) | 459 | 459 | 459 | 459 | 459 | Urban | 70
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | 10 POE Load (A) | 157.9008 | 158.5048 | 156.6931 | 157.9008 | 158.5048
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | Power Factor | 0.99912 | 0.99875 | 0.99871 | 0.99839 | 0.99823
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | ECC Rating (A) | 522 | 522 | 522 | 522 | 522
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | 50 POE Load (A) | 233.2087 | 234.1185 | 232.2992 | 234.1185 | 234.1185
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | 10 POE Load (A) | 303.1707 | 313.2442 | 310.3471 | 312.1959 | 312.1959
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | Power Factor | 0.99851 | 0.99845 | 0.99839 | 0.99841 | 0.9983
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | 50 POE Load (A) | 511.447 | 525.5174 | 520.2062 | 522.8555 | 524.6141
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | 10 POE Load (A) | 303.1707 | 313.2442 | 310.3471 | 312.1959 | 312.1959
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | Power Factor | 0.99851 | 0.99845 | 0.99839 | 0.99841 | 0.9983
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | 50 POE Load (A) | 511.447 | 525.5174 | 520.2062 | 522.8555 | 524.6141
Nudgee Bulk | 636-1 | Hendra | Clayfield | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
Nudgee Bulk | 636-1 | Hendra | Clayfield | 10 POE Load (A) | 113.7531 | 115.5174 | 114.6382 | 116.3898 | 116.3898
Nudgee Bulk | 636-1 | Hendra | Clayfield | Power Factor | 0.99329 | 0.99338 | 0.9933 | 0.99328 | 0.99318
Nudgee Bulk | 636-1 | Hendra | Clayfield | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
Nudgee Bulk | 636-1 | Hendra | Clayfield | 50 POE Load (A) | 220.1528 | 221.9649 | 221.9562 | 223.7449 | 225.5334
Nudgee Bulk | 643-1 | Hendra | Hamilton | NCC Rating (A) | 753 | 753 | 753 | 753 | 753 | Urban | 70
Nudgee Bulk | 643-1 | Hendra | Hamilton | 10 POE Load (A) | 135.8899 | 148.1101 | 146.3594 | 147.2353 | 147.2353
Nudgee Bulk | 643-1 | Hendra | Hamilton | Power Factor | 0.99766 | 0.99765 | 0.99756 | 0.99753 | 0.99742
Nudgee Bulk | 643-1 | Hendra | Hamilton | ECC Rating (A) | 805 | 805 | 805 | 805 | 805
Nudgee Bulk | 643-1 | Hendra | Hamilton | 50 POE Load (A) | 257.9986 | 283.0145 | 279.4253 | 281.2201 | 283.0147
Nudgee Bulk | 674-1 | Hendra | Hamilton | NCC Rating (A) | 753 | 753 | 753 | 753 | 753 | Urban | 70
Nudgee Bulk | 674-1 | Hendra | Hamilton | 10 POE Load (A) | 135.5932 | 147.7866 | 146.0397 | 146.9137 | 146.9137
Nudgee Bulk | 674-1 | Hendra | Hamilton | Power Factor | 0.99766 | 0.99765 | 0.99756 | 0.99753 | 0.99742
Nudgee Bulk | 674-1 | Hendra | Hamilton | ECC Rating (A) | 805 | 805 | 805 | 805 | 805
Nudgee Bulk | 674-1 | Hendra | Hamilton | 50 POE Load (A) | 258.0076 | 283.0265 | 279.4368 | 281.2319 | 283.0266
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | NCC Rating (A) | 488 | 488 | 488 | 488 | 488 | Urban | 70
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | 10 POE Load (A) | 153.966 | 154.558 | 152.7823 | 153.966 | 154.558
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | Power Factor | 0.95865 | 0.95917 | 0.95921 | 0.95959 | 0.95977
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | ECC Rating (A) | 488 | 488 | 488 | 488 | 488
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | 50 POE Load (A) | 228.1483 | 229.0415 | 227.2553 | 229.0415 | 229.0415
Nudgee Bulk | 684-1 | Nudgee BS | Geebung | NCC Rating (A) | [5 empty] | Urban | 70
Nudgee Bulk | 684-1 | Nudgee BS | Geebung | 10 POE Load (A)
Nudgee Bulk | 684-1 | Nudgee BS | Geebung | Power Factor | 0 | 0 | 0 | 0 | 0
Nudgee Bulk | 684-1 | Nudgee BS | Geebung | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
Nudgee Bulk | 684-1 | Nudgee BS | Geebung | 50 POE Load (A)
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | 10 POE Load (A) | 41.5231 | 41.5231 | 41.5231 | 41.5231 | 41.5231
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | Power Factor | 0.98154 | 0.98168 | 0.9817 | 0.98181 | 0.98179
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | 50 POE Load (A) | 38.0995 | 38.0995 | 38.0995 | 38.0995 | 38.0995
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | 10 POE Load (A) | 25.82 | 25.82 | 25.82 | 25.82 | 25.82
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | Power Factor | 0.99799 | 0.99799 | 0.99799 | 0.998 | 0.99802
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | 50 POE Load (A)
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | 10 POE Load (A) | 0.49454 | 0.49454 | 0.49469 | 0.49454 | 0.49454
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | Power Factor | 0.00011888 | 0.00011884 | 0.00011884 | 0.00011878 | 0.00011882
Raceview Bulk | 354-1 | Raceview BS | Roderick St | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Urban | 70
Raceview Bulk | 354-1 | Raceview BS | Roderick St | 10 POE Load (A) | 217.7621 | 221.5108 | 221.0611 | 224.8122 | 227.6008
Raceview Bulk | 354-1 | Raceview BS | Roderick St | Power Factor | 0.99571 | 0.99581 | 0.99575 | 0.99581 | 0.99571
Raceview Bulk | 354-1 | Raceview BS | Roderick St | ECC Rating (A) | 532 | 532 | 532 | 532 | 532
Raceview Bulk | 354-1 | Raceview BS | Roderick St | 50 POE Load (A) | 329.788 | 335.0406 | 335.0406 | 338.5445 | 342.0502
Raceview Bulk | 355-1 | Roderick St | Booval | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Raceview Bulk | 355-1 | Roderick St | Booval | 10 POE Load (A) | 122.9101 | 124.3819 | 123.1003 | 124.572 | 125.2707
Raceview Bulk | 355-1 | Roderick St | Booval | Power Factor | 0.98504 | 0.98512 | 0.98509 | 0.98511 | 0.98504
Raceview Bulk | 355-1 | Roderick St | Booval | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Raceview Bulk | 355-1 | Roderick St | Booval | 50 POE Load (A) | 331.6872 | 336.9453 | 336.9591 | 340.5222 | 344.0833
Raceview Bulk | 361-1 | Raceview BS | Booval | NCC Rating (A) | 870 | 870 | 870 | 870 | 870 | Urban | 70
Raceview Bulk | 361-1 | Raceview BS | Booval | 10 POE Load (A) | 241.6017 | 247.9413 | 251.3224 | 257.671 | 262.3288
Raceview Bulk | 361-1 | Raceview BS | Booval | Power Factor | 0.99309 | 0.99322 | 0.99317 | 0.9932 | 0.9931
Raceview Bulk | 361-1 | Raceview BS | Booval | ECC Rating (A) | 943 | 943 | 943 | 943 | 943
Raceview Bulk | 361-1 | Raceview BS | Booval | 50 POE Load (A) | 393.7158 | 402.3793 | 406.7121 | 417.5572 | 425.5158
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | NCC Rating (A) | 515 | 515 | 515 | 515 | 515 | Rural | 170
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | 10 POE Load (A) | 99.7545 | 100.6424 | 99.0705 | 104.0469 | 104.3724
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | Power Factor | 0.99748 | 0.99763 | 0.99756 | 0.99761 | 0.99711
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | ECC Rating (A) | 515 | 515 | 515 | 515 | 515
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | 50 POE Load (A) | 229.6289 | 235.4324 | 236.6655 | 250.1085 | 255.0054
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | 10 POE Load (A) | 30.9445 | 31.3615 | 30.6447 | 27.9803 | 27.922
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | Power Factor | 0.72576 | 0.71697 | 0.71041 | 0.70614 | 0.64004
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | 50 POE Load (A) | 112.793 | 118.3943 | 120.6566 | 132.5051 | 138.3363
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | 10 POE Load (A) | 123.8169 | 124.9358 | 122.7432 | 123.8826 | 123.9045
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | Power Factor | 0.97962 | 0.97989 | 0.97962 | 0.97979 | 0.9794
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | ECC Rating (A) | 400 | 400 | 400 | 400 | 400
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | 50 POE Load (A) | 217.2081 | 217.3097 | 215.1209 | 217.7308 | 215.7337
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | 10 POE Load (A) | 98.1244 | 98.9969 | 97.4437 | 102.1041 | 102.4056
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | Power Factor | 0.99913 | 0.99922 | 0.99917 | 0.9992 | 0.9989
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | 50 POE Load (A) | 218.2016 | 223.5869 | 224.6773 | 237.2012 | 241.6924
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | 10 POE Load (A) | 5.2869 | 5.1899 | 5.1945 | 5.4876 | 5.5188
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | Power Factor | 0.66407 | 0.61473 | 0.59338 | 0.56003 | 0.040821
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | 50 POE Load (A) | 114.3705 | 119.2828 | 121.2153 | 131.8918 | 136.8666
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Rural | 170
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | 10 POE Load (A) | 101.6373 | 102.5555 | 100.7643 | 101.9405 | 101.977
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | Power Factor | 1 | 1 | 1 | 1 | 1
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | 50 POE Load (A) | 225.8892 | 226.0082 | 223.5565 | 226.4715 | 224.2862
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | NCC Rating (A) | 760 | 760 | 760 | 760 | 760 | Urban | 70
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | 10 POE Load (A) | 247.9984 | 255.1451 | 259.4935 | 271.5253 | 279.6158
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | Power Factor | 0.9855 | 0.98586 | 0.98562 | 0.98568 | 0.9844
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | 50 POE Load (A) | 289.0938 | 297.3239 | 299.9961 | 315.2546 | 322.3154
Raceview Bulk | 3972-1 | Yamanto | Flinders | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Raceview Bulk | 3972-1 | Yamanto | Flinders | 10 POE Load (A) | 104.2973 | 104.6678 | 102.0031 | 107.3511 | 106.8736
Raceview Bulk | 3972-1 | Yamanto | Flinders | Power Factor | 0.94027 | 0.93931 | 0.93838 | 0.93812 | 0.93567
Raceview Bulk | 3972-1 | Yamanto | Flinders | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Raceview Bulk | 3972-1 | Yamanto | Flinders | 50 POE Load (A) | 156.0667 | 163.1145 | 169.1411 | 178.1992 | 188.7859
Raceview Bulk | 3980-1 | Kalbar | Boonah | NCC Rating (A) | 841 | 841 | 841 | 841 | 841 | Rural | 170
Raceview Bulk | 3980-1 | Kalbar | Boonah | 10 POE Load (A) | 55.7428 | 56.7335 | 55.7122 | 55.8346 | 55.8527
Raceview Bulk | 3980-1 | Kalbar | Boonah | Power Factor | 0.99943 | 0.99952 | 0.9995 | 0.99952 | 0.99948
Raceview Bulk | 3980-1 | Kalbar | Boonah | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Raceview Bulk | 3980-1 | Kalbar | Boonah | 50 POE Load (A) | 103.7897 | 103.8213 | 101.8718 | 103.9528 | 102.0779
Raceview Bulk | 401-1 | Kalbar | Boonah | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Raceview Bulk | 401-1 | Kalbar | Boonah | 10 POE Load (A) | 53.3207 | 54.2665 | 53.2859 | 53.4083 | 53.4255
Raceview Bulk | 401-1 | Kalbar | Boonah | Power Factor | 0.99857 | 0.99867 | 0.99864 | 0.99866 | 0.99861
Raceview Bulk | 401-1 | Kalbar | Boonah | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Raceview Bulk | 401-1 | Kalbar | Boonah | 50 POE Load (A) | 103.9623 | 103.994 | 102.0383 | 104.1263 | 102.2398
Raceview Bulk | 411-1 | Raceview BS | Booval | NCC Rating (A) | 618 | 618 | 618 | 618 | 618 | Urban | 70
Raceview Bulk | 411-1 | Raceview BS | Booval | 10 POE Load (A) | 204.4134 | 209.7889 | 212.6401 | 218.0129 | 221.9549
Raceview Bulk | 411-1 | Raceview BS | Booval | Power Factor | 0.99699 | 0.99706 | 0.99703 | 0.99705 | 0.99699
Raceview Bulk | 411-1 | Raceview BS | Booval | ECC Rating (A) | 943 | 943 | 943 | 943 | 943
Raceview Bulk | 411-1 | Raceview BS | Booval | 50 POE Load (A) | 382.227 | 390.649 | 394.8617 | 405.3973 | 413.1353
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 763 | 763 | 763 | 763 | 763 | Urban | 70
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | 10 POE Load (A) | 259.4279 | 266.4482 | 271.26 | 281.5476 | 289.0545
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | Power Factor | 0.99481 | 0.99468 | 0.99443 | 0.99432 | 0.99367
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | 50 POE Load (A) | 478.8483 | 493.5652 | 500.4436 | 520.6763 | 534.7478
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | NCC Rating (A) | 509 | 509 | 509 | 509 | 509 | Rural | 170
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | 10 POE Load (A) | 0.48565 | 0.48565 | 0.48565 | 0.48565 | 0.48565
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | Power Factor | 8.7901e-06 | 8.7906e-06 | 8.7906e-06 | 8.7908e-06 | 8.7904e-06
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 763 | 763 | 763 | 763 | 763 | Urban | 70
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | 10 POE Load (A) | 256.8197 | 263.7694 | 268.5326 | 278.7167 | 286.1481
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | Power Factor | 0.99484 | 0.9947 | 0.99446 | 0.99435 | 0.99369
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | 50 POE Load (A) | 478.7377 | 493.4517 | 500.329 | 520.558 | 534.6269
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | NCC Rating (A) | 476 | 476 | 476 | 476 | 476 | Rural | 170
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | 10 POE Load (A) | 0.62897 | 0.62897 | 0.62897 | 0.62897 | 0.62897
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | Power Factor | 1.6632e-05 | 1.6632e-05 | 1.6632e-05 | 1.6632e-05 | 1.6632e-05
Richlands Bulk | 3818-1 | Richlands BS | Wacol | NCC Rating (A) | 760 | 760 | 760 | 760 | 760 | Urban | 70
Richlands Bulk | 3818-1 | Richlands BS | Wacol | 10 POE Load (A) | 80.4483 | 80.4483 | 99.5266 | 99.9616 | 100.3967
Richlands Bulk | 3818-1 | Richlands BS | Wacol | Power Factor | 0.99241 | 0.99194 | 0.99195 | 0.99215 | 0.99214
Richlands Bulk | 3818-1 | Richlands BS | Wacol | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
Richlands Bulk | 3818-1 | Richlands BS | Wacol | 50 POE Load (A) | 155.991 | 156.8836 | 196.3142 | 197.2194 | 198.1249
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 475 | 475 | 475 | 475 | 475 | Urban | 70
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | 10 POE Load (A) | 182.6293 | 182.6293 | 180.837 | 181.733 | 181.733
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | Power Factor | 0.97522 | 0.97533 | 0.97524 | 0.97534 | 0.97528
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | ECC Rating (A) | 520 | 520 | 520 | 520 | 520
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | 50 POE Load (A) | 357.2959 | 358.9321 | 353.6322 | 355.4636 | 355.4636
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 475 | 475 | 475 | 475 | 475 | Urban | 70
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | 10 POE Load (A) | 183.7993 | 183.7993 | 181.9956 | 182.8973 | 182.8973
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | Power Factor | 0.97526 | 0.97537 | 0.97528 | 0.97539 | 0.97532
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | ECC Rating (A) | 520 | 520 | 520 | 520 | 520
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | 50 POE Load (A) | 357.2541 | 359.0868 | 353.5914 | 355.4223 | 355.4223
Richlands Bulk | 543-1 | Inala | 543 Tee1 | NCC Rating (A) | 894 | 894 | 894 | 894 | 894 | Urban | 70
Richlands Bulk | 543-1 | Inala | 543 Tee1 | 10 POE Load (A) | 2.9655 | 2.9654 | 2.9656 | 2.9654 | 2.9653
Richlands Bulk | 543-1 | Inala | 543 Tee1 | Power Factor | 8.3786e-05 | 8.3786e-05 | 8.3786e-05 | 8.3786e-05 | 8.3786e-05
Richlands Bulk | 543-1 | Inala | 543 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Richlands Bulk | 543-1 | Inala | 543 Tee1 | 50 POE Load (A) | 432.0875 | 432.1054 | 425.9303 | 428.0094 | 425.9829
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | 10 POE Load (A) | 0.20627 | 0.20627 | 0.20628 | 0.20627 | 0.20626
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | Power Factor | 7.5155e-06 | 7.5153e-06 | 7.5152e-06 | 7.5153e-06 | 7.5143e-06
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | 50 POE Load (A)
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | 10 POE Load (A) | 2.2014 | 2.2013 | 2.2015 | 2.2013 | 2.2013
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | Power Factor | 9.1011e-05 | 9.1011e-05 | 9.1011e-05 | 9.1011e-05 | 9.1011e-05
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | ECC Rating (A) | 855 | 855 | 855 | 855 | 855
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | 50 POE Load (A) | 432.3392 | 432.357 | 426.1793 | 428.2592 | 426.2318
Richlands Bulk | 616-1 | Richlands BS | Darra | NCC Rating (A) | 434 | 434 | 434 | 434 | 434 | Urban | 70
Richlands Bulk | 616-1 | Richlands BS | Darra | 10 POE Load (A) | 192.8218 | 194.0195 | 193.1885 | 194.2948 | 195.0377
Richlands Bulk | 616-1 | Richlands BS | Darra | Power Factor | 0.78432 | 0.77661 | 0.77563 | 0.77058 | 0.76972
Richlands Bulk | 616-1 | Richlands BS | Darra | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
Richlands Bulk | 616-1 | Richlands BS | Darra | 50 POE Load (A) | 294.0852 | 294.6486 | 293.933 | 296.3496 | 296.9201
Richlands Bulk | 617-1 | Richlands BS | Darra | NCC Rating (A) | 434 | 434 | 434 | 434 | 434 | Urban | 70
Richlands Bulk | 617-1 | Richlands BS | Darra | 10 POE Load (A) | 199.1768 | 200.416 | 199.5562 | 200.701 | 201.4697
Richlands Bulk | 617-1 | Richlands BS | Darra | Power Factor | 0.78483 | 0.77714 | 0.77615 | 0.77111 | 0.77026
Richlands Bulk | 617-1 | Richlands BS | Darra | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
Richlands Bulk | 617-1 | Richlands BS | Darra | 50 POE Load (A) | 298.2416 | 298.8137 | 298.0873 | 300.5408 | 301.12
Richlands Bulk | 618-1 | Richlands BS | Inala | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Richlands Bulk | 618-1 | Richlands BS | Inala | 10 POE Load (A) | 300.4945 | 301.5889 | 299.4004 | 301.5889 | 302.6836
Richlands Bulk | 618-1 | Richlands BS | Inala | Power Factor | 0.98859 | 0.98878 | 0.98855 | 0.98847 | 0.9882
Richlands Bulk | 618-1 | Richlands BS | Inala | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Richlands Bulk | 618-1 | Richlands BS | Inala | 50 POE Load (A) | 547.7673 | 548.8813 | 542.9104 | 546.3836 | 546.2508
Richlands Bulk | 619-1 | Richlands BS | Inala | NCC Rating (A) | 603 | 603 | 603 | 603 | 603 | Urban | 70
Richlands Bulk | 619-1 | Richlands BS | Inala | 10 POE Load (A) | 194.0678 | 194.7745 | 193.3612 | 194.7745 | 195.4814
Richlands Bulk | 619-1 | Richlands BS | Inala | Power Factor | 0.98887 | 0.98906 | 0.98883 | 0.98876 | 0.98849
Richlands Bulk | 619-1 | Richlands BS | Inala | ECC Rating (A) | 603 | 603 | 603 | 603 | 603
Richlands Bulk | 619-1 | Richlands BS | Inala | 50 POE Load (A) | 471.2025 | 473.0432 | 469.3627 | 473.0432 | 474.8847
Richlands Bulk | 620-1 | Richlands BS | Oxley | NCC Rating (A) | 342 | 342 | 342 | 342 | 342 | Urban | 70
Richlands Bulk | 620-1 | Richlands BS | Oxley | 10 POE Load (A) | 133.2947 | 134.1891 | 133.2947 | 134.1891 | 134.1891
Richlands Bulk | 620-1 | Richlands BS | Oxley | Power Factor | 0.97752 | 0.97782 | 0.97787 | 0.97802 | 0.97808
Richlands Bulk | 620-1 | Richlands BS | Oxley | ECC Rating (A) | 378 | 378 | 378 | 378 | 378
Richlands Bulk | 620-1 | Richlands BS | Oxley | 50 POE Load (A) | 251.6894 | 253.496 | 249.8839 | 251.6894 | 253.496
Richlands Bulk | 621-1 | Richlands BS | Oxley | NCC Rating (A) | 342 | 342 | 342 | 342 | 342 | Urban | 70
Richlands Bulk | 621-1 | Richlands BS | Oxley | 10 POE Load (A) | 126.8595 | 127.7107 | 126.8595 | 127.7107 | 127.7107
Richlands Bulk | 621-1 | Richlands BS | Oxley | Power Factor | 0.97347 | 0.9738 | 0.97385 | 0.97402 | 0.97409
Richlands Bulk | 621-1 | Richlands BS | Oxley | ECC Rating (A) | 378 | 378 | 378 | 378 | 378
Richlands Bulk | 621-1 | Richlands BS | Oxley | 50 POE Load (A) | 251.5512 | 253.3572 | 249.7464 | 251.5512 | 253.3572
Richlands Bulk | 641-1 | Darra | Jindalee | NCC Rating (A) | 744 | 744 | 744 | 744 | 744 | Urban | 70
Richlands Bulk | 641-1 | Darra | Jindalee | 10 POE Load (A) | 78.9696 | 79.8212 | 78.9698 | 78.9705 | 78.971
Richlands Bulk | 641-1 | Darra | Jindalee | Power Factor | 0.99693 | 0.99701 | 0.99687 | 0.99665 | 0.99655
Richlands Bulk | 641-1 | Darra | Jindalee | ECC Rating (A) | 826 | 826 | 826 | 826 | 826
Richlands Bulk | 641-1 | Darra | Jindalee | 50 POE Load (A) | 149.6028 | 149.6033 | 147.8664 | 149.6047 | 149.6052
Richlands Bulk | 642-1 | Darra | Jindalee | NCC Rating (A) | 744 | 744 | 744 | 744 | 744 | Urban | 70
Richlands Bulk | 642-1 | Darra | Jindalee | 10 POE Load (A) | 77.3392 | 78.1734 | 77.3395 | 77.3402 | 77.3407
Richlands Bulk | 642-1 | Darra | Jindalee | Power Factor | 0.99645 | 0.99653 | 0.99656 | 0.9966 | 0.99662
Richlands Bulk | 642-1 | Darra | Jindalee | ECC Rating (A) | 826 | 826 | 826 | 826 | 826
Richlands Bulk | 642-1 | Darra | Jindalee | 50 POE Load (A) | 149.5908 | 149.5912 | 147.8544 | 149.5927 | 149.5932
Richlands Bulk | 679-1 | Richlands BS | Wacol | NCC Rating (A) | 663 | 663 | 663 | 663 | 663 | Urban | 70
Richlands Bulk | 679-1 | Richlands BS | Wacol | 10 POE Load (A) | 81.5196 | 81.5196 | 100.8544 | 101.2953 | 101.7362
Richlands Bulk | 679-1 | Richlands BS | Wacol | Power Factor | 0.96537 | 0.96514 | 0.96514 | 0.96524 | 0.96523
Richlands Bulk | 679-1 | Richlands BS | Wacol | ECC Rating (A) | 663 | 663 | 663 | 663 | 663
Richlands Bulk | 679-1 | Richlands BS | Wacol | 50 POE Load (A) | 155.9861 | 156.8785 | 196.297 | 197.2018 | 198.107
Richlands Bulk | 680-1 | Richlands BS | Wacol | NCC Rating (A) | 760 | 760 | 760 | 760 | 760 | Urban | 70
Richlands Bulk | 680-1 | Richlands BS | Wacol | 10 POE Load (A) | 163.8802 | 163.8802 | 203.4211 | 204.3294 | 205.2381
Richlands Bulk | 680-1 | Richlands BS | Wacol | Power Factor | 0.97454 | 0.97382 | 0.97384 | 0.97414 | 0.97413
Richlands Bulk | 680-1 | Richlands BS | Wacol | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
Richlands Bulk | 680-1 | Richlands BS | Wacol | 50 POE Load (A)
Richlands Bulk | 700-1 | Richlands BS | Darra | NCC Rating (A) | 551 | 551 | 551 | 551 | 551 | Urban | 70
Richlands Bulk | 700-1 | Richlands BS | Darra | 10 POE Load (A) | 152.5527 | 153.4983 | 152.842 | 153.7152 | 154.3014
Richlands Bulk | 700-1 | Richlands BS | Darra | Power Factor | 0.83089 | 0.82396 | 0.82307 | 0.81852 | 0.81774
Richlands Bulk | 700-1 | Richlands BS | Darra | ECC Rating (A) | 551 | 551 | 551 | 551 | 551
Richlands Bulk | 700-1 | Richlands BS | Darra | 50 POE Load (A) | 232.6991 | 233.1442 | 232.5785 | 234.4877 | 234.9383
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | NCC Rating (A) | 601 | 601 | 601 | 601 | 601 | Urban | 70
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | 10 POE Load (A) | 342.1135 | 343.5903 | 340.6369 | 342.1135 | 343.5903
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | Power Factor | 0.98176 | 0.98105 | 0.98103 | 0.98115 | 0.98116
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | ECC Rating (A) | 601 | 601 | 601 | 601 | 601
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | 50 POE Load (A) | 402.6792 | 404.4624 | 399.114 | 402.6792 | 402.6792
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | NCC Rating (A) | 450 | 450 | 450 | 450 | 450 | Urban | 70
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | 10 POE Load (A) | 2.354 | 2.354 | 2.354 | 2.354 | 2.354
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | Power Factor | 4.0608e-05 | 4.0608e-05 | 4.0608e-05 | 4.0608e-05 | 4.0608e-05
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | ECC Rating (A) | 450 | 450 | 450 | 450 | 450
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | 50 POE Load (A)
Runcorn Bulk | 434-1 | Runcorn | Calamvale | NCC Rating (A) | 450 | 450 | 450 | 450 | 450 | Urban | 70
Runcorn Bulk | 434-1 | Runcorn | Calamvale | 10 POE Load (A) | 1.6802 | 1.6802 | 1.6803 | 1.6802 | 1.6802
Runcorn Bulk | 434-1 | Runcorn | Calamvale | Power Factor | 6.272e-05 | 6.272e-05 | 6.272e-05 | 6.272e-05 | 6.272e-05
Runcorn Bulk | 434-1 | Runcorn | Calamvale | ECC Rating (A) | 450 | 450 | 450 | 450 | 450
Runcorn Bulk | 434-1 | Runcorn | Calamvale | 50 POE Load (A)
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | NCC Rating (A) | [5 empty] | Urban | 70
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | 10 POE Load (A)
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | Power Factor | 0 | 0 | 0 | 0 | 0
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | ECC Rating (A) | 818 | 818 | 0 | 0 | 0
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | 50 POE Load (A)
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | NCC Rating (A) | [5 empty] | Urban | 70
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | 10 POE Load (A)
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | Power Factor | 0 | 0 | 0 | 0 | 0
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | ECC Rating (A) | 848 | 848 | 0 | 0 | 0
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | 50 POE Load (A)
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 453 | 453 | 453 | 453 | 453 | Urban | 70
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | 10 POE Load (A) | 27.7124 | 27.7124 | 27.7124 | 27.7124 | 27.7124
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | Power Factor | 9.2863e-05 | 9.2863e-05 | 9.2863e-05 | 9.2863e-05 | 9.2863e-05
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | ECC Rating (A) | 453 | 453 | 453 | 453 | 453
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | 50 POE Load (A)
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 453 | 453 | 453 | 453 | 453 | Urban | 70
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | 10 POE Load (A) | 27.8479 | 27.8479 | 27.8479 | 27.8479 | 27.8479
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | Power Factor | 1 | 1 | 1 | 1 | 1
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | ECC Rating (A) | 453 | 453 | 453 | 453 | 453
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | 50 POE Load (A)
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | 10 POE Load (A) | 194.1106 | 194.1106 | 192.1642 | 193.1373 | 192.1642
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | Power Factor | 0.99389 | 0.99392 | 0.99386 | 0.99386 | 0.99372
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | 50 POE Load (A) | 332.9021 | 332.9021 | 329.401 | 331.1514 | 329.401
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | NCC Rating (A) | 685 | 685 | 685 | 685 | 685 | Urban | 70
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | 10 POE Load (A) | 153.6128 | 153.6128 | 152.0724 | 152.8425 | 152.0724
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | Power Factor | 0.99416 | 0.99419 | 0.99412 | 0.99413 | 0.99399
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | 50 POE Load (A) | 333.4244 | 333.4244 | 329.9112 | 331.6676 | 329.9112
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | NCC Rating (A) | 581 | 581 | 581 | 581 | 581 | Urban | 70
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | 10 POE Load (A) | 202.1946 | 203.9535 | 273.1327 | 274.9227 | 276.7136
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | Power Factor | 0.99987 | 0.99996 | 0.99996 | 0.99996 | 0.99994
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | ECC Rating (A) | 581 | 581 | 581 | 581 | 581
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | 50 POE Load (A) | 395.4356 | 399.1271 | 566.4182 | 570.3328 | 572.3035
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Urban | 70
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | 10 POE Load (A) | 51.7243 | 51.7243 | 50.8732 | 50.8732 | 50.8732
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | Power Factor | 1 | 1 | 1 | 1 | 1
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | 50 POE Load (A) | 97.2494 | 97.2494 | 97.2494 | 97.2494 | 97.2494
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Urban | 70
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | 10 POE Load (A) | 218.1807 | 218.9751 | 215.7996 | 215.7996 | 215.7996
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | Power Factor | 0.98023 | 0.98057 | 0.98043 | 0.98064 | 0.98028
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | 50 POE Load (A) | 296.5065 | 296.5065 | 291.9225 | 293.0678 | 291.9225
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | NCC Rating (A) | 521 | 521 | 521 | 521 | 521 | Urban | 70
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | 10 POE Load (A) | 146.9439 | 147.4765 | 145.3476 | 145.3476 | 145.3476
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | Power Factor | 0.99131 | 0.99155 | 0.99145 | 0.9916 | 0.99135
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | ECC Rating (A) | 521 | 521 | 521 | 521 | 521
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | 50 POE Load (A) | 250.1483 | 250.1483 | 246.2694 | 247.2383 | 246.2694
Sandgate Bulk | 524-2 | Geebung | Zillmere | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70
Sandgate Bulk | 524-2 | Geebung | Zillmere | 10 POE Load (A) | 151.517 | 152.0471 | 149.8829 | 149.8829 | 149.8829
Sandgate Bulk | 524-2 | Geebung | Zillmere | Power Factor | 0.99808 | 0.99819 | 0.99814 | 0.99821 | 0.9981
Sandgate Bulk | 524-2 | Geebung | Zillmere | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
Sandgate Bulk | 524-2 | Geebung | Zillmere | 50 POE Load (A) | 254.5849 | 254.5849 | 250.6409 | 251.6262 | 250.6409
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | 10 POE Load (A) | 82.4161 | 82.4161 | 81.5312 | 81.5312 | 81.5312
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | Power Factor | 0.9963 | 0.99636 | 0.99636 | 0.99639 | 0.99636
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | ECC Rating (A) | 841 | 841 | 841 | 841 | 841
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | 50 POE Load (A) | 150.1403 | 150.1403 | 148.412 | 148.412 | 148.412
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | NCC Rating (A) | 379 | 379 | 379 | 379 | 379 | Urban | 70
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | 10 POE Load (A) | 79.0816 | 79.0816 | 78.2439 | 78.2439 | 78.2439
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | Power Factor | 0.99999 | 0.99999 | 0.99999 | 1 | 0.99999
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | ECC Rating (A) | 379 | 379 | 379 | 379 | 379
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | 50 POE Load (A) | 151.262 | 151.262 | 149.5076 | 149.5076 | 149.5076
Sandgate Bulk | 664-1 | Geebung | Zillmere | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70
Sandgate Bulk | 664-1 | Geebung | Zillmere | 10 POE Load (A) | 24.9695 | 24.9683 | 24.973 | 24.9718 | 24.973
Sandgate Bulk | 664-1 | Geebung | Zillmere | Power Factor | 1 | 1 | 1 | 1 | 1
Sandgate Bulk | 664-1 | Geebung | Zillmere | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
Sandgate Bulk | 664-1 | Geebung | Zillmere | 50 POE Load (A)
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | 10 POE Load (A) | 128.6864 | 129.1544 | 127.3063 | 127.3063 | 127.3063
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | Power Factor | 1 | 1 | 1 | 0.99999 | 1
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | ECC Rating (A) | 495 | 599 | 599 | 599 | 599
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | 50 POE Load (A) | 219.0828 | 219.0828 | 215.6794 | 216.5295 | 215.6794
Stafford Bulk | 502-1 | Kedron | Clayfield | NCC Rating (A) | [5 empty] | Urban | 70
Stafford Bulk | 502-1 | Kedron | Clayfield | 10 POE Load (A)
Stafford Bulk | 502-1 | Kedron | Clayfield | Power Factor | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 502-1 | Kedron | Clayfield | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 502-1 | Kedron | Clayfield | 50 POE Load (A)
Stafford Bulk | 522-1 | Kedron | Chermside | NCC Rating (A) | [5 empty] | Urban | 70
Stafford Bulk | 522-1 | Kedron | Chermside | 10 POE Load (A)
Stafford Bulk | 522-1 | Kedron | Chermside | Power Factor | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 525-1 | Chermside | Zillmere | NCC Rating (A) | [5 empty] | Urban | 70
Stafford Bulk | 525-1 | Chermside | Zillmere | 10 POE Load (A)
Stafford Bulk | 525-1 | Chermside | Zillmere | Power Factor | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 534-1 | Kedron | Clayfield | NCC Rating (A) | [5 empty] | Urban | 70
Stafford Bulk | 534-1 | Kedron | Clayfield | 10 POE Load (A)
Stafford Bulk | 534-1 | Kedron | Clayfield | Power Factor | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 534-1 | Kedron | Clayfield | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 534-1 | Kedron | Clayfield | 50 POE Load (A)
Stafford Bulk | 548-1 | Stafford BS | Enoggera | NCC Rating (A) | 886 | 886 | 886 | 886 | 886 | Urban | 170
Stafford Bulk | 548-1 | Stafford BS | Enoggera | 10 POE Load (A) | 440.1203 | 440.1171 | 436.6176 | 438.3657 | 437.4903
Stafford Bulk | 548-1 | Stafford BS | Enoggera | Power Factor | 0.99158 | 0.99166 | 0.99165 | 0.99167 | 0.99165
Stafford Bulk | 548-1 | Stafford BS | Enoggera | ECC Rating (A) | 1020 | 1020 | 1020 | 1020 | 1020
Stafford Bulk | 548-1 | Stafford BS | Enoggera | 50 POE Load (A) | 834.9281 | 836.6805 | 827.8983 | 831.4091 | 831.4023
Stafford Bulk | 550-1 | Stafford BS | Chermside | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70
Stafford Bulk | 550-1 | Stafford BS | Chermside | 10 POE Load (A) | 249.2609 | 250.1403 | 247.483 | 248.3621 | 248.3621
Stafford Bulk | 550-1 | Stafford BS | Chermside | Power Factor | 0.99234 | 0.99826 | 0.9983 | 0.99836 | 0.99834
Stafford Bulk | 550-1 | Stafford BS | Chermside | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Stafford Bulk | 550-1 | Stafford BS | Chermside | 50 POE Load (A) | 478.2671 | 480.031 | 474.701 | 476.4641 | 476.4641
Stafford Bulk | 551-1 | Stafford BS | Chermside | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70
Stafford Bulk | 551-1 | Stafford BS | Chermside | 10 POE Load (A) | 248.786 | 249.6637 | 247.0115 | 247.8889 | 247.8889
Stafford Bulk | 551-1 | Stafford BS | Chermside | Power Factor | 0.99235 | 0.99826 | 0.99831 | 0.99837 | 0.99835
Stafford Bulk | 551-1 | Stafford BS | Chermside | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Stafford Bulk | 551-1 | Stafford BS | Chermside | 50 POE Load (A) | 478.2721 | 480.0361 | 474.7059 | 476.4691 | 476.4691
Stafford Bulk | 567-1 | Stafford BS | Kedron | NCC Rating (A) | 613 | 613 | 613 | 613 | 613 | Urban | 70
Stafford Bulk | 567-1 | Stafford BS | Kedron | 10 POE Load (A) | 213.7085 | 225.0155 | 223.2742 | 224.1447 | 224.1447
Stafford Bulk | 567-1 | Stafford BS | Kedron | Power Factor | 0.99996 | 0.99997 | 0.9998 | 0.99981 | 0.99977
Stafford Bulk | 567-1 | Stafford BS | Kedron | ECC Rating (A) | 685 | 685 | 685 | 685 | 685
Stafford Bulk | 567-1 | Stafford BS | Kedron | 50 POE Load (A) | 402.2023 | 426.7163 | 421.4578 | 424.9631 | 424.9631
Stafford Bulk | 568-1 | Stafford BS | Kedron | NCC Rating (A) | 613 | 613 | 613 | 613 | 613 | Urban | 70
Stafford Bulk | 568-1 | Stafford BS | Kedron | 10 POE Load (A) | 215.3456 | 226.7386 | 224.984 | 225.8612 | 225.8612
Stafford Bulk | 568-1 | Stafford BS | Kedron | Power Factor | 0.99292 | 0.99297 | 0.99229 | 0.99231 | 0.99218
Stafford Bulk | 568-1 | Stafford BS | Kedron | ECC Rating (A) | 685 | 685 | 685 | 685 | 685
Stafford Bulk | 568-1 | Stafford BS | Kedron | 50 POE Load (A) | 402.1821 | 426.6935 | 421.4356 | 424.9405 | 424.9405
Stafford Bulk | 594-1 | Stafford BS | Enoggera | NCC Rating (A) | 886 | 886 | 886 | 886 | 886 | Urban | 70
Stafford Bulk | 594-1 | Stafford BS | Enoggera | 10 POE Load (A) | 437.3457 | 437.3425 | 433.8651 | 435.6022 | 434.7322
Stafford Bulk | 594-1 | Stafford BS | Enoggera | Power Factor | 0.9916 | 0.99168 | 0.99167 | 0.99169 | 0.99167
Stafford Bulk | 594-1 | Stafford BS | Enoggera | ECC Rating (A) | 1020 | 1020 | 1020 | 1020 | 1020
Stafford Bulk | 594-1 | Stafford BS | Enoggera | 50 POE Load (A) | 834.9709 | 836.7236 | 827.9403 | 831.4515 | 831.4447
Stafford Bulk | 595-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
Stafford Bulk | 595-1 | Enoggera | Grovely | 10 POE Load (A) | 161.6981 | 160.8343 | 158.2371 | 159.1038 | 158.2387
Stafford Bulk | 595-1 | Enoggera | Grovely | Power Factor | 0.9987 | 0.99887 | 0.99888 | 0.99892 | 0.99889
Stafford Bulk | 595-1 | Enoggera | Grovely | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
Stafford Bulk | 595-1 | Enoggera | Grovely | 50 POE Load (A) | 307.4967 | 307.4999 | 302.1112 | 303.9074 | 302.1174
Stafford Bulk | 596-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
Stafford Bulk | 596-1 | Enoggera | Grovely | 10 POE Load (A) | 162.7837 | 161.9141 | 159.2994 | 160.1719 | 159.3011
Stafford Bulk | 596-1 | Enoggera | Grovely | Power Factor | 0.99867 | 0.99885 | 0.99885 | 0.99889 | 0.99887
Stafford Bulk | 596-1 | Enoggera | Grovely | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
Stafford Bulk | 596-1 | Enoggera | Grovely | 50 POE Load (A) | 307.4416 | 307.4447 | 302.0589 | 303.8542 | 302.0652
Stafford Bulk | 607-1 | Chermside | Zillmere | NCC Rating (A) | 332 | 332 |  |  |  | Urban | 70
Stafford Bulk | 607-1 | Chermside | Zillmere | 10 POE Load (A) | 0.21114 | 0.21114
Stafford Bulk | 607-1 | Chermside | Zillmere | Power Factor | 4.7374e-06 | 4.7372e-06 | 1.3215e-05 | 1.3215e-05 | 1.3215e-05
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | 10 POE Load (A) | 501.971 | 550.7059 | 542.1015 | 546.8294 | 544.5462
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | Power Factor | 0.98906 | 0.98916 | 0.98705 | 0.98707 | 0.98676
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | 50 POE Load (A)
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | 10 POE Load (A) | 501.971 | 550.7324 | 542.1015 | 546.8294 | 544.5731
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | Power Factor | 0.99192 | 0.99199 | 0.99059 | 0.99061 | 0.99039
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | 50 POE Load (A)
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | 10 POE Load (A) | 0.0016505 | 0.0016425 | 0.0016438 | 0.0016434 | 0.0016438
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | Power Factor | 1 | 1 | 1 | 1 | 1
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | NCC Rating (A) | 888 | 888 | 888 | 888 | 888 | Urban | 70
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | 10 POE Load (A) | 720.05 | 770.2077 | 759.4151 | 766.2411 | 763.8892
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | Power Factor | 0.00040897 | 0.00040879 | 0.00040913 | 0.00040916 | 0.00040902
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | 50 POE Load (A)
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | 10 POE Load (A) | 720.1575 | 770.3225 | 759.5295 | 766.3564 | 764.0042
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | Power Factor | 0.98363 | 0.98379 | 0.98102 | 0.98103 | 0.9805
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | 50 POE Load (A)
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | 10 POE Load (A) | 382.014 | 380.7844 | 374.3314 | 375.7586 | 373.4418
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | Power Factor | 0.98558 | 0.9862 | 0.98945 | 0.9896 | 0.98959
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | 50 POE Load (A) | 608.755 | 606.4675 | 598.0981 | 598.0981 | 594.48
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | 10 POE Load (A) | 143.8831 | 143.1728 | 140.6042 | 140.1215 | 139.7182
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | Power Factor | 0.98248 | 0.98351 | 0.98184 | 0.98213 | 0.98226
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | 50 POE Load (A) | 389.0288 | 387.2113 | 381.7764 | 381.7764 | 378.1712
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | 10 POE Load (A) | 238.1564 | 237.7023 | 233.8167 | 235.7261 | 233.8168
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | Power Factor | 0.99405 | 0.99426 | 0.9972 | 0.9972 | 0.99715
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | 50 POE Load (A) | 219.8322 | 219.3683 | 216.4338 | 216.4338 | 216.4181
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | NCC Rating (A) | 1108 | 1108 | 1108 | 1108 | 1108 | Urban | 70
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | 10 POE Load (A) | 267.004 | 265.9885 | 261.4099 | 261.8994 | 260.5139
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | Power Factor | 0.98291 | 0.9838 | 0.98537 | 0.9856 | 0.98564
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | 50 POE Load (A) | 387.5814 | 385.7835 | 380.3937 | 380.3937 | 376.8037
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | 10 POE Load (A) | 267.0177 | 266.0022 | 261.4234 | 261.9129 | 260.5274
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | Power Factor | 0.98548 | 0.98617 | 0.98783 | 0.98801 | 0.98805
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | 50 POE Load (A) | 387.5951 | 385.7972 | 380.4073 | 380.4073 | 376.8171
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | 10 POE Load (A) | 0.00064377 | 0.00064377 | 0.00064377 | 0.00064377 | 0.00064377
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | Power Factor | 0.0003073 | 0.00030692 | 0.00030662 | 0.00030718 | 0.00030691
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | 10 POE Load (A) | 115.8899 | 115.4399 | 113.4744 | 113.5234 | 113.4723
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | Power Factor | 0.99167 | 0.99204 | 0.99882 | 0.9988 | 0.99873
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | 50 POE Load (A) | 106.6169 | 106.1563 | 103.3038 | 103.3038 | 103.2962
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | 10 POE Load (A) | 115.9047 | 115.454 | 113.4884 | 113.5374 | 113.4863
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | Power Factor | 0.99148 | 0.99183 | 0.99847 | 0.99845 | 0.99838
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | 50 POE Load (A) | 106.6314 | 106.1698 | 103.3172 | 103.3172 | 103.3096
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | 10 POE Load (A) | 39.7588 | 39.2655 | 39.2251 | 39.242 | 39.2244
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | Power Factor | 0.97018 | 0.97006 | 1.5722e-05 | 1.5722e-05 | 1.5722e-05
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | 50 POE Load (A) | 37.9084 | 37.3958 | 36.4403 | 36.4403 | 36.4376
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | 10 POE Load (A) | 76.4467 | 76.4496 | 74.5281 | 74.5298 | 74.5267
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | Power Factor | 0.99791 | 0.99811 | 0.99815 | 0.99813 | 0.99805
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | ECC Rating (A) | 293 | 490 | 490 | 490 | 490
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | 50 POE Load (A) | 69.0668 | 69.0382 | 67.1388 | 67.1388 | 67.1339
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | NCC Rating (A) | 468 | 468 | 468 | 468 | 468 | Rural | 170
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | 10 POE Load (A) | 76.5757 | 76.5476 | 74.6245 | 74.6567 | 74.6231
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | Power Factor | 0.99721 | 0.99725 | 0.9972 | 0.99718 | 0.99712
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | 50 POE Load (A) | 69.1586 | 69.13 | 67.229 | 67.229 | 67.2241
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | 10 POE Load (A) | 1.0406 | 1.041 | 1.0414 | 1.0411 | 1.0415
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | Power Factor | 1.4325e-06 | 1.4325e-06 | 1.4325e-06 | 1.4325e-06 | 1.4326e-06
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | ECC Rating (A) | 293 | 582 | 582 | 582 | 582
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | 50 POE Load (A)
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | NCC Rating (A) | 779 | 779 | 779 | 779 | 779 | Urban | 70
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | 10 POE Load (A) | 92.6606 | 90.7045 | 89.1662 | 89.0013 | 88.464
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | Power Factor | 0.9991 | 0.99949 | 0.9996 | 0.9997 | 0.99968
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | ECC Rating (A) | 779 | 779 | 779 | 779 | 779
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | 50 POE Load (A) | 125.6942 | 122.4701 | 120.2847 | 120.4431 | 120.022
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | NCC Rating (A) | 640 | 640 | 640 | 640 | 640 | Urban | 70
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | 10 POE Load (A) | 94.473 | 94.5956 | 93.6796 | 93.7053 | 93.669
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | Power Factor | 0.99006 | 0.98957 | 0.98962 | 0.98985 | 0.98983
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | 50 POE Load (A) | 184.6371 | 184.6371 | 182.8367 | 183.7367 | 182.8367
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | NCC Rating (A) | 640 | 640 | 640 | 640 | 640 | Urban | 70
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | 10 POE Load (A) | 191.5845 | 191.5845 | 189.7788 | 189.7788 | 189.7788
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | Power Factor | 0.97198 | 0.97147 | 0.97166 | 0.97203 | 0.97204
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | 50 POE Load (A)
Tennyson Bulk | 3460-1 | Annerley | Buranda | NCC Rating (A) | 859 | 859 | 859 | 859 | 859 | Urban | 70
Tennyson Bulk | 3460-1 | Annerley | Buranda | 10 POE Load (A) | 128.7772 | 179.9827 | 179.1074 | 180.8582 | 182.6081
Tennyson Bulk | 3460-1 | Annerley | Buranda | Power Factor | 0.99505 | 0.99637 | 0.99304 | 0.99307 | 0.99299
Tennyson Bulk | 3460-1 | Annerley | Buranda | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 3460-1 | Annerley | Buranda | 50 POE Load (A) | 244.1055 | 346.6082 | 344.8591 | 348.361 | 351.8648
Tennyson Bulk | 3461-1 | Annerley | Buranda | NCC Rating (A) | 859 | 859 | 859 | 859 | 859 | Urban | 70
Tennyson Bulk | 3461-1 | Annerley | Buranda | 10 POE Load (A) | 128.9752 | 180.2596 | 179.383 | 181.1364 | 182.889
Tennyson Bulk | 3461-1 | Annerley | Buranda | Power Factor | 0.99506 | 0.99637 | 0.99304 | 0.99308 | 0.99299
Tennyson Bulk | 3461-1 | Annerley | Buranda | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 3461-1 | Annerley | Buranda | 50 POE Load (A) | 244.1051 | 346.6073 | 344.8582 | 348.3601 | 351.8639
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | NCC Rating (A) | 425 | 425 | 425 | 425 | 425 | Urban | 70
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | 10 POE Load (A) | 170.3691 | 171.7604 | 169.5279 | 169.1741 | 168.6646
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | Power Factor | 0.99999 | 1 | 1 | 0.99999 | 0.99999
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | ECC Rating (A) | 480 | 480 | 480 | 480 | 480
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | 50 POE Load (A) | 264.9378 | 267.6383 | 263.0878 | 264.2863 | 263.0518
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | NCC Rating (A) | 774 | 774 | 774 | 774 | 774 | Urban | 70
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | 10 POE Load (A) | 296.7313 | 297.4248 | 293.4048 | 293.4889 | 292.1533
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | Power Factor | 0.99792 | 0.99819 | 0.99823 | 0.99833 | 0.99828
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | 50 POE Load (A) | 394.4098 | 395.6263 | 389.0955 | 390.5532 | 388.4304
Tennyson Bulk | 480-1 | Taringa | St Lucia | NCC Rating (A) | 640 | 640 | 640 | 640 | 640 | Urban | 70
Tennyson Bulk | 480-1 | Taringa | St Lucia | 10 POE Load (A) | 94.1537 | 94.0368 | 93.2109 | 93.1865 | 93.221
Tennyson Bulk | 480-1 | Taringa | St Lucia | Power Factor | 0.969 | 0.96855 | 0.96865 | 0.96875 | 0.96877
Tennyson Bulk | 480-1 | Taringa | St Lucia | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
Tennyson Bulk | 480-1 | Taringa | St Lucia | 50 POE Load (A) | 184.0238 | 184.0343 | 182.244 | 183.1346 | 182.2421
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | 10 POE Load (A) | 236.6402 | 240.5669 | 237.7711 | 237.8356 | 237.0841
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | Power Factor | 0.99563 | 0.99582 | 0.99583 | 0.99597 | 0.99593
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | 50 POE Load (A) | 341.0667 | 348.0188 | 342.4945 | 344.2888 | 342.225
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Urban | 70
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | 10 POE Load (A) | 94.6018 | 92.5991 | 91.0247 | 90.8559 | 90.306
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | Power Factor | 0.99412 | 0.9948 | 0.99487 | 0.99508 | 0.99503
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | ECC Rating (A) | 917 | 917 | 917 | 917 | 917
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | 50 POE Load (A) | 126.853 | 123.5845 | 121.3735 | 121.5332 | 121.1079
Tennyson Bulk | 507B-1 | Toowong | Taringa | NCC Rating (A) | 783 | 783 | 783 | 783 | 783 | Urban | 70
Tennyson Bulk | 507B-1 | Toowong | Taringa | 10 POE Load (A) | 93.4837 | 91.4702 | 89.9082 | 89.7422 | 89.1958
Tennyson Bulk | 507B-1 | Toowong | Taringa | Power Factor | 0.99966 | 0.99988 | 0.99993 | 0.99997 | 0.99996
Tennyson Bulk | 507B-1 | Toowong | Taringa | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 507B-1 | Toowong | Taringa | 50 POE Load (A) | 125.7839 | 122.5036 | 120.3048 | 120.4612 | 120.0411
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | NCC Rating (A) | 801 | 801 | 801 | 801 | 801 | Urban | 70
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | 10 POE Load (A) | 132.9914 | 133.8557 | 140.7774 | 142.5098 | 143.3763
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | Power Factor | 0.97858 | 0.9785 | 0.97832 | 0.97823 | 0.97801
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | ECC Rating (A) | 816 | 816 | 816 | 816 | 816
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | 50 POE Load (A) | 244.3908 | 246.1217 | 259.9832 | 263.4526 | 265.1878
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | NCC Rating (A) | 801 | 801 | 801 | 801 | 801 | Urban | 70
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | 10 POE Load (A) | 133.7627 | 134.6321 | 141.594 | 143.3365 | 144.208
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | Power Factor | 0.98083 | 0.98074 | 0.98053 | 0.98043 | 0.98017
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | 50 POE Load (A) | 244.3893 | 246.1201 | 259.9814 | 263.4507 | 265.186
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | NCC Rating (A) | 768 | 768 | 768 | 768 | 768 | Urban | 70
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | 10 POE Load (A) | 314.848 | 315.5827 | 311.3136 | 311.4031 | 309.9844
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | Power Factor | 0.99894 | 0.99913 | 0.99916 | 0.99923 | 0.9992
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | ECC Rating (A) | 797 | 797 | 797 | 797 | 797
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | 50 POE Load (A) | 418.4398 | 419.729 | 412.7963 | 414.3435 | 412.0899
Tennyson Bulk | 523A&B-1 | Tennyson BS | Rocklea | NCC Rating (A) | [5 empty] | Urban | 70
Tennyson Bulk | 523A&B-1 | Tennyson BS | Rocklea | 10 POE Load (A)
Tennyson Bulk | 523A&B-1 | Tennyson BS | Rocklea | Power Factor | 0 | 0 | 0 | 0 | 0
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | 10 POE Load (A) | 7.7883 | 7.7883 | 7.7883 | 7.7883 | 7.7883
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | Power Factor | 1.0729e-05 | 1.0729e-05 | 1.0729e-05 | 1.0729e-05 | 1.0729e-05
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | ECC Rating (A) | 0 | 688 | 688 | 688 | 688
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | 50 POE Load (A)
Tennyson Bulk | 539-1 | Sherwood | Kenmore | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 340
Tennyson Bulk | 539-1 | Sherwood | Kenmore | 10 POE Load (A) | 210.4331 | 209.8382 | 206.727 | 205.9715 | 204.4756
Tennyson Bulk | 539-1 | Sherwood | Kenmore | Power Factor | 0.99727 | 0.99757 | 0.99767 | 0.99779 | 0.99777
Tennyson Bulk | 539-1 | Sherwood | Kenmore | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Tennyson Bulk | 539-1 | Sherwood | Kenmore | 50 POE Load (A) | 461.0708 | 459.1838 | 449.7313 | 449.7341 | 446.1952
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | NCC Rating (A) | 768 | 768 | 768 | 768 | 768 | Urban | 70
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | 10 POE Load (A) | 333.7644 | 334.5432 | 330.0191 | 330.1138 | 328.6104
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | Power Factor | 0.99826 | 0.9985 | 0.99853 | 0.99862 | 0.99858
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | 50 POE Load (A) | 433.1497 | 434.4843 | 427.3098 | 428.911 | 426.5788
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | 10 POE Load (A) | 274.3941 | 273.1945 | 269.0723 | 268.0288 | 265.9196
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | Power Factor | 0.99043 | 0.99099 | 0.99119 | 0.99141 | 0.99138
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | 50 POE Load (A) | 455.923 | 454.0991 | 444.888 | 444.8983 | 441.2247
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | 10 POE Load (A) | 237.7578 | 241.7031 | 238.8941 | 238.959 | 238.204
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | Power Factor | 0.99932 | 0.99938 | 0.99935 | 0.99941 | 0.99939
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | 50 POE Load (A) | 341.8153 | 348.7827 | 343.2463 | 345.0445 | 342.9762
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | NCC Rating (A) | 765 | 765 | 765 | 765 | 765 | Urban | 70
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | 10 POE Load (A) | 255.2825 | 305.5406 | 304.6685 | 309.0169 | 310.7557
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | Power Factor | 0.99757 | 0.99826 | 0.99634 | 0.99635 | 0.99625
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | 50 POE Load (A) | 481.5295 | 582.6558 | 580.8997 | 586.1543 | 589.6539
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | NCC Rating (A) | 765 | 765 | 765 | 765 | 765 | Urban | 70
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | 10 POE Load (A) | 256.1497 | 306.5788 | 305.7038 | 310.0669 | 311.8116
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | Power Factor | 0.99756 | 0.99825 | 0.99633 | 0.99634 | 0.99624
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | 50 POE Load (A) | 481.5216 | 582.6437 | 580.8877 | 586.142 | 589.6414
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | NCC Rating (A) | 425 | 425 | 425 | 425 | 425 | Urban | 70
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | 10 POE Load (A) | 172.1548 | 173.5607 | 171.305 | 170.9475 | 170.4327
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | Power Factor | 0.99999 | 1 | 1 | 0.99999 | 0.99999
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | ECC Rating (A) | 480 | 480 | 480 | 480 | 480
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | 50 POE Load (A) | 265.9342 | 268.6448 | 264.0774 | 265.2804 | 264.0412
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 525 | 525 | 525 | 525 | 525 | Urban | 70
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 0.14991 | 0.14991 | 0.14991 | 0.14991 | 0.14991
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | Power Factor | 0.96802 | 0.96802 | 0.96802 | 0.96802 | 0.96802
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 542 | 542 | 542 | 542 | 542
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A) | 0.1578 | 0.1578 | 0.1578 | 0.1578 | 0.1578
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 502 | 502 | 502 | 502 | 502 | Urban | 70
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 130.7265 | 131.5959 | 130.7265 | 131.5959 | 131.5959
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | Power Factor | 0.96907 | 0.96904 | 0.9689 | 0.96894 | 0.96883
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 542 | 542 | 542 | 542 | 542
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A) | 264.4647 | 266.2925 | 264.4647 | 266.2925 | 268.1216
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 536 | 536 | 536 | 536 | 536 | Urban | 70
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | 10 POE Load (A) | 162.664 | 162.664 | 160.0845 | 160.9442 | 160.0845
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | Power Factor | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | 50 POE Load (A) | 303.3957 | 303.3957 | 299.953 | 299.953 | 299.953
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 525 | 525 | 525 | 525 | 525 | Urban | 70
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 132.2963 | 133.176 | 132.2963 | 133.176 | 133.176
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | Power Factor | 0.96942 | 0.96938 | 0.96924 | 0.96928 | 0.96917
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 542 | 542 | 542 | 542 | 542
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A) | 264.3633 | 266.1892 | 264.3633 | 266.1892 | 268.0165
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 536 | 536 | 536 | 536 | 536 | Urban | 70
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | 10 POE Load (A) | 162.664 | 162.664 | 160.0845 | 160.9442 | 160.0845
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | Power Factor | 0.99339 | 0.99343 | 0.99338 | 0.9934 | 0.99353
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | 50 POE Load (A) | 303.3957 | 303.3957 | 299.953 | 299.953 | 299.953
Victoria Park Bulk | 659B-1 | Victoria Pk BS | Clayfield | NCC Rating (A) | [5 empty] | Urban | 70
Victoria Park Bulk | 659B-1 | Victoria Pk BS | Clayfield | 10 POE Load (A)
Victoria Park Bulk | 659B-1 | Victoria Pk BS | Clayfield | Power Factor | 0 | 0 | 0 | 0 | 0
Victoria Park Bulk | 659B-1 | Victoria Pk BS | Clayfield | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
Victoria Park Bulk | 659B-1 | Victoria Pk BS | Clayfield | 50 POE Load (A)
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 588 | 588 | 588 | 588 | 588 | Urban | 70
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 9.2967 | 9.2967 | 9.2967 | 9.2967 | 9.2967
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | Power Factor | 1 | 1 | 1 | 1 | 1
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 588 | 588 | 588 | 588 | 588
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A)
Note on J1364: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: F3828-1: Approved project WR7111761 to reconductor this feeder with Moon by April 2020. Rating for new Moon 400A for 75A (As per Plant Rating Manual)
Note on L1631: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: F421-1: Open CB4742 @ ARL and Open CB3892 @ LDR
Note on L1646: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: F474A-1: Open CB4742 @ HWL and Open CB3892 @ LDR